## BuildingSummary
Building Summary Hospital pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Hospital
| Available Fuel Types | gas, electricity
| Principal Building Activity | Health care, inpatient
Form
| Total Floor Area (m2) | 22422.1768 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.3142
| Number of Floors | 5 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.1334
| East | 0.121
| North | 0.117
| West | 0.2315
| Total | 0.1461
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | See pictures and zone summary
| Floor to Ceiling Height (m) | 4.27
| Floor to Floor Height (m) | 4.27
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 5184.32
| Net Dimensions - Total Area (m2) | 4338.78
| Wall to Skin Ratio | 0.41902
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 3739.134
| Net Dimensions - Total Area (m2) | 3739.134
| Roof to Skin Ratio | 0.58098
Window Dimensions (m2)
| South | 220.72
| East | 144.86
| North | 186.18
| West | 293.66
| Total Area (m2) | 845.42
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 4 in slab
| Dimensions - Total Area (m2) | 3739.134
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 15534.17
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 44872.35
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.26534 | See Benchmark Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Boiler | 2003 CBECS
| Cooling Type | Chiller, water cooled | 2003 CBECS
| Fan Control | CAV, VAV | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80 | Winiarski and Halverson, 2008
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 4037.61

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 3739.35 | 9120.3661 | 2.439 | 0 | 0 | 37.1613 | 100.625 | 19.375 | 8.0729 |  |  | 10 |  | 1006.2497 |  | 0
ER_Exam1_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 26.02 | 0 | 4.6452 | 5.9998 | 41.3698 | 16.1458 |  | 3.7854 |  |  | 66.0874 |  | 0.89274
ER_Trauma1_Flr_1 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 0 | 4.6452 | 5.9998 | 41.3698 | 43.0556 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
ER_Exam3_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 19.51 | 0 | 4.6452 | 5.9998 | 41.3698 | 16.1458 |  | 3.7854 |  |  | 66.0874 |  | 0.66938
ER_Trauma2_Flr_1 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 0 | 4.6452 | 5.9998 | 41.3698 | 43.0556 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
ER_Triage_Mult4_Flr_1 | Yes | 4 | 27.87 | 118.9573 | 4.2683 | 26.02 | 0 | 4.6452 | 5.9998 | 41.3698 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 0.89274
Office1_Mult4_Flr_1 | Yes | 4 | 13.94 | 59.5 | 4.2683 | 13.01 | 2.96 | 13.2719 | 1.0503 | 25.7922 | 11.8403 |  |  | 10 |  | 10.5034 |  | 0.89241
Lobby_Records_Flr_1 | Yes | 1 | 1474.81 | 6294.9218 | 4.2683 | 409.7804 | 62.6301 | 13.0064 | 113.3908 | 15.7328 | 1.0764 |  |  | 10 |  | 1133.9077 |  | 0.26568
Corridor_Flr_1 | Yes | 1 | 569.03 | 2428.787 | 4.2683 | 91.0701 | 0 | 92.9031 | 6.125 | 14.5995 | 0 |  |  |  | 0.25 | 1349.325 |  | 0.15304
ER_NurseStn_Lobby_Flr_1 | Yes | 1 | 1235.61 | 5273.946 | 4.2683 | 110.5801 | 30.42 | 14.8645 | 83.1249 | 17.8959 | 14.6389 |  |  |  |  | 2929.9675 |  | 0.085575
OR1_Flr_2 | Yes | 1 | 55.74 | 237.9147 | 4.2683 | 65.0501 | 0 | 18.5806 | 2.9999 | 104.9796 | 53.8195 |  | 7.5708 |  |  | 198.2621 |  | 1.1159
OR2_Mult5_Flr_2 | Yes | 5 | 55.74 | 237.9147 | 4.2683 | 26.02 | 0 | 18.5806 | 2.9999 | 104.9796 | 53.8195 |  | 7.5708 |  |  | 198.2621 |  | 0.44637
OR3_Flr_2 | Yes | 1 | 55.74 | 237.9147 | 4.2683 | 39.03 | 0 | 18.5806 | 2.9999 | 104.9796 | 53.8195 |  | 7.5708 |  |  | 198.2621 |  | 0.66955
OR4_Flr_2 | Yes | 1 | 222.97 | 951.7014 | 4.2683 | 0 | 0 | 18.5806 | 12.0001 | 84.9091 | 53.8195 |  | 22.7124 |  |  | 793.0838 |  | 0
IC_PatRoom1_Mult5_Flr_2 | Yes | 5 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 41.3698 | 32.2917 |  |  |  |  | 49.5596 |  | 0.89261
IC_PatRoom2_Flr_2 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 41.3698 | 32.2917 |  |  |  |  | 66.0874 |  | 1.5621
IC_PatRoom3_Mult6_Flr_2 | Yes | 6 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 41.3698 | 32.2917 |  |  |  |  | 49.5596 |  | 0.89261
ICU_Flr_2 | Yes | 1 | 617.96 | 2637.6346 | 4.2683 | 214.6802 | 25.03 | 4.6452 | 133.0332 | 41.3698 | 32.2917 |  |  |  |  | 1465.3513 |  | 0.33219
ICU_NurseStn_Lobby_Flr_2 | Yes | 1 | 668.77 | 2854.5066 | 4.2683 | 0 | 0 | 18.5806 | 35.9929 | 18.4588 | 21.5278 |  |  | 10 |  | 1585.8356 |  | 0
Corridor_Flr_2 | Yes | 1 | 569.03 | 2428.787 | 4.2683 | 91.0701 | 0 | 92.9031 | 6.125 | 14.5995 | 0 |  |  | 10 | 0.25 | 1349.325 |  | 0.15304
OR_NurseStn_Lobby_Flr_2 | Yes | 1 | 1012.64 | 4322.2446 | 4.2683 | 182.1402 | 35.76 | 13.0064 | 77.8568 | 15.6644 | 11.1945 |  |  | 10 |  | 2401.245 |  | 0.17199
PatRoom1_Mult10_Flr_3 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
PatRoom2_Flr_3 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
PatRoom3_Mult10_Flr_3 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
PatRoom4_Flr_3 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
PatRoom5_Mult10_Flr_3 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
PhysTherapy_Flr_3 | Yes | 1 | 487.74 | 2081.8174 | 4.2683 | 0 | 0 | 18.5806 | 26.2499 | 26.9378 | 16.1458 |  | 3.7854 | 15 |  | 1156.5643 |  | 0
PatRoom6_Flr_3 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
PatRoom7_Mult10_Flr_3 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
PatRoom8_Flr_3 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
NurseStn_Lobby_Flr_3 | Yes | 1 | 905.8 | 3866.2201 | 4.2683 | 0 | 0 | 13.0064 | 69.6424 | 15.7501 | 11.1945 |  |  | 10 |  | 2147.8983 |  | 0
Lab_Flr_3 | Yes | 1 | 264.77 | 1130.116 | 4.2683 | 0 | 0 | 18.5806 | 14.2498 | 22.6566 | 43.0556 |  | 7.5708 | 10 |  | 627.8417 |  | 0
Corridor_SE_Flr_3 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823
Corridor_NW_Flr_3 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823
PatRoom1_Mult10_Flr_4 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
PatRoom2_Flr_4 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
PatRoom3_Mult10_Flr_4 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
PatRoom4_Flr_4 | Yes | 1 | 34.84 | 148.7073 | 4.2683 | 52.04 | 13.08 | 18.5806 | 1.8751 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 82.6151 |  | 1.4283
PatRoom5_Mult10_Flr_4 | Yes | 10 | 20.9 | 89.2073 | 4.2683 | 19.51 | 4.91 | 18.5806 | 1.1248 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 49.5596 |  | 0.89261
Radiology_Flr_4 | Yes | 1 | 487.74 | 2081.8174 | 4.2683 | 0 | 0 | 18.5806 | 26.2499 | 23.8269 | 107.639 |  | 3.7854 | 15 |  | 1156.5643 |  | 0
PatRoom6_Flr_4 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
PatRoom7_Mult10_Flr_4 | Yes | 10 | 20.21 | 86.2622 | 4.2683 | 18.87 | 4.74 | 18.5806 | 1.0877 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 47.9234 |  | 0.89281
PatRoom8_Flr_4 | Yes | 1 | 27.87 | 118.9573 | 4.2683 | 45.53 | 11.44 | 18.5806 | 1.4999 | 23.5705 | 21.5278 |  | 3.7854 |  |  | 66.0874 |  | 1.5621
NurseStn_Lobby_Flr_4 | Yes | 1 | 905.8 | 3866.2201 | 4.2683 | 0 | 0 | 13.0064 | 69.6424 | 15.7501 | 11.1945 |  |  | 10 |  | 2147.8983 |  | 0
Lab_Flr_4 | Yes | 1 | 264.77 | 1130.116 | 4.2683 | 0 | 0 | 18.5806 | 14.2498 | 22.6566 | 43.0556 |  | 7.5708 | 10 |  | 627.8417 |  | 0
Corridor_SE_Flr_4 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823
Corridor_NW_Flr_4 | Yes | 1 | 566.71 | 2418.8845 | 4.2683 | 45.53 | 0 | 92.9031 | 6.1 | 14.6034 | 0 |  |  |  | 0.25 | 1343.8236 |  | 0.076823
Dining_Flr_5 | Yes | 1 | 696.7728 | 2974.0307 | 4.2683 | 227.6702 | 35.76 | 9.2903 | 74.9999 | 27.7331 | 10.7639 |  |  | 10 |  | 749.9993 |  | 0.31244
NurseStn_Lobby_Flr_5 | Yes | 1 | 1040.514 | 4441.2192 | 4.2683 | 104.0801 | 0 | 13.0064 | 79.9999 | 15.6443 | 11.1945 |  |  | 10 |  | 2467.3419 |  | 0.095647
Kitchen_Flr_5 | Yes | 1 | 929.03 | 3965.3726 | 4.2683 | 260.2002 | 0 | 18.5806 | 49.9999 | 15.2932 | 80.7294 | 304.9413 | 567.81 | 15 |  | 2202.9829 | 2501.3191 | 0.26781
Office1_Flr_5 | Yes | 1 | 69.7 | 297.5 | 4.2683 | 71.5601 | 17.98 | 13.2719 | 5.2517 | 25.7922 | 10.7639 |  |  | 10 |  | 52.5171 |  | 0.98173
Office2_Mult5_Flr_5 | Yes | 5 | 69.68 | 297.4147 | 4.2683 | 32.52 | 8.17 | 13.2719 | 5.2502 | 25.7922 | 10.7639 |  |  | 10 |  | 52.502 |  | 0.44627
Office3_Flr_5 | Yes | 1 | 69.68 | 297.4147 | 4.2683 | 71.5501 | 17.98 | 13.2719 | 5.2502 | 25.7922 | 10.7639 |  |  | 10 |  | 52.502 |  | 0.98187
Office4_Mult6_Flr_5 | Yes | 6 | 13.94 | 59.5 | 4.2683 | 13.01 | 2.96 | 13.2719 | 1 | 25.7922 | 10.7639 |  |  | 10 |  | 10 |  | 0.89241
Corridor_Flr_5 | Yes | 1 | 501.68 | 2141.3174 | 4.2683 | 78.0601 | 0 | 92.9031 | 5.4 | 14.6034 | 0 |  |  |  | 0.25 | 125.42 |  | 0.14878
Building Total Conditioned Zones |  |  | 22422.1768 | 88864.1522 |  | 5184.3248 | 845.5408 |  | 1291.1824 |  |  |  | 1052.3412
Data Source | [7 empty] | 1 |  | 2 | 5, 6 | 5, 6 | 5, 6 | 3, 4 | 3, 4 | 3, 4 | 5 | 5
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] AIA Guidelines for Design and Construction of Hospital and Health Care Facilities: 2001 Edition. Washington, D.C.: American Institute of Architects.
[4] Green Guide for Health Care: Best Practices for Creating High Performance Healing Environments, Version 2.2. www.gghc.org.
[5] DOE Benchmark Report
[6] Smith, V. A. and D.R. Fisher. (2001). Estimating Food Service Loads and Profiles. ASHRAE Transactions 2001. V. 107. Pt 2. Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
| Construction | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab | 4 in slab
| R-value (m2·K / W) | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717 | 0.22717
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 3342.2324 | 3314.793 | 3054.4392 | 3108.9446 | 2604.5905 | 2701.535 | 2235.848 | 3119.3259 | 2242.8346 | 2341.4801 | 2956.782 | 2115.5725 | 2839.9209 | 2003.0375 | 2550.1851 | 1921.3793
Heating (kW)
| HEATSYS1 BOILER | 3506.0819 | 3704.9457 | 3671.5844 | 3715.8731 | 3373.921 | 3614.9506 | 3359.7285 | 3816.5661 | 3346.09 | 3603.3103 | 3780.3312 | 3296.9624 | 3863.3932 | 3563.0489 | 3768.0587 | 4149.6444
HVAC Efficiency
| Air Conditioning (COP) | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54 | 5.54
| Heating Efficiency (%) | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79 | 0.79
HVAC Control - Economizer
| CAV_1_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| CAV_2_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| CAV_1_FAN | 18.81 | 19.05 | 20.83 | 19.35 | 18.04 | 20.75 | 18.05 | 19.04 | 19.67 | 18.82 | 17.13 | 17.38 | 17.09 | 17.25 | 16.63 | 16.47
| CAV_2_FAN | 15.92 | 16.07 | 16.97 | 16.44 | 15.45 | 17.42 | 15.07 | 15.84 | 18.25 | 15.75 | 15.7 | 17.74 | 15.77 | 16.94 | 15.66 | 15.23
| VAV_1_FAN | 30.41 | 30.55 | 30.42 | 30.9 | 28.82 | 30.57 | 26.41 | 29.75 | 31.64 | 27.94 | 28.14 | 29.57 | 28 | 28.34 | 26.15 | 23.74
| VAV_2_FAN | 48.74 | 49.69 | 52.28 | 50.29 | 46.84 | 52.11 | 45.48 | 48.09 | 52.02 | 46.74 | 46.08 | 48.99 | 45.02 | 46.64 | 44.5 | 42.96
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.075012 | 0.096919 | 0.06728 | 0.096213 | 0.043883 | 0.086901 | 0.13 | 0.054911 | 0.036953 | 0.065548 | 0.098282 | 0.036954 | 0.051395 | 0.068964 | 0.051494 | 0.087234
| Total Cost ($/m2) | 29.57 | 36.54 | 24.55 | 34.26 | 14.59 | 31.46 | 39.83 | 19.2 | 12.52 | 20.36 | 32.36 | 11.99 | 16.84 | 21.85 | 16.29 | 27.09
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011448 | 0.0081774 | 0.0085705 | 0.010691 | 0.0084095 | 0.0081059 | 0.0084113 | 0.010061 | 0.0071663 | 0.0082953 | 0.0088667 | 0.007163 | 0.0079646 | 0.0086552 | 0.0079664 | 0.0041679
| Total Cost ($/m2) | 6.27 | 5.16 | 5.46 | 7.48 | 5.29 | 5.16 | 5.86 | 7.78 | 4.18 | 6.56 | 6.44 | 4.03 | 6.25 | 5.71 | 6.7 | 4.8
Total Utility Costs
| Cost Intensity ($/m2) | 35.84 | 41.7 | 30.01 | 41.74 | 19.88 | 36.62 | 45.69 | 26.98 | 16.7 | 26.92 | 38.8 | 16.02 | 23.1 | 27.56 | 23 | 31.89
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 2282263.8889 | 1854413.8889 | 1308136.1111 | 1310961.1111 | 1070336.1111 | 986272.2222 | 639219.4444 | 1093919.4444 | 665597.2222 | 569855.5556 | 744411.1111 | 495236.1111 | 669844.4444 | 396380.5556 | 414397.2222 | 254505.5556
| Interior Lighting | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667 | 2326391.6667
| Exterior Lighting | 30086.1111 | 30033.3333 | 30025 | 30075 | 30069.4444 | 30041.6667 | 30008.3333 | 30038.8889 | 30033.3333 | 29988.8889 | 29997.2222 | 30002.7778 | 30022.2222 | 29986.1111 | 29977.7778 | 29797.2222
| Interior Equipment | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444 | 1817169.4444
| Exterior Equipment | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667 | 694291.6667
| Fans | 751113.8889 | 748422.2222 | 812780.5556 | 756788.8889 | 707063.8889 | 814961.1111 | 693302.7778 | 732027.7778 | 805913.8889 | 719125 | 681536.1111 | 732994.4444 | 683063.8889 | 706875 | 662963.8889 | 652925
| Pumps | 510608.3333 | 489372.2222 | 437077.7778 | 444883.3333 | 381911.1111 | 384197.2222 | 313505.5556 | 433727.7778 | 315530.5556 | 321786.1111 | 390316.6667 | 284775 | 357252.7778 | 258083.3333 | 302752.7778 | 189805.5556
| Heat Rejection | 362841.6667 | 345672.2222 | 322625 | 302613.8889 | 282163.8889 | 266019.4444 | 240511.1111 | 266413.8889 | 183255.5556 | 229997.2222 | 207066.6667 | 152972.2222 | 184388.8889 | 132575 | 143272.2222 | 89283.3333
| Humidification | 7638.8889 | 94105.5556 | 377788.8889 | 248702.7778 | 92025 | 746075 | 64141.6667 | 395844.4444 | 707975 | 204111.1111 | 441863.8889 | 690302.7778 | 535636.1111 | 691702.7778 | 653716.6667 | 861155.5556
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 56850 | 54633.3333 | 54847.2222 | 52625 | 53094.4444 | 53219.4444 | 51544.4444 | 51308.3333 | 51175 | 50355.5556 | 50458.3333 | 50141.6667 | 49983.3333 | 49372.2222 | 48838.8889 | 47908.3333
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas (MJ)
| Heating | 10469070 | 12243730 | 12436940 | 13690020 | 12121820 | 12354870 | 13570260 | 15274140 | 11039580 | 15645360 | 14154210 | 10509000 | 15427570 | 12611230 | 16608580 | 23459360
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420 | 1358420
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 456550 | 547640 | 495230 | 635430 | 618380 | 558340 | 693490 | 704420 | 691330 | 740330 | 764980 | 761820 | 817320 | 826810 | 903630 | 1008110
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 44105340 | 44586020 | 43742670 | 44428100 | 40934880 | 43498730 | 40354480 | 45565060 | 40439730 | 42811170 | 42858230 | 38816660 | 44056270 | 40366630 | 44408210 | 50893540
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 366.4286 | 297.7352 | 210.0276 | 210.4812 | 171.8477 | 158.3508 | 102.6298 | 175.6341 | 106.8649 | 91.4931 | 119.5188 | 79.5126 | 107.5468 | 63.6408 | 66.5335 | 40.8621
| Interior Lighting (elec) | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135 | 373.5135
| Exterior Lighting (elec) | 4.8305 | 4.822 | 4.8207 | 4.8287 | 4.8278 | 4.8233 | 4.818 | 4.8229 | 4.822 | 4.8149 | 4.8162 | 4.8171 | 4.8202 | 4.8144 | 4.8131 | 4.7841
| Interior Equipment (elec) | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554 | 291.7554
| Exterior Equipment (elec) | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719 | 111.4719
| Fans (elec) | 120.595 | 120.1628 | 130.4959 | 121.5061 | 113.5226 | 130.846 | 111.3131 | 117.5306 | 129.3934 | 115.459 | 109.4239 | 117.6858 | 109.6692 | 113.4922 | 106.4421 | 104.8303
| Pumps (elec) | 81.9807 | 78.5711 | 70.175 | 71.4282 | 61.3177 | 61.6847 | 50.3348 | 69.6371 | 50.66 | 51.6643 | 62.6672 | 45.722 | 57.3587 | 41.4365 | 48.6084 | 30.4742
| Heat Rejection (elec) | 58.256 | 55.4994 | 51.799 | 48.5861 | 45.3028 | 42.7107 | 38.6152 | 42.774 | 29.4226 | 36.9272 | 33.2456 | 24.5604 | 29.6045 | 21.2856 | 23.0031 | 14.3349
| Humidification (elec) | 1.2265 | 15.1091 | 60.6558 | 39.9304 | 14.7751 | 119.786 | 10.2983 | 63.5548 | 113.6688 | 32.771 | 70.9434 | 110.8315 | 85.999 | 111.0563 | 104.9574 | 138.2627
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 9.1275 | 8.7716 | 8.806 | 8.4492 | 8.5246 | 8.5446 | 8.2757 | 8.2378 | 8.2164 | 8.0848 | 8.1013 | 8.0505 | 8.0251 | 7.927 | 7.8413 | 7.6919
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Gas (MJ/m2)
| Heating (gas) | 466.9056 | 546.0529 | 554.6698 | 610.5554 | 540.6159 | 551.0096 | 605.2143 | 681.2049 | 492.3496 | 697.7608 | 631.2576 | 468.6864 | 688.0477 | 562.4429 | 740.719 | 1046.2541
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836 | 60.5836
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 20.3615 | 24.424 | 22.0866 | 28.3393 | 27.5789 | 24.9012 | 30.9287 | 31.4161 | 30.8323 | 33.0177 | 34.117 | 33.9761 | 36.4513 | 36.8745 | 40.3006 | 44.9603
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1967.0354 | 1988.4731 | 1950.8608 | 1981.43 | 1825.6374 | 1939.9815 | 1799.7524 | 2032.1368 | 1803.5544 | 1909.3173 | 1911.4161 | 1731.1678 | 1964.847 | 1800.2943 | 1980.543 | 2269.7795
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 1441.5789 | 1397.7264 | 1386.9737 | 1322.237 | 1329.9648 | 1363.7571 | 1250.5853 | 1326.0757 | 1320.5087 | 1239.4779 | 1230.1406 | 1291.5083 | 1224.6035 | 1216.249 | 1219.4312 | 1207.5441
| Feb | 1446.4916 | 1356.9937 | 1426.9521 | 1335.5388 | 1292.0021 | 1367.0915 | 1235.2164 | 1287.0711 | 1362.3926 | 1247.0655 | 1213.4278 | 1278.4016 | 1225.9907 | 1255.0006 | 1219.8298 | 1211.8487
| Mar | 1460.5913 | 1389.5178 | 1480.7805 | 1384.8766 | 1348.6243 | 1398.9923 | 1231.1875 | 1334.1319 | 1386.8485 | 1251.2635 | 1251.5642 | 1370.4544 | 1252.2082 | 1292.1983 | 1225.1252 | 1208.4476
| Apr | 1482.1711 | 1430.264 | 1458.9339 | 1357.6642 | 1413.0013 | 1396.1487 | 1279.3175 | 1329.7061 | 1442.8787 | 1242.188 | 1298.5291 | 1319.7723 | 1256.4183 | 1294.8598 | 1241.1256 | 1213.5914
| May | 1562.5618 | 1560.8181 | 1501.466 | 1445.478 | 1329.3592 | 1511.0499 | 1271.6891 | 1435.775 | 1439.6492 | 1275.4234 | 1357.7446 | 1351.1647 | 1326.6601 | 1305.9875 | 1292.1699 | 1283.4734
| Jun | 1617.4823 | 1548.0392 | 1563.4087 | 1505.9042 | 1353.9579 | 1540.8921 | 1258.8643 | 1562.638 | 1480.1112 | 1285.782 | 1488.6117 | 1412.8702 | 1455.2476 | 1351.2903 | 1359.5032 | 1301.8234
| Jul | 1595.9344 | 1623.4574 | 1521.7901 | 1530.7735 | 1353.6446 | 1501.2643 | 1277.6618 | 1567.0843 | 1458.0807 | 1322.4149 | 1477.3988 | 1368.0406 | 1503.8024 | 1357.0283 | 1395.5455 | 1264.3634
| Aug | 1574.4291 | 1590.9844 | 1531.3477 | 1524.5782 | 1392.6687 | 1470.0766 | 1274.1067 | 1625.6557 | 1368.4638 | 1319.7026 | 1548.2918 | 1373.2627 | 1493.219 | 1344.2035 | 1378.9694 | 1242.4286
| Sep | 1557.0184 | 1606.5217 | 1473.7842 | 1477.6013 | 1381.3622 | 1483.7902 | 1314.1909 | 1409.1343 | 1412.8574 | 1320.1714 | 1405.9213 | 1398.8726 | 1358.9679 | 1284.3989 | 1358.7782 | 1199.8242
| Oct | 1557.967 | 1481.7631 | 1436.0212 | 1381.2438 | 1356.2841 | 1427.8544 | 1259.0599 | 1372.0667 | 1375.2821 | 1246.6686 | 1319.2825 | 1364.4661 | 1235.8501 | 1292.6527 | 1230.5344 | 1196.0951
| Nov | 1483.1512 | 1435.8138 | 1406.3473 | 1345.0098 | 1308.5197 | 1351.6947 | 1221.5559 | 1323.6413 | 1329.0306 | 1230.071 | 1332.6622 | 1323.8152 | 1255.5024 | 1237.8351 | 1238.7436 | 1196.9671
| Dec | 1449.3756 | 1389.2604 | 1418.9491 | 1327.9808 | 1331.0732 | 1365.7646 | 1240.8862 | 1301.0297 | 1289.9992 | 1190.0467 | 1213.5911 | 1275.722 | 1225.7005 | 1222.3233 | 1209.8293 | 1207.1294
Time of Peak Electrical Demand
| Jan | 06-JAN-11:45 | 03-JAN-11:45 | 26-JAN-16:15 | 30-JAN-16:15 | 26-JAN-13:00 | 30-JAN-16:00 | 20-JAN-14:00 | 05-JAN-14:00 | 20-JAN-16:15 | 03-JAN-17:00 | 26-JAN-16:00 | 24-JAN-16:15 | 03-JAN-17:00 | 10-JAN-17:30 | 31-JAN-17:00 | 25-JAN-16:15
| Feb | 23-FEB-11:45 | 15-FEB-16:15 | 28-FEB-17:00 | 06-FEB-16:15 | 10-FEB-10:00 | 17-FEB-17:30 | 15-FEB-16:30 | 16-FEB-16:15 | 13-FEB-16:30 | 22-FEB-11:45 | 09-FEB-17:15 | 07-FEB-14:00 | 08-FEB-17:00 | 03-FEB-17:30 | 15-FEB-17:00 | 17-FEB-17:00
| Mar | 14-MAR-10:45 | 24-MAR-16:15 | 30-MAR-15:00 | 22-MAR-16:00 | 31-MAR-15:00 | 21-MAR-15:00 | 13-MAR-12:00 | 17-MAR-16:00 | 02-MAR-16:15 | 23-MAR-15:00 | 31-MAR-16:45 | 30-MAR-15:15 | 31-MAR-15:00 | 29-MAR-16:00 | 06-MAR-17:00 | 22-MAR-15:00
| Apr | 04-APR-16:00 | 20-APR-15:15 | 26-APR-16:00 | 14-APR-16:00 | 11-APR-15:00 | 26-APR-15:00 | 13-APR-15:00 | 20-APR-15:00 | 21-APR-16:00 | 14-APR-16:00 | 27-APR-16:00 | 27-APR-12:00 | 06-APR-16:00 | 06-APR-16:00 | 27-APR-15:15 | 21-APR-16:00
| May | 19-MAY-15:15 | 18-MAY-16:45 | 19-MAY-16:45 | 31-MAY-16:00 | 31-MAY-15:15 | 11-MAY-15:00 | 25-MAY-15:30 | 31-MAY-15:00 | 12-MAY-16:45 | 05-MAY-15:00 | 30-MAY-16:00 | 19-MAY-16:00 | 31-MAY-16:00 | 04-MAY-16:00 | 12-MAY-16:00 | 24-MAY-15:15
| Jun | 27-JUN-15:00 | 29-JUN-16:30 | 08-JUN-15:00 | 08-JUN-15:00 | 23-JUN-16:30 | 08-JUN-15:00 | 16-JUN-15:30 | 30-JUN-16:00 | 27-JUN-16:00 | 27-JUN-16:00 | 08-JUN-12:00 | 15-JUN-16:00 | 29-JUN-16:00 | 30-JUN-15:00 | 14-JUN-15:15 | 15-JUN-16:00
| Jul | 13-JUL-15:45 | 18-JUL-12:30 | 11-JUL-16:15 | 25-JUL-16:15 | 26-JUL-16:00 | 31-JUL-16:30 | 03-JUL-12:00 | 25-JUL-15:00 | 31-JUL-16:00 | 27-JUL-16:00 | 14-JUL-10:45 | 12-JUL-15:00 | 13-JUL-16:00 | 21-JUL-16:00 | 12-JUL-08:30 | 20-JUL-16:00
| Aug | 21-AUG-15:15 | 03-AUG-15:15 | 11-AUG-16:00 | 17-AUG-15:15 | 08-AUG-16:30 | 02-AUG-16:30 | 09-AUG-15:15 | 09-AUG-15:15 | 01-AUG-15:00 | 18-AUG-16:00 | 04-AUG-15:00 | 29-AUG-15:00 | 25-AUG-16:00 | 18-AUG-16:00 | 11-AUG-16:15 | 18-AUG-16:00
| Sep | 01-SEP-15:15 | 15-SEP-15:15 | 12-SEP-15:15 | 01-SEP-15:45 | 01-SEP-15:00 | 20-SEP-16:00 | 28-SEP-15:45 | 27-SEP-15:15 | 20-SEP-16:00 | 01-SEP-15:00 | 07-SEP-16:00 | 13-SEP-15:00 | 22-SEP-12:00 | 01-SEP-16:00 | 08-SEP-16:00 | 07-SEP-15:00
| Oct | 06-OCT-15:00 | 30-OCT-15:15 | 23-OCT-16:30 | 20-OCT-16:45 | 19-OCT-15:45 | 03-OCT-15:00 | 30-OCT-13:00 | 03-OCT-10:45 | 13-OCT-15:15 | 17-OCT-16:00 | 31-OCT-09:00 | 05-OCT-15:00 | 25-OCT-15:15 | 19-OCT-16:00 | 25-OCT-15:15 | 27-OCT-16:00
| Nov | 03-NOV-15:15 | 27-NOV-17:00 | 15-NOV-16:30 | 03-NOV-15:15 | 29-NOV-11:45 | 22-NOV-16:30 | 16-NOV-16:15 | 03-NOV-13:00 | 13-NOV-17:00 | 28-NOV-17:00 | 02-NOV-09:30 | 10-NOV-13:00 | 01-NOV-15:15 | 21-NOV-11:45 | 03-NOV-16:00 | 29-NOV-17:30
| Dec | 15-DEC-17:30 | 06-DEC-17:30 | 06-DEC-16:15 | 28-DEC-14:00 | 18-DEC-11:45 | 05-DEC-16:30 | 29-DEC-16:00 | 06-DEC-16:00 | 12-DEC-15:00 | 07-DEC-17:00 | 05-DEC-16:00 | 29-DEC-14:00 | 20-DEC-16:30 | 12-DEC-17:00 | 21-DEC-16:45 | 13-DEC-17:00
Source Energy
| Total Source Energy (GJ) | 118965.45 | 125995.96 | 108762.24 | 113822.38 | 98453.92 | 120129.95 | 93605.92 | 119875.6 | 105042.19 | 63043.39 | 112030.05 | 100680.98 | 110141.64 | 105039.64 | 108379.39 | 117743.51
| Total Source Energy (MJ/m2) | 5305.69 | 5619.24 | 4850.64 | 5076.32 | 4390.9 | 5357.62 | 4174.69 | 5346.28 | 4684.73 | 2811.65 | 4996.38 | 4490.23 | 4912.16 | 4684.62 | 4833.57 | 5251.19
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 34349.21 | 27857.87 | 36688 | 22541.71 | 18532.98 | 31793.14 | 11263.65 | 19060.7 | 19207.9 | 10637.32 | 14124.1 | 14251.15 | 12562.81 | 10683.3 | 8072.85 | 5436.97
| Humidification | 10.23 | 126.03 | 505.93 | 333.06 | 123.24 | 999.15 | 85.9 | 530.12 | 948.12 | 273.34 | 591.75 | 924.45 | 717.32 | 926.33 | 875.46 | 1153.26
| Water Systems | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61 | 4037.61
| Total Building | 38397.05 | 32021.5 | 41231.54 | 26912.38 | 22693.83 | 36829.89 | 15387.15 | 23628.42 | 24193.63 | 14948.27 | 18753.45 | 19213.21 | 17317.74 | 15647.24 | 12985.92 | 10627.83
Emissions
| Carbon Equivalent (kg) | 2645680 | 3075250 | 2727380 | 2742340 | 1125410 | 2995570 | 1084590 | 2428610 | 3339530 | 827123.614 | 4230040 | 3199270 | 2832620 | 2862460 | 2768440 | 2425080
| CO2 (kg) | 6253280 | 7813630 | 6552490 | 6399260 | 3060440 | 7229050 | 2957460 | 5648400 | 7913400 | 2129190 | 9930660 | 7581940 | 6715620 | 6808010 | 6581000 | 6253770
| NOX (kg) | 10480.645 | 9970.5967 | 10492.322 | 11520.9338 | 2657.31 | 11310.7895 | 2573.3241 | 10307.4975 | 13306.9787 | 2774.9749 | 17308.3978 | 12745.706 | 11413.8213 | 11416.3305 | 11107.6132 | 7370.6587
| SO2 (kg) | 37838.8334 | 40331.7958 | 32901.7994 | 28029.8292 | 21695.53 | 44662.8324 | 19995.3164 | 28627.9221 | 33179.5512 | 5386.6534 | 49763.3001 | 31768.7222 | 17347.2796 | 18969.3604 | 16747.4959 | 35452.5768
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.1737 | 0.1149 | 0.0908 | 0.104 | 0.0113 | 0.0852 | 0.0107 | 0.1172 | 0.1306 | 0.0229 | 0.1517 | 0.1251 | 0.1283 | 0.133 | 0.1241 | 0.1226
| Water for Electricity (m3) | 4682.67 | 13756.5 | 243016 | 49852.1 | 130885 | 222727 | 120623 | 1780.23 | 34498 | 71140.3 | 11455.1 | 33031.1 | 11400.1 | 449922 | 11005.6 | 7114.2

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 44105.34 | 1967.04 | 1967.04
Net Site Energy | 44105.34 | 1967.04 | 1967.04
Total Source Energy | 118965.45 | 5305.69 | 5305.69
Net Source Energy | 118965.45 | 5305.69 | 5305.69
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 10469.07 | 0 | 0 | 0 | 0
Cooling | 8216.15 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.31 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2704.01 | 0 | 0 | 0 | 0 | 0
Pumps | 1838.19 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1306.23 | 0 | 0 | 0 | 0 | 34349.21
Humidification | 27.5 | 0 | 0 | 0 | 0 | 10.23
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 456.55 | 0 | 0 | 0 | 4037.61
Refrigeration | 204.66 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 31821.31 | 12284.03 | 0 | 0 | 0 | 38397.05
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.54 | 0.384 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.54 | 0.384 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.54 | 0.384 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.54 | 0.384 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.54 | 0.384 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 186.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3342232.39 | 5.54
HEATSYS1 BOILER | Boiler:HotWater | 3506081.94 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3156418.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 621527.9 | 402417.32 | 219110.58 | 0.65 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 401872.41 | 284738.1 | 117134.3 | 0.71 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 945612.85 | 623591.28 | 322021.57 | 0.66 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1543448.63 | 1012110.24 | 531338.39 | 0.66 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 79793.99 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14569.67 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16735.32 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 21050.87 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16667.03 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16667.03 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16667.03 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16667.03 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 54530.19 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65574.44 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65574.44 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 55713.46 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16393.61 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16393.61 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65574.44 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 200456.25 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29819.54 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40651.53 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18142.83 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 79671.04 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 150408.03 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 77806.32 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77806.32 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 59274.03 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 28535.72 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29098.46 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 53391.29 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 57134.46 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 271850.76 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 54695.86 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198678.97 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 37194.92 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 9433.27 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4498.63 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 41755.04 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 9751.22 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 8420.31 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61469.06 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61469.06 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13600.02 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13517 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 88687.24 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 88087.77 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13845.08 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13762.11 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 62582.13 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 62394.6 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14820.86 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14749.82 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 109422.69 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 108924.83 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15626.57 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15550 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 43033.68 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 107584.19 | -
CAV_1_HEATC | Coil:Heating:Water | 41817.12 | -
CAV_2_HEATC | Coil:Heating:Water | 196600.76 | -
VAV_1_HEATC | Coil:Heating:Water | 73782.8 | -
VAV_2_HEATC | Coil:Heating:Water | 126321.34 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.81 | 31669.86 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.92 | 26978.96 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 30.41 | 50854.79 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 48.74 | 80740.09 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 30626.93 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19305.98 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 44548.45 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 506532.1636 | 838.5031 | 2982.7416 | 0 | 0.0137 | 369114.2572 | 213259.1157
February | 455842.8377 | 756.7119 | 2700.9323 | 0 | 0.0124 | 334242.1603 | 192130.3191
March | 516035.3745 | 860.0623 | 3084.5703 | 0 | 0.0142 | 381720.5207 | 217844.0811
April | 497459.0875 | 832.513 | 3000.3812 | 0 | 0.0138 | 371304.8392 | 210343.926
May | 545243.1317 | 917.9995 | 3332.0207 | 0 | 0.0153 | 412350.6719 | 231101.7236
June | 538014.918 | 908.7437 | 3310.7831 | 0 | 0.0152 | 409724.8177 | 228330.014
July | 558262.678 | 944.5448 | 3447.9849 | 0 | 0.0158 | 426705.4915 | 237083.4797
August | 565691.3743 | 957.8818 | 3499.9123 | 0 | 0.016 | 433132.3932 | 240315.2718
September | 537108.0688 | 906.1902 | 3297.1606 | 0 | 0.0151 | 408038.1395 | 227842.7719
October | 536083.2269 | 900.6988 | 3261.2573 | 0 | 0.015 | 403591.8753 | 227031.0456
November | 499894.8309 | 833.6945 | 2992.2883 | 0 | 0.0138 | 370300.9208 | 211083.7911
December | 497109.7744 | 823.1015 | 2928.8008 | 0 | 0.0135 | 362439.2488 | 209311.7701
Annual Sum or Average | 6253280 | 10480.645 | 37838.8334 | 0 | 0.1737 | 4682670 | 2645680
Minimum of Months | 455842.8377 | 756.7119 | 2700.9323 | 0 | 0.0124 | 334242.1603 | 192130.3191
Maximum of Months | 565691.3743 | 957.8818 | 3499.9123 | 0 | 0.016 | 433132.3932 | 240315.2718
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2508340000000 | 1441578.877 | 06-JAN-11:45 | 445952.007 | 310109.712 | 93692.376 | 0 | 315440.266 | 0 | 60974.704 | 41427.996 | 162962.637 | 0 | 0 | 0 | 11019.178 | 0 | 0
February | 2271360000000 | 1446491.561 | 23-FEB-11:45 | 445952.007 | 310109.712 | 96111.494 | 0 | 317706.296 | 0 | 61043.289 | 41427.996 | 162962.637 | 0 | 0 | 0 | 11178.13 | 0 | 0
March | 2594000000000 | 1460591.346 | 14-MAR-10:45 | 445952.007 | 310109.712 | 93027.799 | 0 | 334536.795 | 0 | 61511.775 | 41427.996 | 162962.637 | 0 | 0 | 0 | 11062.624 | 0 | 0
April | 2523220000000 | 1482171.13 | 04-APR-16:00 | 445952.007 | 310109.712 | 107071.605 | 0 | 345583.222 | 0 | 62538.091 | 41427.996 | 162962.637 | 0 | 0 | 0 | 6525.859 | 0 | 0
May | 2802150000000 | 1562561.772 | 19-MAY-15:15 | 445952.007 | 310109.712 | 110766.693 | 0 | 420213.355 | 0 | 64581.958 | 41427.996 | 162962.637 | 0 | 0 | 0 | 6547.414 | 0 | 0
June | 2784310000000 | 1617482.319 | 27-JUN-15:00 | 445952.007 | 310109.712 | 107838.549 | 0 | 477087.978 | 0 | 65406.507 | 41427.996 | 162962.637 | 0 | 0 | 0 | 6696.933 | 0 | 0
July | 2899700000000 | 1595934.424 | 13-JUL-15:45 | 445952.007 | 310109.712 | 111917.964 | 0 | 451622.822 | 0 | 65285.414 | 41427.996 | 162962.637 | 0 | 0 | 0 | 6655.873 | 0 | 0
August | 2943380000000 | 1574429.129 | 21-AUG-15:15 | 445952.007 | 310109.712 | 100455.209 | 0 | 442862.788 | 0 | 63986.245 | 41427.996 | 162962.637 | 0 | 0 | 0 | 6672.535 | 0 | 0
September | 2772850000000 | 1557018.353 | 01-SEP-15:15 | 445952.007 | 310109.712 | 109271.217 | 0 | 416374.962 | 0 | 64343.707 | 41427.996 | 162962.637 | 0 | 0 | 0 | 6576.114 | 0 | 0
October | 2742630000000 | 1557966.972 | 06-OCT-15:00 | 445952.007 | 310109.712 | 112058.959 | 0 | 414155.433 | 0 | 64721.754 | 41427.996 | 162962.637 | 0 | 0 | 0 | 6578.473 | 0 | 0
November | 2516400000000 | 1483151.179 | 03-NOV-15:15 | 445952.007 | 310109.712 | 98179.897 | 0 | 355848.774 | 0 | 62382.877 | 41427.996 | 162962.637 | 0 | 0 | 0 | 6287.278 | 0 | 0
December | 2462980000000 | 1449375.613 | 15-DEC-17:30 | 445952.007 | 310109.712 | 99768.623 | 0 | 314510.172 | 6881 | 61477.267 | 41427.996 | 162962.637 | 0 | 0 | 0 | 6286.197 | 0 | 0
Annual Sum or Average | 31821300000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 2271360000000 | 1441578.877 |  | 445952.007 | 310109.712 | 93027.799 | 0 | 314510.172 | 0 | 60974.704 | 41427.996 | 162962.637 | 0 | 0 | 0 | 6286.197 | 0 | 0
Maximum of Months | 2943380000000 | 1617482.319 |  | 445952.007 | 310109.712 | 112058.959 | 0 | 477087.978 | 6881 | 65406.507 | 41427.996 | 162962.637 | 0 | 0 | 0 | 11178.13 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 663045.69 | 140629.02 | 0 | 803674.7
Cost per Total Building Area ($/m2) | 29.57 | 6.27 | 0 | 35.84
Cost per Net Conditioned Building Area ($/m2) | 29.57 | 6.27 | 0 | 35.84

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 44586.02 | 1988.47 | 1988.47
Net Site Energy | 44586.02 | 1988.47 | 1988.47
Total Source Energy | 125995.96 | 5619.24 | 5619.24
Net Source Energy | 125995.96 | 5619.24 | 5619.24
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 12243.73 | 0 | 0 | 0 | 0
Cooling | 6675.89 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.12 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2694.32 | 0 | 0 | 0 | 0 | 0
Pumps | 1761.74 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1244.42 | 0 | 0 | 0 | 0 | 27857.87
Humidification | 338.78 | 0 | 0 | 0 | 0 | 126.03
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 547.64 | 0 | 0 | 0 | 4037.61
Refrigeration | 196.68 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 30436.23 | 14149.79 | 0 | 0 | 0 | 32021.5
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.54 | 0.384 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.54 | 0.384 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.54 | 0.384 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.54 | 0.384 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.54 | 0.384 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 186.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3314793 | 5.54
HEATSYS1 BOILER | Boiler:HotWater | 3704945.7 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3130504.86
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 623214.57 | 402915.87 | 220298.71 | 0.65 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 375044.74 | 272201.11 | 102843.63 | 0.73 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 945168.27 | 621487.07 | 323681.21 | 0.66 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1561941.06 | 1022012.45 | 539928.61 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 76575.36 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12785.23 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16674.1 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 22072.09 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16606.06 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16606.06 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16606.06 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16606.06 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 56964 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65334.56 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65334.56 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 55736.22 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16333.64 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16333.64 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65334.56 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 202902.67 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29820.16 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40339.91 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18326.84 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 81270.22 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 155768.82 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 77521.69 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77521.69 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 60295.9 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29494.51 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 30052.19 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 55535.06 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 55935.11 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 269919.03 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 53881.91 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 204758.61 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38443.11 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 9883.31 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4968.19 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 43060.95 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 9979.82 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 8609.49 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 64596 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 64396.39 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14205.76 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14142.98 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 89307.06 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 88787.68 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13837.49 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13766.57 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61996.19 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61838.85 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15467.57 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15385.95 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 111877.2 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 111285.58 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15797.85 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15716.37 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42876.25 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 107190.62 | -
CAV_1_HEATC | Coil:Heating:Water | 24197.94 | -
CAV_2_HEATC | Coil:Heating:Water | 210664.02 | -
VAV_1_HEATC | Coil:Heating:Water | 122480.88 | -
VAV_2_HEATC | Coil:Heating:Water | 218617.55 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 19.05 | 32071.61 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.07 | 27232.13 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 30.55 | 51088.9 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 49.69 | 82317.13 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 30375.49 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20401.01 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 44182.71 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 635624.6519 | 802.1819 | 3156.1533 | 0 | 0.009 | 1076470 | 249018.0554
February | 557475.0438 | 702.4818 | 2753.0871 | 0 | 0.0079 | 938987.8888 | 218263.2301
March | 641631.9998 | 814.6313 | 3254.1608 | 0 | 0.0093 | 1109920 | 251999.0232
April | 624298.9228 | 796.2745 | 3217.3674 | 0 | 0.0092 | 1097390 | 245661.9393
May | 677635.2159 | 868.662 | 3553.2852 | 0 | 0.0101 | 1211980 | 267211.6256
June | 684279.8738 | 880.764 | 3638.3262 | 0 | 0.0103 | 1241010 | 270293.8104
July | 716330.5899 | 923.0611 | 3823.3533 | 0 | 0.0108 | 1304120 | 283088.4858
August | 723557.0766 | 932.1446 | 3858.7234 | 0 | 0.0109 | 1316190 | 285914.8817
September | 662448.839 | 850.6038 | 3493.3904 | 0 | 0.0099 | 1191560 | 261404.8381
October | 653400.6965 | 834.5943 | 3384.171 | 0 | 0.0096 | 1154290 | 257268.3556
November | 614405.1874 | 780.4767 | 3121.8611 | 0 | 0.0089 | 1064800 | 241359.0297
December | 622539.2587 | 784.7207 | 3077.9166 | 0 | 0.0088 | 1049780 | 243769.548
Annual Sum or Average | 7813630 | 9970.5967 | 40331.7958 | 0 | 0.1149 | 13756500 | 3075250
Minimum of Months | 557475.0438 | 702.4818 | 2753.0871 | 0 | 0.0079 | 938987.8888 | 218263.2301
Maximum of Months | 723557.0766 | 932.1446 | 3858.7234 | 0 | 0.0109 | 1316190 | 285914.8817
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2381680000000 | 1397726.419 | 03-JAN-11:45 | 445952.007 | 310109.712 | 84310.178 | 0 | 283207.097 | 0 | 59230.45 | 41087.876 | 162962.637 | 0 | 0 | 0 | 10866.461 | 0 | 0
February | 2077510000000 | 1356993.693 | 15-FEB-16:15 | 445952.007 | 310109.712 | 89860.99 | 0 | 242851.978 | 0 | 58049.291 | 41087.876 | 162962.637 | 0 | 0 | 0 | 6119.201 | 0 | 0
March | 2455700000000 | 1389517.79 | 24-MAR-16:15 | 445952.007 | 310109.712 | 93476.789 | 0 | 270489.342 | 0 | 59153.683 | 41087.876 | 162962.637 | 0 | 0 | 0 | 6285.744 | 0 | 0
April | 2427970000000 | 1430264.034 | 20-APR-15:15 | 445952.007 | 310109.712 | 99966.566 | 0 | 303533.636 | 0 | 60315.715 | 41087.876 | 162962.637 | 0 | 0 | 0 | 6335.884 | 0 | 0
May | 2681510000000 | 1560818.112 | 18-MAY-16:45 | 445952.007 | 310109.712 | 109595.705 | 0 | 420101.263 | 0 | 64372.464 | 41087.876 | 162962.637 | 0 | 0 | 0 | 6636.447 | 0 | 0
June | 2745730000000 | 1548039.229 | 29-JUN-16:30 | 445952.007 | 310109.712 | 109013.925 | 0 | 408622.631 | 0 | 63658.51 | 41087.876 | 162962.637 | 0 | 0 | 0 | 6631.93 | 0 | 0
July | 2885370000000 | 1623457.444 | 18-JUL-12:30 | 445952.007 | 302612.437 | 103214.761 | 0 | 495154.614 | 0 | 64887.825 | 41087.876 | 162962.637 | 0 | 0 | 0 | 7585.286 | 0 | 0
August | 2912060000000 | 1590984.362 | 03-AUG-15:15 | 445952.007 | 310109.712 | 110195.583 | 0 | 449307.426 | 0 | 64714.547 | 41087.876 | 162962.637 | 0 | 0 | 0 | 6654.573 | 0 | 0
September | 2636330000000 | 1606521.736 | 15-SEP-15:15 | 445952.007 | 310109.712 | 107311.862 | 0 | 467771.52 | 0 | 64713.635 | 41087.876 | 162962.637 | 0 | 0 | 0 | 6612.486 | 0 | 0
October | 2553860000000 | 1481763.079 | 30-OCT-15:15 | 445952.007 | 310109.712 | 92493.274 | 0 | 361499.591 | 0 | 61341.054 | 41087.876 | 162962.637 | 0 | 0 | 0 | 6316.929 | 0 | 0
November | 2355860000000 | 1435813.823 | 27-NOV-17:00 | 445952.007 | 310109.712 | 88354.029 | 0 | 313954.922 | 6881 | 60246.691 | 41087.876 | 162962.637 | 0 | 0 | 0 | 6264.948 | 0 | 0
December | 2322640000000 | 1389260.372 | 06-DEC-17:30 | 445952.007 | 310109.712 | 89166.784 | 0 | 268051.091 | 6881 | 58985.682 | 41087.876 | 162962.637 | 0 | 0 | 0 | 6063.582 | 0 | 0
Annual Sum or Average | 30436200000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 2077510000000 | 1356993.693 |  | 445952.007 | 302612.437 | 84310.178 | 0 | 242851.978 | 0 | 58049.291 | 41087.876 | 162962.637 | 0 | 0 | 0 | 6063.582 | 0 | 0
Maximum of Months | 2912060000000 | 1623457.444 |  | 445952.007 | 310109.712 | 110195.583 | 0 | 495154.614 | 6881 | 64887.825 | 41087.876 | 162962.637 | 0 | 0 | 0 | 10866.461 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 819400.96 | 115708.77 | 0 | 935109.73
Cost per Total Building Area ($/m2) | 36.54 | 5.16 | 0 | 41.7
Cost per Net Conditioned Building Area ($/m2) | 36.54 | 5.16 | 0 | 41.7

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 43742.67 | 1950.86 | 1950.86
Net Site Energy | 43742.67 | 1950.86 | 1950.86
Total Source Energy | 108762.24 | 4850.64 | 4850.64
Net Source Energy | 108762.24 | 4850.64 | 4850.64
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 12436.94 | 0 | 0 | 0 | 0
Cooling | 4709.29 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.09 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2926.01 | 0 | 0 | 0 | 0 | 0
Pumps | 1573.48 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1161.45 | 0 | 0 | 0 | 0 | 36688
Humidification | 1360.04 | 0 | 0 | 0 | 0 | 505.93
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 495.23 | 0 | 0 | 0 | 4037.61
Refrigeration | 197.45 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 29452.08 | 14290.59 | 0 | 0 | 0 | 41231.54
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.54 | 0.384 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.54 | 0.384 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.54 | 0.384 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.54 | 0.384 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.54 | 0.384 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 186.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3054439.16 | 5.54
HEATSYS1 BOILER | Boiler:HotWater | 3671584.41 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2884625.58
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 630619.87 | 405340.15 | 225279.72 | 0.64 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 386888.83 | 274709.49 | 112179.34 | 0.71 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 889774.67 | 578267.04 | 311507.63 | 0.65 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1546633.73 | 1001443.12 | 545190.61 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 47194.62 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15088.85 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16079.49 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 23245.22 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16013.87 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16013.87 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16013.87 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16013.87 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 60833.19 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63004.66 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63004.66 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 57020.32 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15751.17 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15751.17 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63004.66 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 210701 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29824 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 43215.35 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19858.53 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 85831.7 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 163744.09 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 74757.19 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 74757.19 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64574.94 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 28408.43 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 28954.68 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 57615.8 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 58254 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 274608.3 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 55297.12 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198668.59 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 41448.33 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 10860.61 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5917.03 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 45271.42 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 10770.04 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 9560.06 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 76768.88 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 76559.9 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16944.77 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16889.6 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 96546.73 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 96172.11 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15707.67 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15650.85 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 67869.5 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 67794.59 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 17396.88 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 17318.63 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 119225.49 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 118631.33 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 17332.07 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 17251.75 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 41347.24 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 103368.1 | -
CAV_1_HEATC | Coil:Heating:Water | 16199.19 | -
CAV_2_HEATC | Coil:Heating:Water | 211989.64 | -
VAV_1_HEATC | Coil:Heating:Water | 82131.46 | -
VAV_2_HEATC | Coil:Heating:Water | 172223.5 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 20.83 | 35068.6 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.97 | 28563.48 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 30.42 | 50887.08 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 52.28 | 86615.93 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 27989.71 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20217.3 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 40712.47 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 540874.0804 | 848.4316 | 2588.154 | 0 | 0.0072 | 19115400 | 223345.8643
February | 493435.9127 | 777.0158 | 2382.8377 | 0 | 0.0066 | 17599100 | 204060.0618
March | 553560.6171 | 881.1256 | 2741.4095 | 0 | 0.0076 | 20248000 | 229878.2848
April | 538398.2913 | 862.9168 | 2709.1879 | 0 | 0.0075 | 20010300 | 224181.0169
May | 563372.8159 | 908.3257 | 2873.7846 | 0 | 0.0079 | 21226400 | 235124.1744
June | 553971.7096 | 900.4119 | 2878.2305 | 0 | 0.0079 | 21259600 | 231933.1114
July | 574335.9879 | 936.1529 | 3003.1438 | 0 | 0.0082 | 22182400 | 240726.1939
August | 580221.133 | 945.1312 | 3029.4721 | 0 | 0.0083 | 22376800 | 243130.7553
September | 539363.6709 | 873.2612 | 2777.685 | 0 | 0.0076 | 20516800 | 225472.5775
October | 546812.6405 | 875.7244 | 2746.6201 | 0 | 0.0076 | 20286800 | 227616.0149
November | 522458.2203 | 828.3237 | 2563.545 | 0 | 0.0071 | 18934100 | 216629.1393
December | 545684.1086 | 855.5011 | 2607.7292 | 0 | 0.0072 | 19259900 | 225283.9883
Annual Sum or Average | 6552490 | 10492.322 | 32901.7994 | 0 | 0.0908 | 243016000 | 2727380
Minimum of Months | 493435.9127 | 777.0158 | 2382.8377 | 0 | 0.0066 | 17599100 | 204060.0618
Maximum of Months | 580221.133 | 945.1312 | 3029.4721 | 0 | 0.0083 | 22376800 | 243130.7553
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2316670000000 | 1386973.688 | 26-JAN-16:15 | 445952.007 | 310109.712 | 101219.719 | 0 | 153098.316 | 0 | 51294.435 | 37860.711 | 162962.637 | 0 | 0 | 0 | 6002.424 | 0 | 0
February | 2132910000000 | 1426952.082 | 28-FEB-17:00 | 445952.007 | 310109.712 | 100661.458 | 0 | 163075.215 | 0 | 51430.825 | 37860.711 | 162962.637 | 0 | 0 | 0 | 6170.914 | 0 | 0
March | 2453940000000 | 1480780.499 | 30-MAR-15:00 | 445952.007 | 310109.712 | 111322.465 | 0 | 192626.418 | 0 | 52805.613 | 37860.711 | 162962.637 | 0 | 0 | 0 | 6410.007 | 0 | 0
April | 2425140000000 | 1458933.944 | 26-APR-16:00 | 445952.007 | 310109.712 | 116799.87 | 0 | 213036.353 | 0 | 53511.079 | 37860.711 | 162962.637 | 0 | 0 | 0 | 6555.201 | 0 | 0
May | 2572510000000 | 1501465.979 | 19-MAY-16:45 | 445952.007 | 310109.712 | 124268.976 | 0 | 243399.822 | 0 | 54630.313 | 37860.711 | 162962.637 | 0 | 0 | 0 | 6667.099 | 0 | 0
June | 2576540000000 | 1563408.747 | 08-JUN-15:00 | 445952.007 | 310109.712 | 132761.52 | 0 | 308212.218 | 0 | 56470.186 | 37860.711 | 162962.637 | 0 | 0 | 0 | 6740.969 | 0 | 0
July | 2688380000000 | 1521790.149 | 11-JUL-16:15 | 445952.007 | 310109.712 | 127100.028 | 0 | 372425.98 | 0 | 58527.038 | 37860.711 | 162962.637 | 0 | 0 | 0 | 6852.036 | 0 | 0
August | 2711940000000 | 1531347.741 | 11-AUG-16:00 | 445952.007 | 310109.712 | 127060.303 | 0 | 380273.144 | 0 | 60285.398 | 37860.711 | 162962.637 | 0 | 0 | 0 | 6843.828 | 0 | 0
September | 2486510000000 | 1473784.216 | 12-SEP-15:15 | 445952.007 | 310109.712 | 125858.465 | 0 | 326950.074 | 0 | 57309.804 | 37860.711 | 162962.637 | 0 | 0 | 0 | 6780.805 | 0 | 0
October | 2458640000000 | 1436021.169 | 23-OCT-16:30 | 445952.007 | 310109.712 | 106128.862 | 0 | 193528.047 | 0 | 52474.473 | 37860.711 | 162962.637 | 0 | 0 | 0 | 6412.388 | 0 | 0
November | 2294700000000 | 1406347.262 | 15-NOV-16:30 | 445952.007 | 310109.712 | 106050.405 | 0 | 178826.806 | 0 | 52125.045 | 37860.711 | 162962.637 | 0 | 0 | 0 | 6241.546 | 0 | 0
December | 2334190000000 | 1418949.075 | 06-DEC-16:15 | 445952.007 | 310109.712 | 99478.852 | 0 | 137658.173 | 0 | 50791.773 | 37860.711 | 162962.637 | 0 | 0 | 0 | 5834.851 | 0 | 0
Annual Sum or Average | 29452100000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 2132910000000 | 1386973.688 |  | 445952.007 | 310109.712 | 99478.852 | 0 | 137658.173 | 0 | 50791.773 | 37860.711 | 162962.637 | 0 | 0 | 0 | 5834.851 | 0 | 0
Maximum of Months | 2711940000000 | 1563408.747 |  | 445952.007 | 310109.712 | 132761.52 | 0 | 380273.144 | 0 | 60285.398 | 37860.711 | 162962.637 | 0 | 0 | 0 | 6852.036 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 550428.99 | 122478.18 | 0 | 672907.17
Cost per Total Building Area ($/m2) | 24.55 | 5.46 | 0 | 30.01
Cost per Net Conditioned Building Area ($/m2) | 24.55 | 5.46 | 0 | 30.01

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 44428.1 | 1981.43 | 1981.43
Net Site Energy | 44428.1 | 1981.43 | 1981.43
Total Source Energy | 113822.38 | 5076.32 | 5076.32
Net Source Energy | 113822.38 | 5076.32 | 5076.32
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 13690.02 | 0 | 0 | 0 | 0
Cooling | 4719.46 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2724.44 | 0 | 0 | 0 | 0 | 0
Pumps | 1601.58 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1089.41 | 0 | 0 | 0 | 0 | 22541.71
Humidification | 895.33 | 0 | 0 | 0 | 0 | 333.06
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 635.43 | 0 | 0 | 0 | 4037.61
Refrigeration | 189.45 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 28744.23 | 15683.87 | 0 | 0 | 0 | 26912.38
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.54 | 0.384 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.54 | 0.384 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.54 | 0.384 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.54 | 0.384 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.54 | 0.384 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 186.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3108944.6 | 5.54
HEATSYS1 BOILER | Boiler:HotWater | 3715873.13 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2936100.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 608153.34 | 388038.82 | 220114.52 | 0.64 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 370895.66 | 265713.06 | 105182.6 | 0.72 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 919444.15 | 596770.43 | 322673.72 | 0.65 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1521984.77 | 982518 | 539466.77 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 71902.25 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14224.92 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16125.49 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 21500.68 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16059.69 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16059.69 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16059.69 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16059.69 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 56808.87 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63184.92 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63184.92 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 55656.41 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15796.23 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15796.23 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63184.92 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 202436.98 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29823.78 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38713.18 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17808.02 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 80392.22 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 152835.47 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 74971.08 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 74971.08 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 59441.74 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 28349.5 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 28910.51 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 54602.54 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 55869.5 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 269767.51 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 53838.45 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198665.49 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 39083.85 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 9752.55 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5243.15 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 42269.31 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 9655.39 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 8334.57 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 68241.87 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 68033.81 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14687.19 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14629.19 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 89489.89 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 89089.45 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13754.83 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13686.6 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59229.14 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59229.14 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15359.53 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15274.73 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 110326.87 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 109690.3 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15264.9 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15173.8 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 41465.54 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 103663.85 | -
CAV_1_HEATC | Coil:Heating:Water | 22410.13 | -
CAV_2_HEATC | Coil:Heating:Water | 207509.93 | -
VAV_1_HEATC | Coil:Heating:Water | 139414.47 | -
VAV_2_HEATC | Coil:Heating:Water | 245744.9 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 19.35 | 32578.04 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.44 | 27676.4 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 30.9 | 51676.99 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 50.29 | 83308.61 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 28489.17 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20461.18 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 41438.97 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 538815.9023 | 942.7081 | 2226.0254 | 0 | 0.0083 | 3958790 | 228378.6552
February | 486207.6416 | 856.1079 | 2035.3644 | 0 | 0.0076 | 3619770 | 206583.1505
March | 538367.7425 | 960.2577 | 2314.0471 | 0 | 0.0086 | 4115520 | 229881.8711
April | 507581.6118 | 912.8001 | 2218.2602 | 0 | 0.0082 | 3945250 | 217424.6567
May | 535693.7536 | 973.7252 | 2391.9525 | 0 | 0.0088 | 4254270 | 230424.3183
June | 539232.0213 | 989.8722 | 2455.3775 | 0 | 0.0091 | 4367170 | 232843.5309
July | 567971.623 | 1046.0489 | 2603.0034 | 0 | 0.0096 | 4629780 | 245569.2267
August | 577103.6488 | 1063.3599 | 2647.2686 | 0 | 0.0098 | 4708510 | 249563.0312
September | 539372.6682 | 987.5892 | 2443.5608 | 0 | 0.009 | 4346130 | 232669.5768
October | 524815.1058 | 944.7684 | 2298.3629 | 0 | 0.0085 | 4087720 | 224896.8973
November | 511715.1591 | 908.5799 | 2179.1975 | 0 | 0.0081 | 3875650 | 218119.0252
December | 532382.4244 | 935.1164 | 2217.4091 | 0 | 0.0083 | 3943500 | 225990.2124
Annual Sum or Average | 6399260 | 11520.9338 | 28029.8292 | 0 | 0.104 | 49852100 | 2742340
Minimum of Months | 486207.6416 | 856.1079 | 2035.3644 | 0 | 0.0076 | 3619770 | 206583.1505
Maximum of Months | 577103.6488 | 1063.3599 | 2647.2686 | 0 | 0.0098 | 4708510 | 249563.0312
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2282600000000 | 1322236.998 | 30-JAN-16:15 | 445952.007 | 310109.712 | 86426.369 | 0 | 91081.199 | 0 | 48319.8 | 38536.322 | 162962.637 | 0 | 0 | 0 | 5352.54 | 0 | 0
February | 2087130000000 | 1335538.762 | 06-FEB-16:15 | 445952.007 | 310109.712 | 88440.925 | 0 | 109383.751 | 0 | 49455.441 | 38536.322 | 162962.637 | 0 | 0 | 0 | 5602.833 | 0 | 0
March | 2372970000000 | 1384876.589 | 22-MAR-16:00 | 445952.007 | 310109.712 | 99955.18 | 0 | 145880.039 | 0 | 51458.972 | 38536.322 | 162962.637 | 0 | 0 | 0 | 6075.888 | 0 | 0
April | 2274790000000 | 1357664.225 | 14-APR-16:00 | 445952.007 | 310109.712 | 102509.91 | 0 | 235987.946 | 0 | 55182.896 | 38536.322 | 162962.637 | 0 | 0 | 0 | 6422.794 | 0 | 0
May | 2452970000000 | 1445477.975 | 31-MAY-16:00 | 445952.007 | 310109.712 | 104550.393 | 0 | 318349.296 | 0 | 58458.102 | 38536.322 | 162962.637 | 0 | 0 | 0 | 6559.505 | 0 | 0
June | 2518070000000 | 1505904.212 | 08-JUN-15:00 | 445952.007 | 310109.712 | 111262.384 | 0 | 370209.938 | 0 | 60338.592 | 38536.322 | 162962.637 | 0 | 0 | 0 | 6532.619 | 0 | 0
July | 2669490000000 | 1530773.504 | 25-JUL-16:15 | 445952.007 | 310109.712 | 105487.225 | 0 | 400400.799 | 0 | 60794.059 | 38536.322 | 162962.637 | 0 | 0 | 0 | 6530.741 | 0 | 0
August | 2714880000000 | 1524578.224 | 17-AUG-15:15 | 445952.007 | 310109.712 | 109565.744 | 0 | 390274.315 | 0 | 60483.752 | 38536.322 | 162962.637 | 0 | 0 | 0 | 6693.733 | 0 | 0
September | 2505940000000 | 1477601.278 | 01-SEP-15:45 | 445952.007 | 310109.712 | 110933.575 | 0 | 343030.807 | 0 | 59640.887 | 38536.322 | 162962.637 | 0 | 0 | 0 | 6435.33 | 0 | 0
October | 2356940000000 | 1381243.823 | 20-OCT-16:45 | 445952.007 | 310109.712 | 100363.074 | 0 | 260465.39 | 0 | 56630.14 | 38536.322 | 162962.637 | 0 | 0 | 0 | 6224.541 | 0 | 0
November | 2234660000000 | 1345009.788 | 03-NOV-15:15 | 445952.007 | 310109.712 | 94142.609 | 0 | 103646.906 | 0 | 49402.588 | 38536.322 | 162962.637 | 0 | 0 | 0 | 5481.556 | 0 | 0
December | 2273790000000 | 1327980.753 | 28-DEC-14:00 | 445952.007 | 302612.437 | 91438.251 | 0 | 96731.366 | 0 | 48887.501 | 38536.322 | 162962.637 | 0 | 0 | 0 | 6270.076 | 0 | 0
Annual Sum or Average | 28744200000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 2087130000000 | 1322236.998 |  | 445952.007 | 302612.437 | 86426.369 | 0 | 91081.199 | 0 | 48319.8 | 38536.322 | 162962.637 | 0 | 0 | 0 | 5352.54 | 0 | 0
Maximum of Months | 2714880000000 | 1530773.504 |  | 445952.007 | 310109.712 | 111262.384 | 0 | 400400.799 | 0 | 60794.059 | 38536.322 | 162962.637 | 0 | 0 | 0 | 6693.733 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 768209.54 | 167676.85 | 0 | 935886.39
Cost per Total Building Area ($/m2) | 34.26 | 7.48 | 0 | 41.74
Cost per Net Conditioned Building Area ($/m2) | 34.26 | 7.48 | 0 | 41.74

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 40934.88 | 1825.64 | 1825.64
Net Site Energy | 40934.88 | 1825.64 | 1825.64
Total Source Energy | 98453.92 | 4390.9 | 4390.9
Net Source Energy | 98453.92 | 4390.9 | 4390.9
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 12121.82 | 0 | 0 | 0 | 0
Cooling | 3853.21 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.25 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2545.43 | 0 | 0 | 0 | 0 | 0
Pumps | 1374.88 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1015.79 | 0 | 0 | 0 | 0 | 18532.98
Humidification | 331.29 | 0 | 0 | 0 | 0 | 123.24
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 618.38 | 0 | 0 | 0 | 4037.61
Refrigeration | 191.14 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 26836.26 | 14098.61 | 0 | 0 | 0 | 22693.83
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.54 | 0.384 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.54 | 0.384 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.54 | 0.384 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.54 | 0.384 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.54 | 0.384 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 186.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2604590.45 | 5.54
HEATSYS1 BOILER | Boiler:HotWater | 3373921.02 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2459786.5
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 535914.08 | 357067.76 | 178846.33 | 0.67 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 347870.46 | 255813.43 | 92057.04 | 0.74 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 814262.32 | 551681.48 | 262580.84 | 0.68 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1346065.07 | 906702.98 | 439362.09 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 72374.39 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11164.92 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16676.07 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 18403.98 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16608.02 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16608.02 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16608.02 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16608.02 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 52881.29 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65342.28 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65342.28 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53824.12 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16335.57 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16335.57 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65342.28 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 194332.11 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29820.18 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31933.83 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14767.1 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 73897.16 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 134871.04 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 77530.86 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77530.86 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53660.48 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29432.05 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29990.47 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 49326.9 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 52251.79 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 263133.93 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 51484.94 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 204759.93 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38578.45 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 8786.17 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5382.3 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 38176.35 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7975.63 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6404.87 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 69230.52 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 68730.78 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13591.1 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13480.02 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 78380.04 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77933.19 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10495.61 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10427.44 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61251.44 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61251.44 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13958.61 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13834.8 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 99944.32 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 99218.54 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12256.92 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12165.14 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42881.32 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 107203.3 | -
CAV_1_HEATC | Coil:Heating:Water | 28285.2 | -
CAV_2_HEATC | Coil:Heating:Water | 192840.97 | -
VAV_1_HEATC | Coil:Heating:Water | 77035.18 | -
VAV_2_HEATC | Coil:Heating:Water | 133918.61 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.04 | 30372.76 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.45 | 26183.14 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 28.82 | 48208.25 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 46.84 | 77591.13 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 23867.47 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18578.24 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 34716.45 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 261085.0687 | 227.1858 | 1762.9194 | 0 | 0.0009 | 10634900 | 95740.5789
February | 230455.8129 | 200.4757 | 1566.4429 | 0 | 0.0008 | 9449730 | 84540.3
March | 258940.2953 | 225.0869 | 1790.0614 | 0 | 0.0009 | 10798900 | 95081.0784
April | 245125.0118 | 212.9864 | 1710.9078 | 0 | 0.0009 | 10321400 | 90058.0911
May | 257517.5296 | 223.5406 | 1835.6149 | 0 | 0.0009 | 11073900 | 94727.6388
June | 253300.3474 | 219.7163 | 1834.8087 | 0 | 0.0009 | 11069200 | 93265.6051
July | 260126.419 | 225.4525 | 1917.3271 | 0 | 0.001 | 11567200 | 95879.8805
August | 267592.78 | 231.7752 | 1998.9192 | 0 | 0.001 | 12059500 | 98712.9348
September | 253467.6382 | 219.6967 | 1865.497 | 0 | 0.0009 | 11254500 | 93417.1335
October | 261759.4903 | 227.1284 | 1882.7446 | 0 | 0.001 | 11358300 | 96339.5792
November | 251158.7808 | 218.2243 | 1753.8728 | 0 | 0.0009 | 10580600 | 92277.4731
December | 259907.4986 | 226.0413 | 1776.4142 | 0 | 0.0009 | 10716400 | 95374.1921
Annual Sum or Average | 3060440 | 2657.31 | 21695.53 | 0 | 0.0113 | 130885000 | 1125410
Minimum of Months | 230455.8129 | 200.4757 | 1566.4429 | 0 | 0.0008 | 9449730 | 84540.3
Maximum of Months | 267592.78 | 231.7752 | 1998.9192 | 0 | 0.001 | 12059500 | 98712.9348
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2180560000000 | 1329964.821 | 26-JAN-13:00 | 445952.007 | 302612.437 | 89870.684 | 0 | 153373.308 | 0 | 44960.832 | 32284.698 | 162962.637 | 0 | 0 | 0 | 7084.997 | 0 | 0
February | 1937550000000 | 1292002.126 | 10-FEB-10:00 | 445952.007 | 310109.712 | 86084.25 | 0 | 127803.821 | 0 | 44142.533 | 32284.698 | 162962.637 | 0 | 0 | 0 | 6818.754 | 0 | 0
March | 2214170000000 | 1348624.273 | 31-MAR-15:00 | 445952.007 | 310109.712 | 96449.179 | 0 | 142166.874 | 0 | 44818.683 | 32284.698 | 162962.637 | 0 | 0 | 0 | 6102.458 | 0 | 0
April | 2116280000000 | 1413001.346 | 11-APR-15:00 | 445952.007 | 310109.712 | 93459.612 | 0 | 182377.439 | 0 | 45493.481 | 32284.698 | 162962.637 | 0 | 0 | 0 | 6519.274 | 0 | 0
May | 2270570000000 | 1329359.184 | 31-MAY-15:15 | 445952.007 | 310109.712 | 92530.746 | 0 | 229270.335 | 0 | 50105.769 | 32284.698 | 162962.637 | 0 | 0 | 0 | 6143.279 | 0 | 0
June | 2269600000000 | 1353957.864 | 23-JUN-16:30 | 445952.007 | 310109.712 | 97715.285 | 0 | 247365.066 | 0 | 51365.156 | 32284.698 | 162962.637 | 0 | 0 | 0 | 6203.303 | 0 | 0
July | 2371700000000 | 1353644.595 | 26-JUL-16:00 | 445952.007 | 310109.712 | 101054.759 | 0 | 243626.853 | 0 | 51436.32 | 32284.698 | 162962.637 | 0 | 0 | 0 | 6217.609 | 0 | 0
August | 2472650000000 | 1392668.674 | 08-AUG-16:30 | 445952.007 | 310109.712 | 103038.279 | 0 | 280411.843 | 0 | 51477.415 | 32284.698 | 162962.637 | 0 | 0 | 0 | 6432.083 | 0 | 0
September | 2307590000000 | 1381362.217 | 01-SEP-15:00 | 445952.007 | 310109.712 | 101950.977 | 0 | 269223.419 | 0 | 52691.032 | 32284.698 | 162962.637 | 0 | 0 | 0 | 6187.735 | 0 | 0
October | 2328880000000 | 1356284.081 | 19-OCT-15:45 | 445952.007 | 310109.712 | 96593.529 | 0 | 250624.287 | 0 | 51620.117 | 32284.698 | 162962.637 | 0 | 0 | 0 | 6137.094 | 0 | 0
November | 2169430000000 | 1308519.675 | 29-NOV-11:45 | 445952.007 | 310109.712 | 86300.462 | 0 | 113401.133 | 0 | 43623.244 | 32284.698 | 162962.637 | 0 | 0 | 0 | 10200.797 | 0 | 0
December | 2197270000000 | 1331073.165 | 18-DEC-11:45 | 445952.007 | 310109.712 | 82606.924 | 0 | 134981.404 | 0 | 44169.72 | 32284.698 | 162962.637 | 0 | 0 | 0 | 10861.407 | 0 | 0
Annual Sum or Average | 26836300000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1937550000000 | 1292002.126 |  | 445952.007 | 302612.437 | 82606.924 | 0 | 113401.133 | 0 | 43623.244 | 32284.698 | 162962.637 | 0 | 0 | 0 | 6102.458 | 0 | 0
Maximum of Months | 2472650000000 | 1413001.346 |  | 445952.007 | 310109.712 | 103038.279 | 0 | 280411.843 | 0 | 52691.032 | 32284.698 | 162962.637 | 0 | 0 | 0 | 10861.407 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 327127.66 | 118561.93 | 0 | 445689.59
Cost per Total Building Area ($/m2) | 14.59 | 5.29 | 0 | 19.88
Cost per Net Conditioned Building Area ($/m2) | 14.59 | 5.29 | 0 | 19.88

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 43498.73 | 1939.98 | 1939.98
Net Site Energy | 43498.73 | 1939.98 | 1939.98
Total Source Energy | 120129.95 | 5357.62 | 5357.62
Net Source Energy | 120129.95 | 5357.62 | 5357.62
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 12354.87 | 0 | 0 | 0 | 0
Cooling | 3550.58 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.15 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2933.86 | 0 | 0 | 0 | 0 | 0
Pumps | 1383.11 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 957.67 | 0 | 0 | 0 | 0 | 31793.14
Humidification | 2685.87 | 0 | 0 | 0 | 0 | 999.15
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 558.34 | 0 | 0 | 0 | 4037.61
Refrigeration | 191.59 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 29227.1 | 14271.63 | 0 | 0 | 0 | 36829.89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.54 | 0.384 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.54 | 0.384 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.54 | 0.384 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.54 | 0.384 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.54 | 0.384 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 186.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2701535.04 | 5.54
HEATSYS1 BOILER | Boiler:HotWater | 3614950.57 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2551341.4
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 578387.92 | 372955.28 | 205432.64 | 0.64 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 354432.42 | 257102.73 | 97329.69 | 0.73 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 829756.18 | 539991.32 | 289764.86 | 0.65 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1438857 | 930826.98 | 508030.02 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 43094.1 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14274.49 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15466.93 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 21282.86 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15403.82 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15403.82 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15403.82 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15403.82 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 57677.26 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 60604.49 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 60604.49 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 55843.28 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15151.12 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15151.12 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 60604.49 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 206881.29 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29828.41 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 41955.87 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18907.11 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 83206.5 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 154075.06 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 71909.3 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 71909.3 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 62609.78 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 28175.74 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 28731.02 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 53882.4 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 55783.47 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 269504.86 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 53812.44 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 204151.72 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40830.95 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 10305.05 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5810.06 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 43100.08 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 10111.11 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 8795.4 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 74767.76 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 74450.03 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16097.98 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16020.73 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 88332.22 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 87878.45 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14255.35 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14216.75 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 65245.52 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 65104.28 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16694.14 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16592.16 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 114932.64 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 114185.81 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16378.19 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16284.56 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 39772.11 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 99430.28 | -
CAV_1_HEATC | Coil:Heating:Water | 12386.17 | -
CAV_2_HEATC | Coil:Heating:Water | 209522.12 | -
VAV_1_HEATC | Coil:Heating:Water | 103199.92 | -
VAV_2_HEATC | Coil:Heating:Water | 201214.56 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 20.75 | 34927.19 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.42 | 29321.79 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 30.57 | 51125.86 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 52.11 | 86322.04 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 24755.83 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19905.45 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 36008.62 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 606668.996 | 930.401 | 3571.3295 | 0 | 0.0069 | 17808900 | 249436.0697
February | 544280.9909 | 840.9956 | 3263.0379 | 0 | 0.0063 | 16271900 | 224436.9447
March | 614821.023 | 953.3079 | 3717.1161 | 0 | 0.0071 | 18536400 | 253869.2777
April | 598519.4261 | 937.7133 | 3709.5612 | 0 | 0.0071 | 18499100 | 248144.3959
May | 627413.492 | 988.1001 | 3936.7477 | 0 | 0.0075 | 19632200 | 260655.7276
June | 620422.6385 | 985.9846 | 3976.4831 | 0 | 0.0075 | 19830700 | 258675.8655
July | 613364.8364 | 975.9712 | 3942.5539 | 0 | 0.0075 | 19661500 | 255858.2478
August | 623178.5236 | 991.0378 | 4000.4773 | 0 | 0.0076 | 19950400 | 259894.8966
September | 593799.9902 | 939.3104 | 3764.8215 | 0 | 0.0071 | 18775000 | 247122.2559
October | 599764.1502 | 937.6911 | 3698.7371 | 0 | 0.0071 | 18445000 | 248455.4532
November | 578424.8628 | 895.0466 | 3479.894 | 0 | 0.0067 | 17353300 | 238650.7937
December | 608386.2755 | 935.2299 | 3602.073 | 0 | 0.0069 | 17962300 | 250370.3146
Annual Sum or Average | 7229050 | 11310.7895 | 44662.8324 | 0 | 0.0852 | 222727000 | 2995570
Minimum of Months | 544280.9909 | 840.9956 | 3263.0379 | 0 | 0.0063 | 16271900 | 224436.9447
Maximum of Months | 627413.492 | 991.0378 | 4000.4773 | 0 | 0.0076 | 19950400 | 260655.7276
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2336960000000 | 1363757.052 | 30-JAN-16:00 | 445952.007 | 310109.712 | 93331.508 | 0 | 90371.106 | 6881 | 43670.091 | 33486.356 | 162962.637 | 0 | 0 | 0 | 5541.109 | 0 | 0
February | 2135260000000 | 1367091.531 | 17-FEB-17:30 | 445952.007 | 310109.712 | 98883.677 | 0 | 96936.183 | 6881 | 44028.706 | 33486.356 | 162962.637 | 0 | 0 | 0 | 5599.757 | 0 | 0
March | 2432410000000 | 1398992.257 | 21-MAR-15:00 | 445952.007 | 310109.712 | 101233.038 | 0 | 124463.297 | 0 | 45810.276 | 33486.356 | 162962.637 | 0 | 0 | 0 | 5881.011 | 0 | 0
April | 2427520000000 | 1396148.743 | 26-APR-15:00 | 445952.007 | 310109.712 | 108090.019 | 0 | 132244.955 | 0 | 46288.843 | 33486.356 | 162962.637 | 0 | 0 | 0 | 5912.157 | 0 | 0
May | 2576220000000 | 1511049.913 | 11-MAY-15:00 | 445952.007 | 310109.712 | 121848.049 | 0 | 203676.51 | 0 | 49287.14 | 33486.356 | 162962.637 | 0 | 0 | 0 | 6588.132 | 0 | 0
June | 2602270000000 | 1540892.093 | 08-JUN-15:00 | 445952.007 | 310109.712 | 133660.034 | 0 | 269625.659 | 0 | 51377.126 | 33486.356 | 162962.637 | 0 | 0 | 0 | 6740.4 | 0 | 0
July | 2580070000000 | 1501264.27 | 31-JUL-16:30 | 445952.007 | 310109.712 | 118149.917 | 0 | 205093.755 | 0 | 48995.889 | 33486.356 | 162962.637 | 0 | 0 | 0 | 6652.851 | 0 | 0
August | 2617970000000 | 1470076.59 | 02-AUG-16:30 | 445952.007 | 310109.712 | 130141.473 | 0 | 327208.707 | 0 | 53352.662 | 33486.356 | 162962.637 | 0 | 0 | 0 | 6863.036 | 0 | 0
September | 2463730000000 | 1483790.215 | 20-SEP-16:00 | 445952.007 | 310109.712 | 124746.8 | 0 | 223926.299 | 0 | 49659.884 | 33486.356 | 162962.637 | 0 | 0 | 0 | 6675.346 | 0 | 0
October | 2420430000000 | 1427854.44 | 03-OCT-15:00 | 445952.007 | 310109.712 | 117309.369 | 0 | 204922.296 | 0 | 48699.007 | 33486.356 | 162962.637 | 0 | 0 | 0 | 6567.524 | 0 | 0
November | 2277170000000 | 1351694.655 | 22-NOV-16:30 | 445952.007 | 310109.712 | 98540.293 | 0 | 101879.948 | 6881 | 44311.936 | 33486.356 | 162962.637 | 0 | 0 | 0 | 5622.156 | 0 | 0
December | 2357090000000 | 1365764.637 | 05-DEC-16:30 | 445952.007 | 310109.712 | 95657.122 | 0 | 121487.597 | 6881 | 45143.009 | 33486.356 | 162962.637 | 0 | 0 | 0 | 5764.127 | 0 | 0
Annual Sum or Average | 29227100000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 2135260000000 | 1351694.655 |  | 445952.007 | 310109.712 | 93331.508 | 0 | 90371.106 | 0 | 43670.091 | 33486.356 | 162962.637 | 0 | 0 | 0 | 5541.109 | 0 | 0
Maximum of Months | 2617970000000 | 1540892.093 |  | 445952.007 | 310109.712 | 133660.034 | 0 | 327208.707 | 6881 | 53352.662 | 33486.356 | 162962.637 | 0 | 0 | 0 | 6863.036 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 705514.51 | 115685.01 | 0 | 821199.52
Cost per Total Building Area ($/m2) | 31.46 | 5.16 | 0 | 36.62
Cost per Net Conditioned Building Area ($/m2) | 31.46 | 5.16 | 0 | 36.62

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 40354.48 | 1799.75 | 1799.75
Net Site Energy | 40354.48 | 1799.75 | 1799.75
Total Source Energy | 93605.92 | 4174.69 | 4174.69
Net Source Energy | 93605.92 | 4174.69 | 4174.69
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 13570.26 | 0 | 0 | 0 | 0
Cooling | 2301.19 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.03 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2495.89 | 0 | 0 | 0 | 0 | 0
Pumps | 1128.62 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 865.84 | 0 | 0 | 0 | 0 | 11263.65
Humidification | 230.91 | 0 | 0 | 0 | 0 | 85.9
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 693.49 | 0 | 0 | 0 | 4037.61
Refrigeration | 185.56 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 24732.31 | 15622.16 | 0 | 0 | 0 | 15387.15
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.54 | 0.384 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.54 | 0.384 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.54 | 0.384 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.54 | 0.384 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.54 | 0.384 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 186.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2235847.99 | 5.54
HEATSYS1 BOILER | Boiler:HotWater | 3359728.52 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2111544.53
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 496797.71 | 338558.18 | 158239.53 | 0.68 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 308852.12 | 234196.03 | 74656.08 | 0.76 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 709263.24 | 487405.98 | 221857.26 | 0.69 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1237357.2 | 846526.93 | 390830.27 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 38914.71 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10987.95 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16729.39 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 15591.22 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16661.12 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16661.12 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16661.12 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16661.12 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 53240.57 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65551.2 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65551.2 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 52185.57 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16387.8 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16387.8 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65551.2 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 192774.13 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29819.72 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30723.64 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13570.34 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 70393.93 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 120326.67 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 77778.74 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77778.74 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 50819.09 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29418.41 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29977.03 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 44418.82 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 49576.87 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 257543.58 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 49895.52 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198681.55 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 42459.58 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 9374.6 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6934.93 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 34830.01 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7036.3 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5468.67 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 89745.97 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 89156.44 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16335.01 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16208.72 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 70708.42 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 70216.19 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10243.07 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10243.07 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61447.27 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61447.27 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16047.49 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15893.21 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 94045.1 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 93175.91 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11033.22 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10924.38 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 43018.42 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 107546.05 | -
CAV_1_HEATC | Coil:Heating:Water | 23224.9 | -
CAV_2_HEATC | Coil:Heating:Water | 195744.71 | -
VAV_1_HEATC | Coil:Heating:Water | 87958.69 | -
VAV_2_HEATC | Coil:Heating:Water | 163093.67 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.05 | 30391.14 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.07 | 25537.83 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 26.41 | 44453.39 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 45.48 | 75347.38 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20488.45 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18500.09 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 29801.51 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 258220.6229 | 225.2037 | 1652.2524 | 0 | 0.0009 | 9966910 | 94411.5488
February | 226622.22 | 197.4046 | 1493.1778 | 0 | 0.0008 | 9007530 | 82989.958
March | 255460.9904 | 222.4697 | 1693.1462 | 0 | 0.0009 | 10213900 | 93581.2008
April | 239717.1666 | 208.6671 | 1605.2634 | 0 | 0.0009 | 9683810 | 87864.1099
May | 249034.8048 | 216.5852 | 1702.1209 | 0 | 0.0009 | 10268300 | 91384.4685
June | 241404.4839 | 209.7929 | 1677.928 | 0 | 0.0009 | 10122400 | 88669.7901
July | 244504.3479 | 212.4193 | 1711.5526 | 0 | 0.0009 | 10325300 | 89845.2454
August | 251679.5168 | 218.5697 | 1776.676 | 0 | 0.0009 | 10718300 | 92527.2725
September | 240491.8393 | 208.8666 | 1695.4012 | 0 | 0.0009 | 10228000 | 88407.2323
October | 248895.0362 | 216.3919 | 1714.0037 | 0 | 0.0009 | 10340000 | 91372.3482
November | 244828.3543 | 213.1725 | 1629.4124 | 0 | 0.0009 | 9829440 | 89706.7783
December | 256605.0318 | 223.7809 | 1644.3818 | 0 | 0.0009 | 9919450 | 93828.3773
Annual Sum or Average | 2957460 | 2573.3241 | 19995.3164 | 0 | 0.0107 | 120623000 | 1084590
Minimum of Months | 226622.22 | 197.4046 | 1493.1778 | 0 | 0.0008 | 9007530 | 82989.958
Maximum of Months | 258220.6229 | 225.2037 | 1776.676 | 0 | 0.0009 | 10718300 | 94411.5488
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2043590000000 | 1250585.283 | 20-JAN-14:00 | 445952.007 | 302612.437 | 88071.976 | 0 | 63518.436 | 0 | 35811.962 | 27714.022 | 162962.637 | 0 | 0 | 0 | 6323.526 | 0 | 0
February | 1846880000000 | 1235216.425 | 15-FEB-16:30 | 445952.007 | 310109.712 | 91499.579 | 0 | 150336.959 | 0 | 40515.537 | 27714.022 | 162962.637 | 0 | 0 | 0 | 6125.971 | 0 | 0
March | 2094230000000 | 1231187.473 | 13-MAR-12:00 | 445952.007 | 302612.437 | 81666.15 | 0 | 78889.783 | 0 | 36726.394 | 27714.022 | 162962.637 | 0 | 0 | 0 | 6482.519 | 0 | 0
April | 1985540000000 | 1279317.55 | 13-APR-15:00 | 445952.007 | 310109.712 | 98495.082 | 0 | 129715.672 | 0 | 39710.054 | 27714.022 | 162962.637 | 0 | 0 | 0 | 6107.041 | 0 | 0
May | 2105380000000 | 1271689.116 | 25-MAY-15:30 | 445952.007 | 310109.712 | 93814.38 | 0 | 181687.832 | 0 | 43301.83 | 27714.022 | 162962.637 | 0 | 0 | 0 | 6146.696 | 0 | 0
June | 2075480000000 | 1258864.251 | 16-JUN-15:30 | 445952.007 | 310109.712 | 98934.44 | 0 | 166030.655 | 0 | 40780.974 | 27714.022 | 162962.637 | 0 | 0 | 0 | 6379.803 | 0 | 0
July | 2117080000000 | 1277661.81 | 03-JUL-12:00 | 445952.007 | 302612.437 | 89656.694 | 0 | 199440.666 | 0 | 41852.307 | 27714.022 | 162962.637 | 0 | 0 | 0 | 7471.039 | 0 | 0
August | 2197650000000 | 1274106.731 | 09-AUG-15:15 | 445952.007 | 310109.712 | 92639.584 | 0 | 185427.795 | 0 | 43130.064 | 27714.022 | 162962.637 | 0 | 0 | 0 | 6170.909 | 0 | 0
September | 2097120000000 | 1314190.876 | 28-SEP-15:45 | 445952.007 | 310109.712 | 106745.884 | 0 | 211286.067 | 0 | 42659.335 | 27714.022 | 162962.637 | 0 | 0 | 0 | 6761.211 | 0 | 0
October | 2120090000000 | 1259059.899 | 30-OCT-13:00 | 445952.007 | 302612.437 | 86080.271 | 0 | 133102.22 | 0 | 39290.658 | 27714.022 | 162962.637 | 0 | 0 | 0 | 6996.023 | 0 | 0
November | 2015400000000 | 1221555.854 | 16-NOV-16:15 | 445952.007 | 310109.712 | 85589.107 | 0 | 141829.003 | 0 | 41565.336 | 27714.022 | 162962.637 | 0 | 0 | 0 | 5834.03 | 0 | 0
December | 2033860000000 | 1240886.188 | 29-DEC-16:00 | 445952.007 | 310109.712 | 84621.521 | 0 | 41026.029 | 6881 | 33960.639 | 27714.022 | 162962.637 | 0 | 0 | 0 | 5347.834 | 0 | 0
Annual Sum or Average | 24732300000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1846880000000 | 1221555.854 |  | 445952.007 | 302612.437 | 81666.15 | 0 | 41026.029 | 0 | 33960.639 | 27714.022 | 162962.637 | 0 | 0 | 0 | 5347.834 | 0 | 0
Maximum of Months | 2197650000000 | 1314190.876 |  | 445952.007 | 310109.712 | 106745.884 | 0 | 211286.067 | 6881 | 43301.83 | 27714.022 | 162962.637 | 0 | 0 | 0 | 7471.039 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 893099.22 | 131402.44 | 0 | 1024501.66
Cost per Total Building Area ($/m2) | 39.83 | 5.86 | 0 | 45.69
Cost per Net Conditioned Building Area ($/m2) | 39.83 | 5.86 | 0 | 45.69

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 45565.06 | 2032.14 | 2032.14
Net Site Energy | 45565.06 | 2032.14 | 2032.14
Total Source Energy | 119875.6 | 5346.28 | 5346.28
Net Source Energy | 119875.6 | 5346.28 | 5346.28
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 15274.14 | 0 | 0 | 0 | 0
Cooling | 3938.11 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.14 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2635.3 | 0 | 0 | 0 | 0 | 0
Pumps | 1561.42 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 959.09 | 0 | 0 | 0 | 0 | 19060.7
Humidification | 1425.04 | 0 | 0 | 0 | 0 | 530.12
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 704.42 | 0 | 0 | 0 | 4037.61
Refrigeration | 184.71 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 28228.08 | 17336.98 | 0 | 0 | 0 | 23628.42
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.54 | 0.384 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.54 | 0.384 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.54 | 0.384 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.54 | 0.384 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.54 | 0.384 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 186.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3119325.91 | 5.54
HEATSYS1 BOILER | Boiler:HotWater | 3816566.12 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2945904.91
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 615230.55 | 398403.92 | 216826.64 | 0.65 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 356798.31 | 261660.38 | 95137.92 | 0.73 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 913304.71 | 600738.62 | 312566.09 | 0.66 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1501795.52 | 982565.91 | 519229.61 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 68180.88 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 12404.6 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16646.51 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 19014.18 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16578.58 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16578.58 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16578.58 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16578.58 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 54286.57 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65226.45 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65226.45 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 55436.92 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16306.61 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16306.61 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 65226.45 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 201801.53 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29820.34 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38330.52 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17525.65 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 79632.76 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 141991.87 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 77393.42 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77393.42 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 58777.54 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29478.04 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 30035.89 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 49793.98 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 54988.9 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 267699.48 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 53345.97 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198675.88 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40354.83 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 9568.05 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5773.49 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 40623.07 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 9259.46 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7805.96 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 74576.73 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 74196.12 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15565.9 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15478 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 87298.22 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 86865.6 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13166.31 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13095.78 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61142.86 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61142.86 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15569.25 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15466.84 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 109024.76 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 108328.52 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14961.4 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14864.9 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42805.31 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 107013.27 | -
CAV_1_HEATC | Coil:Heating:Water | 42536.07 | -
CAV_2_HEATC | Coil:Heating:Water | 212283.96 | -
VAV_1_HEATC | Coil:Heating:Water | 158274.72 | -
VAV_2_HEATC | Coil:Heating:Water | 279015.95 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 19.04 | 32058.98 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.84 | 26839.26 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 29.75 | 49759.38 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 48.09 | 79669.87 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 28584.3 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21015.64 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 41577.34 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 488445.0305 | 858.7495 | 2295.6448 | 0 | 0.0095 | 142743.6954 | 207033.5702
February | 435122.7216 | 771.6138 | 2081.5426 | 0 | 0.0086 | 129433.2625 | 185036.8038
March | 479344.4943 | 864.6387 | 2373.7357 | 0 | 0.0097 | 147607.64 | 205177.6767
April | 450105.5911 | 816.5722 | 2254.7536 | 0 | 0.0092 | 140210.5647 | 193089.7324
May | 467845.2807 | 861.4099 | 2413.4921 | 0 | 0.0099 | 150086.0926 | 201856.9443
June | 471861.8411 | 884.1446 | 2518.9092 | 0 | 0.0103 | 156646.8505 | 204992.511
July | 491645.3594 | 926.5083 | 2653.7532 | 0 | 0.0108 | 165034.3315 | 214071.2609
August | 505135.8056 | 953.0231 | 2732.5995 | 0 | 0.0111 | 169938.0638 | 220045.0839
September | 455015.4094 | 843.5123 | 2378.9179 | 0 | 0.0097 | 147938.0152 | 196844.8476
October | 467007.5716 | 854.3126 | 2378.4993 | 0 | 0.0097 | 147908.118 | 200987.5897
November | 457955.4463 | 825.9734 | 2267.3529 | 0 | 0.0093 | 140992.3363 | 196014.6792
December | 478912.5513 | 847.0391 | 2278.7213 | 0 | 0.0094 | 141693.2875 | 203454.7723
Annual Sum or Average | 5648400 | 10307.4975 | 28627.9221 | 0 | 0.1172 | 1780230 | 2428610
Minimum of Months | 435122.7216 | 771.6138 | 2081.5426 | 0 | 0.0086 | 129433.2625 | 185036.8038
Maximum of Months | 505135.8056 | 953.0231 | 2732.5995 | 0 | 0.0111 | 169938.0638 | 220045.0839
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2263400000000 | 1326075.704 | 05-JAN-14:00 | 445952.007 | 302612.437 | 87262.735 | 0 | 92647.551 | 0 | 48729.015 | 38665.002 | 162962.637 | 0 | 0 | 0 | 6236.799 | 0 | 0
February | 2052350000000 | 1287071.145 | 16-FEB-16:15 | 445952.007 | 310109.712 | 87912.512 | 0 | 73249.427 | 0 | 47338.29 | 30760.568 | 162962.637 | 0 | 0 | 0 | 5160.172 | 0 | 0
March | 2340530000000 | 1334131.859 | 17-MAR-16:00 | 445952.007 | 310109.712 | 89144.857 | 0 | 116150.32 | 0 | 49822.129 | 38665.002 | 162962.637 | 0 | 0 | 0 | 5702.757 | 0 | 0
April | 2223240000000 | 1329706.111 | 20-APR-15:00 | 445952.007 | 310109.712 | 88677.574 | 0 | 106810.076 | 0 | 49539.676 | 38665.002 | 162962.637 | 0 | 0 | 0 | 5621.444 | 0 | 0
May | 2379830000000 | 1435774.993 | 31-MAY-15:00 | 445952.007 | 310109.712 | 92380.463 | 0 | 321066.518 | 0 | 58238.381 | 38665.002 | 162962.637 | 0 | 0 | 0 | 6400.273 | 0 | 0
June | 2483860000000 | 1562637.967 | 30-JUN-16:00 | 445952.007 | 310109.712 | 111291.761 | 0 | 425353.643 | 0 | 61497.909 | 38665.002 | 162962.637 | 0 | 0 | 0 | 6805.296 | 0 | 0
July | 2616850000000 | 1567084.267 | 25-JUL-15:00 | 445952.007 | 310109.712 | 106789.527 | 0 | 434444.518 | 0 | 61362.342 | 38665.002 | 162962.637 | 0 | 0 | 0 | 6798.521 | 0 | 0
August | 2694610000000 | 1625655.719 | 09-AUG-15:15 | 445952.007 | 310109.712 | 108277.429 | 0 | 490543.799 | 0 | 62450.12 | 38665.002 | 162962.637 | 0 | 0 | 0 | 6695.012 | 0 | 0
September | 2345760000000 | 1409134.289 | 27-SEP-15:15 | 445952.007 | 310109.712 | 93522.814 | 0 | 294406.257 | 0 | 57299.641 | 38665.002 | 162962.637 | 0 | 0 | 0 | 6216.219 | 0 | 0
October | 2345290000000 | 1372066.713 | 03-OCT-10:45 | 445952.007 | 310109.712 | 87060.215 | 0 | 260483.961 | 0 | 55868.62 | 38665.002 | 162962.637 | 0 | 0 | 0 | 10964.558 | 0 | 0
November | 2235630000000 | 1323641.322 | 03-NOV-13:00 | 445952.007 | 302612.437 | 91188.022 | 0 | 220674.726 | 0 | 54522.637 | 38665.002 | 162962.637 | 0 | 0 | 0 | 7063.854 | 0 | 0
December | 2246750000000 | 1301029.727 | 06-DEC-16:00 | 445952.007 | 310109.712 | 85835.522 | 0 | 71233.842 | 6881 | 47288.739 | 27551.526 | 162962.637 | 0 | 0 | 0 | 5158.162 | 0 | 0
Annual Sum or Average | 28228100000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 2052350000000 | 1287071.145 |  | 445952.007 | 302612.437 | 85835.522 | 0 | 71233.842 | 0 | 47288.739 | 27551.526 | 162962.637 | 0 | 0 | 0 | 5158.162 | 0 | 0
Maximum of Months | 2694610000000 | 1625655.719 |  | 445952.007 | 310109.712 | 111291.761 | 0 | 490543.799 | 6881 | 62450.12 | 38665.002 | 162962.637 | 0 | 0 | 0 | 10964.558 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 430561.76 | 174427.45 | 0 | 604989.21
Cost per Total Building Area ($/m2) | 19.2 | 7.78 | 0 | 26.98
Cost per Net Conditioned Building Area ($/m2) | 19.2 | 7.78 | 0 | 26.98

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 40439.73 | 1803.55 | 1803.55
Net Site Energy | 40439.73 | 1803.55 | 1803.55
Total Source Energy | 105042.19 | 4684.73 | 4684.73
Net Source Energy | 105042.19 | 4684.73 | 4684.73
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 11039.58 | 0 | 0 | 0 | 0
Cooling | 2396.15 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.12 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2901.29 | 0 | 0 | 0 | 0 | 0
Pumps | 1135.91 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 659.72 | 0 | 0 | 0 | 0 | 19207.9
Humidification | 2548.71 | 0 | 0 | 0 | 0 | 948.12
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 691.33 | 0 | 0 | 0 | 4037.61
Refrigeration | 184.23 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 27350.41 | 13089.32 | 0 | 0 | 0 | 24193.63
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.54 | 0.384 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.54 | 0.384 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.54 | 0.384 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.54 | 0.384 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.54 | 0.384 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 186.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2242834.64 | 5.54
HEATSYS1 BOILER | Boiler:HotWater | 3346089.98 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2118142.75
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 489007.11 | 301795.29 | 187211.82 | 0.62 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 309526.61 | 222866.41 | 86660.2 | 0.72 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 758645.43 | 474698.49 | 283946.94 | 0.63 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1273841.01 | 790655.02 | 483185.99 | 0.62 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 53743.78 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10760.52 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13775.78 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 17559.91 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13719.57 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13719.57 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13719.57 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13719.57 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 49534.85 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53978 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53978 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53198.78 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13494.5 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13494.5 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53978 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 191805.7 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29841.52 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 34150.68 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15431.34 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 73658.73 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 134939.6 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 64046.75 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 64046.75 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 52617.51 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29431.85 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29990.74 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 47431.75 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 50212.2 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 258042.34 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 50452.02 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198620.31 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36427.98 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 8286.36 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4452.71 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 37834.03 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 8170.44 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6582.74 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59100.37 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 58747.08 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12117.38 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12033.02 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 75478.19 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 75022.37 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10444.06 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10385.55 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 50598.64 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 50598.64 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13033 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12928.22 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 99349.7 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 98641.14 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12850.98 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12745.73 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35423.44 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 88558.59 | -
CAV_1_HEATC | Coil:Heating:Water | 24345.82 | -
CAV_2_HEATC | Coil:Heating:Water | 194832.1 | -
VAV_1_HEATC | Coil:Heating:Water | 122838.95 | -
VAV_2_HEATC | Coil:Heating:Water | 229046.23 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 19.67 | 33107.7 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.25 | 30725.08 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 31.64 | 52925.47 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 52.02 | 86174.19 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20552.48 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18424.99 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 29894.63 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 681680.7756 | 1128.5796 | 2762.2741 | 0 | 0.0109 | 2871910 | 285937.98
February | 609980.6102 | 1014.4605 | 2496.5588 | 0 | 0.0099 | 2595680 | 256312.5025
March | 690967.6885 | 1155.0333 | 2859.8685 | 0 | 0.0113 | 2973460 | 290920.1533
April | 661309.1779 | 1113.6305 | 2781.36 | 0 | 0.0109 | 2891890 | 279234.8042
May | 692252.5527 | 1174.4481 | 2958.644 | 0 | 0.0116 | 3076280 | 293154.8299
June | 651627.9447 | 1109.1841 | 2804.8165 | 0 | 0.011 | 2916360 | 276309.9582
July | 653039.7518 | 1113.0484 | 2818.8019 | 0 | 0.0111 | 2930910 | 277051.9309
August | 668563.0457 | 1139.4819 | 2885.6741 | 0 | 0.0113 | 3000440 | 283635.2742
September | 622254.7226 | 1054.1948 | 2651.3712 | 0 | 0.0104 | 2756780 | 263365.2658
October | 656610.9606 | 1103.8807 | 2751.6515 | 0 | 0.0108 | 2860990 | 277070.7071
November | 652719.0396 | 1088.171 | 2685.7268 | 0 | 0.0106 | 2792380 | 274529.2721
December | 672395.0732 | 1112.8658 | 2722.8038 | 0 | 0.0108 | 2830870 | 282009.5917
Annual Sum or Average | 7913400 | 13306.9787 | 33179.5512 | 0 | 0.1306 | 34498000 | 3339530
Minimum of Months | 609980.6102 | 1014.4605 | 2496.5588 | 0 | 0.0099 | 2595680 | 256312.5025
Maximum of Months | 692252.5527 | 1174.4481 | 2958.644 | 0 | 0.0116 | 3076280 | 293154.8299
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2276890000000 | 1320508.739 | 20-JAN-16:15 | 445952.007 | 310109.712 | 99104.767 | 0 | 60862.515 | 0 | 35534.773 | 27800.624 | 162962.637 | 0 | 0 | 0 | 5345.089 | 0 | 0
February | 2057890000000 | 1362392.621 | 13-FEB-16:30 | 445952.007 | 310109.712 | 97602.637 | 0 | 103387.917 | 0 | 38410.57 | 27800.624 | 162962.637 | 0 | 0 | 0 | 5804.263 | 0 | 0
March | 2357400000000 | 1386848.511 | 02-MAR-16:15 | 445952.007 | 310109.712 | 106499.105 | 0 | 114695.985 | 0 | 39292.287 | 27800.624 | 162962.637 | 0 | 0 | 0 | 5869.214 | 0 | 0
April | 2292730000000 | 1442878.672 | 21-APR-16:00 | 445952.007 | 310109.712 | 119735.855 | 0 | 146578.939 | 0 | 41144.174 | 27800.624 | 162962.637 | 0 | 0 | 0 | 6322.456 | 0 | 0
May | 2438910000000 | 1439649.215 | 12-MAY-16:45 | 445952.007 | 310109.712 | 121988.218 | 0 | 149492.43 | 0 | 41262.032 | 27800.624 | 162962.637 | 0 | 0 | 0 | 6296.817 | 0 | 0
June | 2312130000000 | 1480111.171 | 27-JUN-16:00 | 445952.007 | 310109.712 | 126718.043 | 0 | 178468.71 | 0 | 42544.175 | 27800.624 | 162962.637 | 0 | 0 | 0 | 6622.801 | 0 | 0
July | 2323660000000 | 1458080.695 | 31-JUL-16:00 | 445952.007 | 310109.712 | 123603.449 | 0 | 195451.098 | 0 | 42637.775 | 27800.624 | 162962.637 | 0 | 0 | 0 | 6721.929 | 0 | 0
August | 2378790000000 | 1368463.78 | 01-AUG-15:00 | 445952.007 | 310109.712 | 128475.911 | 0 | 241808.801 | 0 | 44507.263 | 27800.624 | 162962.637 | 0 | 0 | 0 | 6846.824 | 0 | 0
September | 2185610000000 | 1412857.368 | 20-SEP-16:00 | 445952.007 | 310109.712 | 127552.954 | 0 | 172676.02 | 0 | 42153.458 | 27800.624 | 162962.637 | 0 | 0 | 0 | 6502.748 | 0 | 0
October | 2268230000000 | 1375282.088 | 13-OCT-15:15 | 445952.007 | 310109.712 | 115781.954 | 0 | 143044.043 | 0 | 40697.181 | 27800.624 | 162962.637 | 0 | 0 | 0 | 6198.43 | 0 | 0
November | 2213830000000 | 1329030.645 | 13-NOV-17:00 | 445952.007 | 310109.712 | 92053.784 | 0 | 65285.152 | 6881 | 35763.845 | 27800.624 | 162962.637 | 0 | 0 | 0 | 5440.363 | 0 | 0
December | 2244350000000 | 1289999.2 | 12-DEC-15:00 | 445952.007 | 302612.437 | 95815.751 | 0 | 58945.127 | 0 | 35413.301 | 27800.624 | 162962.637 | 0 | 0 | 0 | 6199.213 | 0 | 0
Annual Sum or Average | 27350400000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 2057890000000 | 1289999.2 |  | 445952.007 | 302612.437 | 92053.784 | 0 | 58945.127 | 0 | 35413.301 | 27800.624 | 162962.637 | 0 | 0 | 0 | 5345.089 | 0 | 0
Maximum of Months | 2438910000000 | 1480111.171 |  | 445952.007 | 310109.712 | 128475.911 | 0 | 241808.801 | 6881 | 44507.263 | 27800.624 | 162962.637 | 0 | 0 | 0 | 6846.824 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 280745.12 | 93801.45 | 0 | 374546.57
Cost per Total Building Area ($/m2) | 12.52 | 4.18 | 0 | 16.7
Cost per Net Conditioned Building Area ($/m2) | 12.52 | 4.18 | 0 | 16.7

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 42811.17 | 1909.32 | 1909.32
Net Site Energy | 42811.17 | 1909.32 | 1909.32
Total Source Energy | 63043.39 | 2811.65 | 2811.65
Net Source Energy | 63043.39 | 2811.65 | 2811.65
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 15645.36 | 0 | 0 | 0 | 0
Cooling | 2051.48 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 107.96 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2588.85 | 0 | 0 | 0 | 0 | 0
Pumps | 1158.43 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 827.99 | 0 | 0 | 0 | 0 | 10637.32
Humidification | 734.8 | 0 | 0 | 0 | 0 | 273.34
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 740.33 | 0 | 0 | 0 | 4037.61
Refrigeration | 181.28 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 25067.06 | 17744.11 | 0 | 0 | 0 | 14948.27
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 5.835 | 0.54 | 0.384 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 5.835 | 0.54 | 0.384 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 5.835 | 0.54 | 0.384 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 5.835 | 0.54 | 0.384 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 5.835 | 0.54 | 0.384 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 5.835 | 0.54 | 0.384 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 5.835 | 0.54 | 0.384 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 5.835 | 0.54 | 0.384 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 5.835 | 0.54 | 0.384 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 5.835 | 0.54 | 0.384 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 5.835 | 0.54 | 0.384 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 5.835 | 0.54 | 0.384 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 186.18 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 659.24 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2341480.07 | 5.54
HEATSYS1 BOILER | Boiler:HotWater | 3603310.34 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2211303.92
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 520495.88 | 350317.59 | 170178.28 | 0.67 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 311501.41 | 236817.83 | 74683.58 | 0.76 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 753163.35 | 511431.15 | 241732.19 | 0.68 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1280453.68 | 864650.14 | 415803.54 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 47404.82 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 11445.98 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16499.34 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 16531.18 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16432.02 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16432.02 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16432.02 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16432.02 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 54248.74 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64649.81 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64649.81 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53824.9 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16162.45 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16162.45 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64649.81 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 196949.73 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29821.34 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33422.46 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15162.5 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 74462.25 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 127899.21 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 76709.21 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 76709.21 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 54148.56 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29441.68 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 30000.25 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 45672.44 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 51855.39 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 261951.91 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 51328.65 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 204670.58 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 42943.46 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 9702.19 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 6951.57 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 37261.72 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7940.97 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6333.4 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 90541.76 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 90109.27 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 17237.04 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 17132.19 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 78946.95 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 78352.05 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10807.44 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10725.41 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 60602.32 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 60602.32 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16501.65 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16388.82 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 100727.99 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 100063.09 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12626.24 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12540.83 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42426.88 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 106067.2 | -
CAV_1_HEATC | Coil:Heating:Water | 34855.93 | -
CAV_2_HEATC | Coil:Heating:Water | 206865.94 | -
VAV_1_HEATC | Coil:Heating:Water | 126299.12 | -
VAV_2_HEATC | Coil:Heating:Water | 227978.81 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.82 | 31676.03 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.75 | 26689.21 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 27.94 | 46734.88 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 46.74 | 77433.19 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21456.42 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19841.36 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 31209.47 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 196575.539 | 248.8218 | 450.2285 | 0 | 0.0019 | 5944800 | 75573.5128
February | 172767.3711 | 220.8473 | 409.5 | 0 | 0.0018 | 5407430 | 66651.9544
March | 188786.4074 | 243.3095 | 460.1442 | 0 | 0.002 | 6076550 | 73044.5597
April | 175074.9894 | 227.0342 | 435.6381 | 0 | 0.0019 | 5753180 | 67888.9103
May | 172368.6253 | 227.4443 | 453.9303 | 0 | 0.0019 | 5995440 | 67259.2623
June | 164226.2902 | 219.7822 | 452.1649 | 0 | 0.0019 | 5972630 | 64412.1477
July | 166167.9901 | 224.2254 | 469.2886 | 0 | 0.002 | 6199110 | 65371.2749
August | 169882.2574 | 230.7695 | 489.5607 | 0 | 0.002 | 6467130 | 66996.5763
September | 165412.863 | 219.9656 | 446.4641 | 0 | 0.0019 | 5897100 | 64727.1124
October | 178218.4942 | 231.3066 | 444.7109 | 0 | 0.0019 | 5873030 | 69128.8495
November | 185264.5584 | 236.4916 | 437.0093 | 0 | 0.0019 | 5770630 | 71437.8184
December | 194445.7255 | 244.9768 | 438.0137 | 0 | 0.0019 | 5783300 | 74631.6353
Annual Sum or Average | 2129190 | 2774.9749 | 5386.6534 | 0 | 0.0229 | 71140300 | 827123.614
Minimum of Months | 164226.2902 | 219.7822 | 409.5 | 0 | 0.0018 | 5407430 | 64412.1477
Maximum of Months | 196575.539 | 248.8218 | 489.5607 | 0 | 0.002 | 6467130 | 75573.5128
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2094710000000 | 1239477.943 | 03-JAN-17:00 | 445952.007 | 310109.712 | 83720.302 | 0 | 29841.997 | 6881 | 34566.715 | 7361.032 | 162962.637 | 0 | 0 | 0 | 5071.989 | 0 | 0
February | 1905370000000 | 1247065.531 | 22-FEB-11:45 | 445952.007 | 310109.712 | 82813.624 | 0 | 79303.927 | 0 | 38114.246 | 29023.364 | 162962.637 | 0 | 0 | 0 | 9634.362 | 0 | 0
March | 2141140000000 | 1251263.46 | 23-MAR-15:00 | 445952.007 | 310109.712 | 91425.499 | 0 | 75200.529 | 0 | 37819.662 | 29023.364 | 162962.637 | 0 | 0 | 0 | 5608.558 | 0 | 0
April | 2027190000000 | 1242188.044 | 14-APR-16:00 | 445952.007 | 310109.712 | 91853.059 | 0 | 112685.73 | 0 | 40053.703 | 29023.364 | 162962.637 | 0 | 0 | 0 | 5937.641 | 0 | 0
May | 2112560000000 | 1275423.449 | 05-MAY-15:00 | 445952.007 | 310109.712 | 95310.531 | 0 | 182428.782 | 0 | 43316.204 | 29023.364 | 162962.637 | 0 | 0 | 0 | 6320.212 | 0 | 0
June | 2104520000000 | 1285781.968 | 27-JUN-16:00 | 445952.007 | 310109.712 | 99376.479 | 0 | 163251.178 | 0 | 42055.348 | 29023.364 | 162962.637 | 0 | 0 | 0 | 6412.757 | 0 | 0
July | 2184320000000 | 1322414.918 | 27-JUL-16:00 | 445952.007 | 310109.712 | 105148.499 | 0 | 217357.545 | 0 | 45452.097 | 29023.364 | 162962.637 | 0 | 0 | 0 | 6409.056 | 0 | 0
August | 2278760000000 | 1319702.571 | 18-AUG-16:00 | 445952.007 | 310109.712 | 104780.005 | 0 | 215312.85 | 0 | 45088.81 | 29023.364 | 162962.637 | 0 | 0 | 0 | 6473.186 | 0 | 0
September | 2077910000000 | 1320171.4 | 01-SEP-15:00 | 445952.007 | 310109.712 | 101579.451 | 0 | 219277.326 | 0 | 44736.647 | 29023.364 | 162962.637 | 0 | 0 | 0 | 6530.256 | 0 | 0
October | 2069430000000 | 1246668.616 | 17-OCT-16:00 | 445952.007 | 310109.712 | 90441.597 | 0 | 130392.966 | 0 | 40514.458 | 29023.364 | 162962.637 | 0 | 0 | 0 | 6049.461 | 0 | 0
November | 2033340000000 | 1230070.959 | 28-NOV-17:00 | 445952.007 | 310109.712 | 84824.793 | 0 | 23832.719 | 6881 | 34016.47 | 3531.002 | 162962.637 | 0 | 0 | 0 | 4983.662 | 0 | 0
December | 2037810000000 | 1190046.701 | 07-DEC-17:00 | 445952.007 | 310109.712 | 86246.456 | 0 | 33486.351 | 6881 | 34864.024 | 29023.364 | 162962.637 | 0 | 0 | 0 | 5223.999 | 0 | 0
Annual Sum or Average | 25067100000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1905370000000 | 1190046.701 |  | 445952.007 | 310109.712 | 82813.624 | 0 | 23832.719 | 0 | 34016.47 | 3531.002 | 162962.637 | 0 | 0 | 0 | 4983.662 | 0 | 0
Maximum of Months | 2278760000000 | 1322414.918 |  | 445952.007 | 310109.712 | 105148.499 | 0 | 219277.326 | 6881 | 45452.097 | 29023.364 | 162962.637 | 0 | 0 | 0 | 9634.362 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 456415.74 | 147192.21 | 0 | 603607.95
Cost per Total Building Area ($/m2) | 20.36 | 6.56 | 0 | 26.92
Cost per Net Conditioned Building Area ($/m2) | 20.36 | 6.56 | 0 | 26.92

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 42858.23 | 1911.42 | 1911.42
Net Site Energy | 42858.23 | 1911.42 | 1911.42
Total Source Energy | 112030.05 | 4996.38 | 4996.38
Net Source Energy | 112030.05 | 4996.38 | 4996.38
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 14154.21 | 0 | 0 | 0 | 0
Cooling | 2679.88 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 107.99 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2453.53 | 0 | 0 | 0 | 0 | 0
Pumps | 1405.14 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 745.44 | 0 | 0 | 0 | 0 | 14124.1
Humidification | 1590.71 | 0 | 0 | 0 | 0 | 591.75
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 764.98 | 0 | 0 | 0 | 4037.61
Refrigeration | 181.65 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 26580.63 | 16277.6 | 0 | 0 | 0 | 18753.45
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 3.525 | 0.407 | 0.316 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 3.525 | 0.407 | 0.316 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 3.525 | 0.407 | 0.316 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 3.525 | 0.407 | 0.316 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 3.525 | 0.407 | 0.316 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 3.525 | 0.407 | 0.316 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 3.525 | 0.407 | 0.316 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 3.525 | 0.407 | 0.316 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 3.525 | 0.407 | 0.316 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 3.525 | 0.407 | 0.316 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 186.18 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 659.24 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2956781.96 | 5.54
HEATSYS1 BOILER | Boiler:HotWater | 3780331.24 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2792397.69
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 555544.37 | 355930.98 | 199613.39 | 0.64 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 332302.03 | 247379.1 | 84922.93 | 0.74 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 856929.44 | 559768.19 | 297161.25 | 0.65 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1425260.87 | 926437.88 | 498822.99 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 64199.29 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13286.91 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16366.83 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 16657.89 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16300.04 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16300.04 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16300.04 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16300.04 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 48147.36 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64130.57 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64130.57 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 52011.36 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16032.64 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16032.64 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64130.57 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 190359.3 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29822.14 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35246.5 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14449.79 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 65418.53 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 132995.37 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 76093.12 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 76093.12 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 50262.41 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 28372.89 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 28940.29 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 45189.78 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 54492.52 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 266431.06 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 53089.78 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198669.12 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 36783.18 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7743.52 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4446.44 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 33322.58 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7504.77 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6722.93 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 60115.58 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 60115.58 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12032.25 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11997.93 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 68051.35 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 67827.3 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11086.41 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11060.13 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 60115.58 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 60115.58 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12468.86 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12413.65 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 86402.79 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 86045.25 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11925.99 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11880.69 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42086.12 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 105215.31 | -
CAV_1_HEATC | Coil:Heating:Water | 94189.86 | -
CAV_2_HEATC | Coil:Heating:Water | 205698.29 | -
VAV_1_HEATC | Coil:Heating:Water | 192672.33 | -
VAV_2_HEATC | Coil:Heating:Water | 338412.1 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.13 | 28841.74 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.7 | 26593.53 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 28.14 | 47068.96 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 46.08 | 76343.25 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 27094.81 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20816.11 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 39410.8 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 849680.608 | 1449.1767 | 4067.4655 | 0 | 0.0125 | 936249.5171 | 358891.9856
February | 758173.6963 | 1302.0309 | 3682.9155 | 0 | 0.0113 | 847747.0062 | 321094.1282
March | 836221.608 | 1447.6423 | 4131.4475 | 0 | 0.0126 | 951008.6782 | 355255.151
April | 777152.9368 | 1352.0935 | 3879.8315 | 0 | 0.0118 | 893099.4093 | 330802.2518
May | 822868.9339 | 1443.2472 | 4177.7027 | 0 | 0.0127 | 961682.9829 | 351372.3832
June | 847742.0747 | 1498.6528 | 4374.6017 | 0 | 0.0133 | 1007020 | 363119.7338
July | 885260.8648 | 1569.0634 | 4592.6938 | 0 | 0.0139 | 1057230 | 379580.9368
August | 909372.527 | 1611.3033 | 4714.8087 | 0 | 0.0143 | 1085340 | 389872.0479
September | 817192.5107 | 1438.673 | 4181.1459 | 0 | 0.0127 | 962483.1274 | 349463.0567
October | 811896.4389 | 1416.7261 | 4078.3763 | 0 | 0.0124 | 938808.457 | 345991.3456
November | 784007.5282 | 1357.1438 | 3872.8367 | 0 | 0.0118 | 891479.4935 | 333062.6221
December | 831094.1103 | 1422.6449 | 4009.4744 | 0 | 0.0123 | 922908.7901 | 351535.4937
Annual Sum or Average | 9930660 | 17308.3978 | 49763.3001 | 0 | 0.1517 | 11455100 | 4230040
Minimum of Months | 758173.6963 | 1302.0309 | 3682.9155 | 0 | 0.0113 | 847747.0062 | 321094.1282
Maximum of Months | 909372.527 | 1611.3033 | 4714.8087 | 0 | 0.0143 | 1085340 | 389872.0479
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2172500000000 | 1230140.642 | 26-JAN-16:00 | 445952.007 | 310109.712 | 79934.2 | 0 | 146.958 | 6881 | 40022.43 | 0 | 162962.637 | 0 | 0 | 0 | 4912.826 | 0 | 0
February | 1967130000000 | 1213427.815 | 09-FEB-17:15 | 445952.007 | 310109.712 | 80379.104 | 0 | 7931.466 | 6881 | 40759.966 | 0 | 162962.637 | 0 | 0 | 0 | 4942.537 | 0 | 0
March | 2206740000000 | 1251564.246 | 31-MAR-16:45 | 445952.007 | 310109.712 | 84404.584 | 0 | 129739.686 | 0 | 47497.051 | 36650.22 | 162962.637 | 0 | 0 | 0 | 5973.418 | 0 | 0
April | 2072370000000 | 1298529.147 | 27-APR-16:00 | 445952.007 | 310109.712 | 86129.36 | 0 | 95871.15 | 0 | 46314.916 | 36650.22 | 162962.637 | 0 | 0 | 0 | 5722.669 | 0 | 0
May | 2231510000000 | 1357744.582 | 30-MAY-16:00 | 445952.007 | 310109.712 | 81633.264 | 0 | 261076.347 | 0 | 52914.468 | 36650.22 | 162962.637 | 0 | 0 | 0 | 6445.927 | 0 | 0
June | 2336720000000 | 1488611.718 | 08-JUN-12:00 | 445952.007 | 302612.437 | 94144.133 | 0 | 381978.872 | 0 | 56748.471 | 36650.22 | 162962.637 | 0 | 0 | 0 | 7562.942 | 0 | 0
July | 2453230000000 | 1477398.842 | 14-JUL-10:45 | 445952.007 | 310109.712 | 95776.676 | 0 | 357920.435 | 0 | 56198.461 | 36650.22 | 162962.637 | 0 | 0 | 0 | 11828.694 | 0 | 0
August | 2518460000000 | 1548291.784 | 04-AUG-15:00 | 445952.007 | 310109.712 | 102684.582 | 0 | 424831.136 | 0 | 58464.104 | 36650.22 | 162962.637 | 0 | 0 | 0 | 6637.385 | 0 | 0
September | 2233370000000 | 1405921.294 | 07-SEP-16:00 | 445952.007 | 310109.712 | 91049.563 | 0 | 296907.38 | 0 | 56114.036 | 36650.22 | 162962.637 | 0 | 0 | 0 | 6175.739 | 0 | 0
October | 2178430000000 | 1319282.498 | 31-OCT-09:00 | 445952.007 | 310109.712 | 80135.701 | 0 | 223802.019 | 0 | 52813.71 | 36650.22 | 162962.637 | 0 | 0 | 0 | 6856.492 | 0 | 0
November | 2068610000000 | 1332662.229 | 02-NOV-09:30 | 445952.007 | 310109.712 | 80473.158 | 0 | 236294.354 | 0 | 53403.14 | 36650.22 | 162962.637 | 0 | 0 | 0 | 6817 | 0 | 0
December | 2141540000000 | 1213591.104 | 05-DEC-16:00 | 445952.007 | 310109.712 | 79099.491 | 0 | 16542.998 | 6881 | 41422.29 | 0 | 162962.637 | 0 | 0 | 0 | 4947.399 | 0 | 0
Annual Sum or Average | 26580600000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1967130000000 | 1213427.815 |  | 445952.007 | 302612.437 | 79099.491 | 0 | 146.958 | 0 | 40022.43 | 0 | 162962.637 | 0 | 0 | 0 | 4912.826 | 0 | 0
Maximum of Months | 2518460000000 | 1548291.784 |  | 445952.007 | 310109.712 | 102684.582 | 0 | 424831.136 | 6881 | 58464.104 | 36650.22 | 162962.637 | 0 | 0 | 0 | 11828.694 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 725667.73 | 144327.92 | 0 | 869995.65
Cost per Total Building Area ($/m2) | 32.36 | 6.44 | 0 | 38.8
Cost per Net Conditioned Building Area ($/m2) | 32.36 | 6.44 | 0 | 38.8

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 38816.66 | 1731.17 | 1731.17
Net Site Energy | 38816.66 | 1731.17 | 1731.17
Total Source Energy | 100680.98 | 4490.23 | 4490.23
Net Source Energy | 100680.98 | 4490.23 | 4490.23
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 10509 | 0 | 0 | 0 | 0
Cooling | 1782.85 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.01 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2638.78 | 0 | 0 | 0 | 0 | 0
Pumps | 1025.19 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 550.7 | 0 | 0 | 0 | 0 | 14251.15
Humidification | 2485.09 | 0 | 0 | 0 | 0 | 924.45
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 761.82 | 0 | 0 | 0 | 4037.61
Refrigeration | 180.51 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 26187.42 | 12629.24 | 0 | 0 | 0 | 19213.21
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 3.525 | 0.407 | 0.316 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 3.525 | 0.407 | 0.316 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 3.525 | 0.407 | 0.316 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 3.525 | 0.407 | 0.316 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 3.525 | 0.407 | 0.316 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 3.525 | 0.407 | 0.316 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 3.525 | 0.407 | 0.316 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 3.525 | 0.407 | 0.316 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 3.525 | 0.407 | 0.316 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 3.525 | 0.407 | 0.316 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 186.18 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 659.24 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2115572.53 | 5.54
HEATSYS1 BOILER | Boiler:HotWater | 3296962.43 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1997955.86
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 448041.26 | 270536.39 | 177504.86 | 0.6 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 281805.86 | 206136.36 | 75669.5 | 0.73 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 722928.81 | 445062.12 | 277866.7 | 0.62 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1219206.35 | 745699.65 | 473506.7 | 0.61 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 52954.08 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10256.6 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 13750.47 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 15033.43 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13694.36 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13694.36 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13694.36 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13694.36 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 44158.3 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53878.84 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53878.84 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 49941.91 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13469.71 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13469.71 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 53878.84 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 180314.66 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29841.86 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30576.88 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12163.99 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 59429.24 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 122988.49 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 63929.09 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 63929.09 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 43214.88 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29410.03 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29969.88 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 42657.41 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 48938.88 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 255357.09 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 49705.26 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198618.42 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33737 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6515.67 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3464.27 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 30437.2 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6290.17 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5395.41 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 50505.68 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 50505.68 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9403 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9359.9 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 56936.29 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 56589.01 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 8636.39 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 8592.66 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 50505.68 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 50505.68 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10095.78 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10039.28 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 76653.39 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 76264.67 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9615.81 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9560.36 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35358.35 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 88395.89 | -
CAV_1_HEATC | Coil:Heating:Water | 70935.53 | -
CAV_2_HEATC | Coil:Heating:Water | 185725.17 | -
VAV_1_HEATC | Coil:Heating:Water | 153466.72 | -
VAV_2_HEATC | Coil:Heating:Water | 279396 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.38 | 29248.91 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.74 | 29857.19 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 29.57 | 49455.24 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 48.99 | 81161.92 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19386.29 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18154.48 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 28198.36 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 668982.5185 | 1107.1439 | 2708.5852 | 0 | 0.0107 | 2816090 | 280571.0864
February | 594644.7774 | 988.7377 | 2432.6133 | 0 | 0.0096 | 2529200 | 249847.0663
March | 665972.3703 | 1114.9369 | 2765.5408 | 0 | 0.0109 | 2875400 | 280561.6937
April | 618189.858 | 1040.184 | 2595.4904 | 0 | 0.0102 | 2698630 | 260946.0114
May | 627463.1266 | 1059.7714 | 2655.9878 | 0 | 0.0104 | 2761560 | 265251.1642
June | 605578.8664 | 1028.1344 | 2592.1757 | 0 | 0.0102 | 2695250 | 256522.2326
July | 628527.0704 | 1072.3831 | 2719.0261 | 0 | 0.0107 | 2827180 | 266761.7414
August | 635897.5119 | 1083.6507 | 2743.8328 | 0 | 0.0108 | 2852960 | 269761.6581
September | 606629.6413 | 1028.6813 | 2589.9778 | 0 | 0.0102 | 2692950 | 256845.993
October | 635515.6807 | 1070.6347 | 2675.2576 | 0 | 0.0105 | 2781570 | 268386.7648
November | 629000.914 | 1050.4292 | 2597.8744 | 0 | 0.0102 | 2701050 | 264730.1028
December | 665534.225 | 1101.0189 | 2692.3601 | 0 | 0.0106 | 2799220 | 279083.8508
Annual Sum or Average | 7581940 | 12745.706 | 31768.7222 | 0 | 0.1251 | 33031100 | 3199270
Minimum of Months | 594644.7774 | 988.7377 | 2432.6133 | 0 | 0.0096 | 2529200 | 249847.0663
Maximum of Months | 668982.5185 | 1114.9369 | 2765.5408 | 0 | 0.0109 | 2875400 | 280571.0864
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2232630000000 | 1291508.332 | 24-JAN-16:15 | 445952.007 | 310109.712 | 88622.581 | 0 | 73064.657 | 0 | 34373.137 | 26223.171 | 162962.637 | 0 | 0 | 0 | 5566.586 | 0 | 0
February | 2005180000000 | 1278401.626 | 07-FEB-14:00 | 445952.007 | 302612.437 | 88847.728 | 0 | 67862.674 | 0 | 34246.253 | 26223.171 | 162962.637 | 0 | 0 | 0 | 6393.562 | 0 | 0
March | 2279650000000 | 1370454.379 | 30-MAR-15:15 | 445952.007 | 310109.712 | 97967.573 | 0 | 107331.47 | 0 | 36726.863 | 26223.171 | 162962.637 | 0 | 0 | 0 | 5970.907 | 0 | 0
April | 2139510000000 | 1319772.256 | 27-APR-12:00 | 445952.007 | 302612.437 | 95664.802 | 0 | 95353.085 | 0 | 35984.885 | 26223.171 | 162962.637 | 0 | 0 | 0 | 6705.534 | 0 | 0
May | 2189400000000 | 1351164.669 | 19-MAY-16:00 | 445952.007 | 310109.712 | 102164.015 | 0 | 115135.285 | 0 | 37013.467 | 26223.171 | 162962.637 | 0 | 0 | 0 | 6090.55 | 0 | 0
June | 2136820000000 | 1412870.152 | 15-JUN-16:00 | 445952.007 | 310109.712 | 111802.506 | 0 | 136802.317 | 0 | 38206.118 | 26223.171 | 162962.637 | 0 | 0 | 0 | 6323.599 | 0 | 0
July | 2241420000000 | 1368040.649 | 12-JUL-15:00 | 445952.007 | 310109.712 | 115515.361 | 0 | 170152.553 | 0 | 39178.209 | 26223.171 | 162962.637 | 0 | 0 | 0 | 6625.318 | 0 | 0
August | 2261860000000 | 1373262.697 | 29-AUG-15:00 | 445952.007 | 310109.712 | 116692.353 | 0 | 177296.784 | 0 | 39555.022 | 26223.171 | 162962.637 | 0 | 0 | 0 | 6699.035 | 0 | 0
September | 2135000000000 | 1398872.567 | 13-SEP-15:00 | 445952.007 | 310109.712 | 105952.369 | 0 | 136463.412 | 0 | 37993.763 | 26223.171 | 162962.637 | 0 | 0 | 0 | 6320.977 | 0 | 0
October | 2205270000000 | 1364466.149 | 05-OCT-15:00 | 445952.007 | 310109.712 | 106026.582 | 0 | 139961.816 | 0 | 37999.579 | 26223.171 | 162962.637 | 0 | 0 | 0 | 6335.404 | 0 | 0
November | 2141430000000 | 1323815.205 | 10-NOV-13:00 | 445952.007 | 302612.437 | 92023.272 | 0 | 100797.216 | 0 | 36194.867 | 26223.171 | 162962.637 | 0 | 0 | 0 | 6729.883 | 0 | 0
December | 2219250000000 | 1275721.957 | 29-DEC-14:00 | 445952.007 | 302612.437 | 89353.215 | 0 | 61650.063 | 0 | 33917.764 | 26223.171 | 162962.637 | 0 | 0 | 0 | 6310.769 | 0 | 0
Annual Sum or Average | 26187400000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 2005180000000 | 1275721.957 |  | 445952.007 | 302612.437 | 88622.581 | 0 | 61650.063 | 0 | 33917.764 | 26223.171 | 162962.637 | 0 | 0 | 0 | 5566.586 | 0 | 0
Maximum of Months | 2279650000000 | 1412870.152 |  | 445952.007 | 310109.712 | 116692.353 | 0 | 177296.784 | 0 | 39555.022 | 26223.171 | 162962.637 | 0 | 0 | 0 | 6729.883 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 268815.52 | 90463.39 | 0 | 359278.91
Cost per Total Building Area ($/m2) | 11.99 | 4.03 | 0 | 16.02
Cost per Net Conditioned Building Area ($/m2) | 11.99 | 4.03 | 0 | 16.02

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 44056.27 | 1964.85 | 1964.85
Net Site Energy | 44056.27 | 1964.85 | 1964.85
Total Source Energy | 110141.64 | 4912.16 | 4912.16
Net Source Energy | 110141.64 | 4912.16 | 4912.16
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 15427.57 | 0 | 0 | 0 | 0
Cooling | 2411.44 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 108.08 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2459.03 | 0 | 0 | 0 | 0 | 0
Pumps | 1286.11 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 663.8 | 0 | 0 | 0 | 0 | 12562.81
Humidification | 1928.29 | 0 | 0 | 0 | 0 | 717.32
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 817.32 | 0 | 0 | 0 | 4037.61
Refrigeration | 179.94 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 26452.96 | 17603.31 | 0 | 0 | 0 | 17317.74
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 3.525 | 0.407 | 0.316 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 3.525 | 0.407 | 0.316 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 3.525 | 0.407 | 0.316 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 3.525 | 0.407 | 0.316 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 3.525 | 0.407 | 0.316 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 3.525 | 0.407 | 0.316 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 3.525 | 0.407 | 0.316 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 3.525 | 0.407 | 0.316 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 3.525 | 0.407 | 0.316 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 3.525 | 0.407 | 0.316 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 186.18 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 659.24 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2839920.86 | 5.54
HEATSYS1 BOILER | Boiler:HotWater | 3863393.24 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2682033.56
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 550082.98 | 348808.07 | 201274.91 | 0.63 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 327003.14 | 241587.56 | 85415.57 | 0.74 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 847227.93 | 547340.64 | 299887.29 | 0.65 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1388095.77 | 891508.39 | 496587.38 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 62529.26 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 13149.41 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16240.97 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 15390.26 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16174.7 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16174.7 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16174.7 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16174.7 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 45259.6 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63637.41 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63637.41 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 52011.15 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15909.35 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15909.35 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 63637.41 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 189226.77 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29823.01 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 34768.41 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14097.2 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 64367.64 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 136183.47 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 75507.97 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 75507.97 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 49228.3 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 28326.38 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 28893.66 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 41393.82 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 54254.63 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 265794.51 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 52972.56 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198669.63 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 37144.01 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7372.7 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4615.65 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 31592.98 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7079.72 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6234.89 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 60087.85 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59948.37 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12289.39 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12244.71 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 68269.14 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 67948.08 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10815.59 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10783.34 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 59653.3 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 59653.3 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 12235.94 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 12176.39 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 84591.09 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 84216.89 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11553.47 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11506.23 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 41762.48 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 104406.21 | -
CAV_1_HEATC | Coil:Heating:Water | 115836.78 | -
CAV_2_HEATC | Coil:Heating:Water | 210133.92 | -
VAV_1_HEATC | Coil:Heating:Water | 205940.86 | -
VAV_2_HEATC | Coil:Heating:Water | 366521.62 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.09 | 28775.2 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.77 | 26716.48 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 28 | 46836.92 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 45.02 | 74580.04 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 26023.94 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21273.49 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 37853.16 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 614400.0708 | 995.7898 | 1429.3427 | 0 | 0.0107 | 939109.3816 | 254521.0184
February | 538488.4862 | 888.7842 | 1304.932 | 0 | 0.0097 | 857444.8118 | 224606.0078
March | 570299.8231 | 962.2984 | 1450.43 | 0 | 0.0107 | 953144.289 | 239882.8469
April | 526809.7687 | 899.724 | 1375.018 | 0 | 0.0102 | 903634.4815 | 222622.9843
May | 549116.1342 | 949.0534 | 1469.8158 | 0 | 0.0108 | 965981.1456 | 233123.0843
June | 555180.8558 | 968.6553 | 1515.7457 | 0 | 0.0111 | 996204.4265 | 236569.5752
July | 577771.7359 | 1011.232 | 1587.716 | 0 | 0.0117 | 1043520 | 246497.9936
August | 592163.3421 | 1036.5026 | 1627.5313 | 0 | 0.012 | 1069690 | 252645.81
September | 526005.7966 | 908.879 | 1407.2005 | 0 | 0.0104 | 924828.6874 | 223289.5754
October | 537867.5381 | 917.9616 | 1401.7707 | 0 | 0.0104 | 921213.1132 | 227233.9442
November | 535707.1017 | 901.7251 | 1355.2775 | 0 | 0.0101 | 890605.6891 | 225121.6688
December | 591811.0157 | 973.216 | 1422.4995 | 0 | 0.0106 | 934679.8042 | 246505.0786
Annual Sum or Average | 6715620 | 11413.8213 | 17347.2796 | 0 | 0.1283 | 11400100 | 2832620
Minimum of Months | 526005.7966 | 888.7842 | 1304.932 | 0 | 0.0097 | 857444.8118 | 222622.9843
Maximum of Months | 614400.0708 | 1036.5026 | 1627.5313 | 0 | 0.012 | 1069690 | 254521.0184
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2179130000000 | 1224603.517 | 03-JAN-17:00 | 445952.007 | 310109.712 | 78278.942 | 0 | 1054.988 | 6881 | 38585.112 | 0 | 162962.637 | 0 | 0 | 0 | 4918.81 | 0 | 0
February | 1989640000000 | 1225990.664 | 08-FEB-17:00 | 445952.007 | 310109.712 | 80020.54 | 0 | 575.942 | 6881 | 38499.272 | 0 | 162962.637 | 0 | 0 | 0 | 4916.402 | 0 | 0
March | 2211700000000 | 1252208.154 | 31-MAR-15:00 | 445952.007 | 310109.712 | 83021.236 | 0 | 48081.648 | 0 | 42350.116 | 35201.691 | 162962.637 | 0 | 0 | 0 | 5365.799 | 0 | 0
April | 2096820000000 | 1256418.278 | 06-APR-16:00 | 445952.007 | 310109.712 | 85477.393 | 0 | 99858.395 | 0 | 44958.423 | 35201.691 | 162962.637 | 0 | 0 | 0 | 5754.645 | 0 | 0
May | 2241490000000 | 1326660.072 | 31-MAY-16:00 | 445952.007 | 310109.712 | 88572.933 | 0 | 226114.302 | 0 | 51585.674 | 35201.691 | 162962.637 | 0 | 0 | 0 | 6161.116 | 0 | 0
June | 2311620000000 | 1455247.634 | 29-JUN-16:00 | 445952.007 | 310109.712 | 103155.614 | 0 | 336622.418 | 0 | 54558.489 | 35201.691 | 162962.637 | 0 | 0 | 0 | 6685.066 | 0 | 0
July | 2421410000000 | 1503802.385 | 13-JUL-16:00 | 445952.007 | 310109.712 | 100744.039 | 0 | 386320.861 | 0 | 55901.153 | 35201.691 | 162962.637 | 0 | 0 | 0 | 6610.284 | 0 | 0
August | 2482130000000 | 1493218.966 | 25-AUG-16:00 | 445952.007 | 310109.712 | 102482.535 | 0 | 374117.898 | 0 | 55782.172 | 35201.691 | 162962.637 | 0 | 0 | 0 | 6610.314 | 0 | 0
September | 2146000000000 | 1358967.907 | 22-SEP-12:00 | 445952.007 | 302612.437 | 85474.042 | 0 | 266719.249 | 0 | 53147.241 | 35201.691 | 162962.637 | 0 | 0 | 0 | 6898.604 | 0 | 0
October | 2137610000000 | 1235850.141 | 25-OCT-15:15 | 445952.007 | 310109.712 | 83953.333 | 0 | 93888.046 | 0 | 44720.528 | 35201.691 | 162962.637 | 0 | 0 | 0 | 5631.375 | 0 | 0
November | 2066580000000 | 1255502.432 | 01-NOV-15:15 | 445952.007 | 310109.712 | 82237.673 | 0 | 83967.801 | 0 | 44127.887 | 35201.691 | 162962.637 | 0 | 0 | 0 | 5518.158 | 0 | 0
December | 2168850000000 | 1225700.482 | 20-DEC-16:30 | 445952.007 | 310109.712 | 79701.909 | 0 | 135.138 | 6881 | 38444.667 | 0 | 162962.637 | 0 | 0 | 0 | 4907.806 | 0 | 0
Annual Sum or Average | 26453000000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1989640000000 | 1224603.517 |  | 445952.007 | 302612.437 | 78278.942 | 0 | 135.138 | 0 | 38444.667 | 0 | 162962.637 | 0 | 0 | 0 | 4907.806 | 0 | 0
Maximum of Months | 2482130000000 | 1503802.385 |  | 445952.007 | 310109.712 | 103155.614 | 0 | 386320.861 | 6881 | 55901.153 | 35201.691 | 162962.637 | 0 | 0 | 0 | 6898.604 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 377651.42 | 140203.11 | 0 | 517854.53
Cost per Total Building Area ($/m2) | 16.84 | 6.25 | 0 | 23.1
Cost per Net Conditioned Building Area ($/m2) | 16.84 | 6.25 | 0 | 23.1

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 40366.63 | 1800.29 | 1800.29
Net Site Energy | 40366.63 | 1800.29 | 1800.29
Total Source Energy | 105039.64 | 4684.62 | 4684.62
Net Source Energy | 105039.64 | 4684.62 | 4684.62
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 12611.23 | 0 | 0 | 0 | 0
Cooling | 1426.97 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 107.95 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2544.75 | 0 | 0 | 0 | 0 | 0
Pumps | 929.1 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 477.27 | 0 | 0 | 0 | 0 | 10683.3
Humidification | 2490.13 | 0 | 0 | 0 | 0 | 926.33
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 826.81 | 0 | 0 | 0 | 4037.61
Refrigeration | 177.74 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 25570.17 | 14796.46 | 0 | 0 | 0 | 15647.24
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 3.525 | 0.407 | 0.316 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 3.525 | 0.407 | 0.316 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 3.525 | 0.407 | 0.316 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 3.525 | 0.407 | 0.316 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 3.525 | 0.407 | 0.316 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 3.525 | 0.407 | 0.316 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 3.525 | 0.407 | 0.316 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 3.525 | 0.407 | 0.316 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 3.525 | 0.407 | 0.316 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 3.525 | 0.407 | 0.316 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 186.18 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 659.24 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2003037.49 | 5.54
HEATSYS1 BOILER | Boiler:HotWater | 3563048.86 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1891677.28
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 437855.92 | 276517.91 | 161338.01 | 0.63 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 260472.77 | 199660.23 | 60812.54 | 0.77 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 693602.14 | 443914.86 | 249687.29 | 0.64 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1166745.32 | 740752.77 | 425992.55 | 0.63 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 50332.08 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10579.32 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 14519.34 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 13521.69 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14460.09 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14460.09 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14460.09 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 14460.09 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 42713.03 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 56891.49 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 56891.49 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 50390.24 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14222.87 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 14222.87 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 56891.49 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 182290.79 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29835.34 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31488.97 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12384.2 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 60050.94 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 115680.45 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 67503.7 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 67503.7 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 43942.68 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29414.41 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29973.83 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 39656.79 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 49496.19 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 256483.94 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 50047.44 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198632.79 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35592.93 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6564.39 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4141.35 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 29541.04 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6178.1 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 5830.62 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 55687.06 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 55554.86 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10970.82 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10932.76 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 60606.61 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 60368.19 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9145.42 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9112.85 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 53329.72 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 53329.72 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10691.77 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10637.34 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 77549.97 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77183.92 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9828.81 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9778.17 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 37335.43 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 93338.58 | -
CAV_1_HEATC | Coil:Heating:Water | 107590.26 | -
CAV_2_HEATC | Coil:Heating:Water | 197185.61 | -
VAV_1_HEATC | Coil:Heating:Water | 188584.53 | -
VAV_2_HEATC | Coil:Heating:Water | 338190.38 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.25 | 29036.62 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.94 | 28518.2 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 28.34 | 47407.15 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 46.64 | 77272.31 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18355.07 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 19619.66 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 26698.39 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 620013.2477 | 1009.8154 | 1619.4908 | 0 | 0.0114 | 38407000 | 257798.7333
February | 545167.0597 | 894.6755 | 1448.4457 | 0 | 0.0102 | 34351700 | 227331.671
March | 601283.6634 | 1006.6279 | 1669.3618 | 0 | 0.0117 | 39594300 | 252651.6528
April | 555546.5877 | 934.4203 | 1558.1569 | 0 | 0.0109 | 36957400 | 233855.1992
May | 558599.2679 | 944.9594 | 1586.2643 | 0 | 0.0111 | 37624900 | 235662.6361
June | 543509.4136 | 926.0054 | 1567.184 | 0 | 0.011 | 37173400 | 229931.8621
July | 548734.0865 | 939.5902 | 1599.1863 | 0 | 0.0112 | 37933200 | 232594.8679
August | 557319.1933 | 953.1765 | 1620.1778 | 0 | 0.0113 | 38430900 | 236126.2134
September | 532559.5637 | 904.6447 | 1525.8285 | 0 | 0.0107 | 36192000 | 225038.0616
October | 570464.5431 | 960.8211 | 1604.7315 | 0 | 0.0112 | 38062300 | 240261.3846
November | 566409.7222 | 945.0931 | 1561.1438 | 0 | 0.011 | 37027100 | 237693.4624
December | 608406.0874 | 996.5009 | 1609.3889 | 0 | 0.0114 | 38168300 | 253512.8793
Annual Sum or Average | 6808010 | 11416.3305 | 18969.3604 | 0 | 0.133 | 449922000 | 2862460
Minimum of Months | 532559.5637 | 894.6755 | 1448.4457 | 0 | 0.0102 | 34351700 | 225038.0616
Maximum of Months | 620013.2477 | 1009.8154 | 1669.3618 | 0 | 0.0117 | 39594300 | 257798.7333
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2182760000000 | 1216248.964 | 10-JAN-17:30 | 445952.007 | 310109.712 | 82815.006 | 0 | 15825.706 | 6881 | 28803.069 | 864.307 | 162962.637 | 0 | 0 | 0 | 4996.759 | 0 | 0
February | 1952290000000 | 1255000.601 | 03-FEB-17:30 | 445952.007 | 310109.712 | 88366.839 | 0 | 51413.173 | 6881 | 31340.082 | 24828.264 | 162962.637 | 0 | 0 | 0 | 5451.46 | 0 | 0
March | 2250240000000 | 1292198.275 | 29-MAR-16:00 | 445952.007 | 310109.712 | 91684.149 | 0 | 94626.568 | 0 | 34527.067 | 24828.264 | 162962.637 | 0 | 0 | 0 | 5878.405 | 0 | 0
April | 2100380000000 | 1294859.839 | 06-APR-16:00 | 445952.007 | 310109.712 | 91686.38 | 0 | 98865.753 | 0 | 34695.857 | 24828.264 | 162962.637 | 0 | 0 | 0 | 5907.753 | 0 | 0
May | 2138310000000 | 1305987.476 | 04-MAY-16:00 | 445952.007 | 310109.712 | 98311.102 | 0 | 117925.58 | 0 | 35718.711 | 24828.264 | 162962.637 | 0 | 0 | 0 | 6144.744 | 0 | 0
June | 2112650000000 | 1351290.342 | 30-JUN-15:00 | 445952.007 | 310109.712 | 105870.469 | 0 | 193679.174 | 0 | 38131.002 | 24828.264 | 162962.637 | 0 | 0 | 0 | 6810.49 | 0 | 0
July | 2155830000000 | 1357028.346 | 21-JUL-16:00 | 445952.007 | 310109.712 | 115787.566 | 0 | 191459.929 | 0 | 38826.106 | 24828.264 | 162962.637 | 0 | 0 | 0 | 6791.222 | 0 | 0
August | 2184120000000 | 1344203.502 | 18-AUG-16:00 | 445952.007 | 310109.712 | 110270.634 | 0 | 166193.315 | 0 | 37669.94 | 24828.264 | 162962.637 | 0 | 0 | 0 | 6588.967 | 0 | 0
September | 2056880000000 | 1284398.869 | 01-SEP-16:00 | 445952.007 | 310109.712 | 105278.542 | 0 | 164711.306 | 0 | 37398.852 | 24828.264 | 162962.637 | 0 | 0 | 0 | 6579.504 | 0 | 0
October | 2163170000000 | 1292652.708 | 19-OCT-16:00 | 445952.007 | 310109.712 | 90225.8 | 0 | 95446.902 | 0 | 34441.379 | 24828.264 | 162962.637 | 0 | 0 | 0 | 5856.424 | 0 | 0
November | 2104340000000 | 1237835.145 | 21-NOV-11:45 | 445952.007 | 310109.712 | 82045.134 | 0 | 61964.835 | 0 | 32235.96 | 24828.264 | 162962.637 | 0 | 0 | 0 | 9524.205 | 0 | 0
December | 2169200000000 | 1222323.267 | 12-DEC-17:00 | 445952.007 | 310109.712 | 81995.348 | 0 | 614.556 | 6881 | 27355.99 | 0 | 162962.637 | 0 | 0 | 0 | 4915.39 | 0 | 0
Annual Sum or Average | 25570200000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1952290000000 | 1216248.964 |  | 445952.007 | 310109.712 | 81995.348 | 0 | 614.556 | 0 | 27355.99 | 0 | 162962.637 | 0 | 0 | 0 | 4915.39 | 0 | 0
Maximum of Months | 2250240000000 | 1357028.346 |  | 445952.007 | 310109.712 | 115787.566 | 0 | 193679.174 | 6881 | 38826.106 | 24828.264 | 162962.637 | 0 | 0 | 0 | 9524.205 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 489837.56 | 128065.99 | 0 | 617903.55
Cost per Total Building Area ($/m2) | 21.85 | 5.71 | 0 | 27.56
Cost per Net Conditioned Building Area ($/m2) | 21.85 | 5.71 | 0 | 27.56

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 44408.21 | 1980.54 | 1980.54
Net Site Energy | 44408.21 | 1980.54 | 1980.54
Total Source Energy | 108379.39 | 4833.57 | 4833.57
Net Source Energy | 108379.39 | 4833.57 | 4833.57
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 16608.58 | 0 | 0 | 0 | 0
Cooling | 1491.83 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 107.92 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2386.67 | 0 | 0 | 0 | 0 | 0
Pumps | 1089.91 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 515.78 | 0 | 0 | 0 | 0 | 8072.85
Humidification | 2353.38 | 0 | 0 | 0 | 0 | 875.46
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 903.63 | 0 | 0 | 0 | 4037.61
Refrigeration | 175.82 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 25537.58 | 18870.62 | 0 | 0 | 0 | 12985.92
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 3.525 | 0.407 | 0.316 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 3.525 | 0.407 | 0.316 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 3.525 | 0.407 | 0.316 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 3.525 | 0.407 | 0.316 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 3.525 | 0.407 | 0.316 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 3.525 | 0.407 | 0.316 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 3.525 | 0.407 | 0.316 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 3.525 | 0.407 | 0.316 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 3.525 | 0.407 | 0.316 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 3.525 | 0.407 | 0.316 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 186.18 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 659.24 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 2550185.15 | 5.54
HEATSYS1 BOILER | Boiler:HotWater | 3768058.69 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 2408405.9
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 503943.18 | 322141.67 | 181801.51 | 0.64 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 355171.81 | 251603.56 | 103568.25 | 0.71 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 751130.54 | 488589.81 | 262540.72 | 0.65 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1290449.45 | 836748.71 | 453700.74 | 0.65 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 45541.25 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10764.98 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 15902.22 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 13786.68 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15837.33 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15837.33 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 15837.33 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 15837.33 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 43046.33 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 62310.09 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 62310.09 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 50715.73 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15577.52 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 15577.52 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 62310.09 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 183008.62 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29825.51 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31459.07 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 12576.59 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 60486.16 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 111584.03 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 73933.06 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 73933.06 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 44923.9 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29415.12 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29974.09 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 40069.97 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 51282.52 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 259902.39 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 51159.83 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 198642.03 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 35722.89 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6663.1 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 4217.55 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 29819.82 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6311.48 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6274.02 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 58409.08 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 58409.08 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10902.69 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10856.1 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 61672.37 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 61442.2 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 9736.61 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9736.61 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 58409.08 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 58409.08 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10835.62 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10774.26 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 78302.41 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 77932.18 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10028.74 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 9980.2 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 40891.43 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 102228.56 | -
CAV_1_HEATC | Coil:Heating:Water | 126989.03 | -
CAV_2_HEATC | Coil:Heating:Water | 207537.75 | -
VAV_1_HEATC | Coil:Heating:Water | 207565.35 | -
VAV_2_HEATC | Coil:Heating:Water | 375121.96 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.63 | 27991.07 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.66 | 26527.22 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 26.15 | 44014.88 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 44.5 | 73713.83 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 23368.92 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20748.53 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 33991.29 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 614923.516 | 995.715 | 1427.5542 | 0 | 0.0107 | 937929.9538 | 254649.6117
February | 545675.6367 | 890.2354 | 1288.4479 | 0 | 0.0096 | 846566.0949 | 226608.621
March | 581997.0046 | 973.2463 | 1451.5594 | 0 | 0.0108 | 953848.3529 | 243962.8326
April | 522425.2256 | 888.5523 | 1351.5799 | 0 | 0.01 | 888215.8404 | 220418.0387
May | 531914.2124 | 912.523 | 1401.6301 | 0 | 0.0103 | 921140.6721 | 225170.1652
June | 517314.188 | 895.7844 | 1390.2115 | 0 | 0.0102 | 913671.2542 | 219783.8485
July | 547867.7807 | 953.4634 | 1487.8595 | 0 | 0.0109 | 977866.76 | 233220.8806
August | 547095.9114 | 950.0144 | 1478.9068 | 0 | 0.0109 | 971974.2102 | 232691.0272
September | 502054.7514 | 862.1775 | 1325.8131 | 0 | 0.0098 | 871318.0232 | 212614.1412
October | 530457.2495 | 904.2364 | 1378.9473 | 0 | 0.0102 | 906209.4915 | 224000.2374
November | 543414.8585 | 908.8391 | 1355.6963 | 0 | 0.0101 | 890855.3334 | 227800.5868
December | 595857.0602 | 972.8261 | 1409.2898 | 0 | 0.0105 | 925967.8443 | 247517.0967
Annual Sum or Average | 6581000 | 11107.6132 | 16747.4959 | 0 | 0.1241 | 11005600 | 2768440
Minimum of Months | 502054.7514 | 862.1775 | 1288.4479 | 0 | 0.0096 | 846566.0949 | 212614.1412
Maximum of Months | 614923.516 | 995.715 | 1487.8595 | 0 | 0.0109 | 977866.76 | 254649.6117
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2176400000000 | 1219431.189 | 31-JAN-17:00 | 445952.007 | 310109.712 | 77378.939 | 0 | 268.902 | 6881 | 34610.554 | 0 | 162962.637 | 0 | 0 | 0 | 4918.448 | 0 | 0
February | 1964390000000 | 1219829.75 | 15-FEB-17:00 | 445952.007 | 310109.712 | 78622.471 | 0 | 1944.733 | 6881 | 34776.931 | 0 | 162962.637 | 0 | 0 | 0 | 4923.035 | 0 | 0
March | 2213330000000 | 1225125.194 | 06-MAR-17:00 | 445952.007 | 310109.712 | 75776.263 | 0 | 2801.697 | 6881 | 34847.038 | 0 | 162962.637 | 0 | 0 | 0 | 4923.754 | 0 | 0
April | 2061040000000 | 1241125.555 | 27-APR-15:15 | 445952.007 | 310109.712 | 83453.055 | 0 | 51250.431 | 0 | 38537.749 | 31610.327 | 162962.637 | 0 | 0 | 0 | 5454.928 | 0 | 0
May | 2137440000000 | 1292169.947 | 12-MAY-16:00 | 445952.007 | 310109.712 | 88039.036 | 0 | 86462.237 | 0 | 40771.387 | 31610.327 | 162962.637 | 0 | 0 | 0 | 5777.629 | 0 | 0
June | 2120110000000 | 1359503.164 | 14-JUN-15:15 | 445952.007 | 310109.712 | 91389.944 | 0 | 262156.435 | 0 | 48860.69 | 31610.327 | 162962.637 | 0 | 0 | 0 | 6461.411 | 0 | 0
July | 2269070000000 | 1395545.514 | 12-JUL-08:30 | 445952.007 | 302612.437 | 85729.055 | 0 | 308496.029 | 0 | 51219.58 | 31610.327 | 162962.637 | 0 | 0 | 0 | 6963.441 | 0 | 0
August | 2255390000000 | 1378969.413 | 11-AUG-16:15 | 445952.007 | 310109.712 | 97094.86 | 0 | 275228.427 | 0 | 49444.354 | 31610.327 | 162962.637 | 0 | 0 | 0 | 6567.09 | 0 | 0
September | 2021830000000 | 1358778.156 | 08-SEP-16:00 | 445952.007 | 310109.712 | 89092.633 | 0 | 262634.503 | 0 | 50221.324 | 31610.327 | 162962.637 | 0 | 0 | 0 | 6195.012 | 0 | 0
October | 2102790000000 | 1230534.387 | 25-OCT-15:15 | 445952.007 | 310109.712 | 81952.531 | 0 | 68411.772 | 0 | 39413.796 | 31610.327 | 162962.637 | 0 | 0 | 0 | 5495.979 | 0 | 0
November | 2067160000000 | 1238743.634 | 03-NOV-16:00 | 445952.007 | 310109.712 | 82400.804 | 0 | 36991.54 | 6881 | 37354.205 | 31610.327 | 162962.637 | 0 | 0 | 0 | 5376.583 | 0 | 0
December | 2148640000000 | 1209829.279 | 21-DEC-16:45 | 445952.007 | 310109.712 | 78703.276 | 0 | 1476.287 | 6881 | 34747.929 | 0 | 162962.637 | 0 | 0 | 0 | 4928.905 | 0 | 0
Annual Sum or Average | 25537600000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1964390000000 | 1209829.279 |  | 445952.007 | 302612.437 | 75776.263 | 0 | 268.902 | 0 | 34610.554 | 0 | 162962.637 | 0 | 0 | 0 | 4918.448 | 0 | 0
Maximum of Months | 2269070000000 | 1395545.514 |  | 445952.007 | 310109.712 | 97094.86 | 0 | 308496.029 | 6881 | 51219.58 | 31610.327 | 162962.637 | 0 | 0 | 0 | 6963.441 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 365287.09 | 150329.99 | 0 | 515617.08
Cost per Total Building Area ($/m2) | 16.29 | 6.7 | 0 | 23
Cost per Net Conditioned Building Area ($/m2) | 16.29 | 6.7 | 0 | 23

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 50893.54 | 2269.78 | 2269.78
Net Site Energy | 50893.54 | 2269.78 | 2269.78
Total Source Energy | 117743.51 | 5251.19 | 5251.19
Net Source Energy | 117743.51 | 5251.19 | 5251.19
Area [m2]
Total Building Area | 22422.24
Net Conditioned Building Area | 22422.24
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 23459.36 | 0 | 0 | 0 | 0
Cooling | 916.22 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 8375.01 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 107.27 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 6541.81 | 1358.42 | 0 | 0 | 0 | 0
Exterior Equipment | 2499.45 | 0 | 0 | 0 | 0 | 0
Fans | 2350.53 | 0 | 0 | 0 | 0 | 0
Pumps | 683.3 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 321.42 | 0 | 0 | 0 | 0 | 5436.97
Humidification | 3100.16 | 0 | 0 | 0 | 0 | 1153.26
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 1008.11 | 0 | 0 | 0 | 4037.61
Refrigeration | 172.47 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 25067.65 | 25825.89 | 0 | 0 | 0 | 10627.83
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3739.35 | Yes | 9120.27 | 1 | 0 | 0 | 19.37 | 37.17 | 8.07
CORRIDOR_FLR_1 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_2 | 569.03 | Yes | 2428.79 | 1 | 91.07 | 0 | 14.59 | 92.59 | 0
CORRIDOR_FLR_5 | 501.68 | Yes | 2141.32 | 1 | 78.06 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_NW_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_3 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
CORRIDOR_SE_FLR_4 | 566.71 | Yes | 2418.88 | 1 | 45.53 | 0 | 14.59 | 92.59 | 0
DINING_FLR_5 | 696.77 | Yes | 2974.04 | 1 | 227.67 | 35.76 | 27.72 | 9.29 | 10.76
ER_EXAM1_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 16.04
ER_EXAM3_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 19.51 | 0 | 41.35 | 4.65 | 16.04
ER_NURSESTN_LOBBY_FLR_1 | 1235.61 | Yes | 5273.95 | 1 | 110.58 | 30.42 | 17.89 | 69.93 | 14.63
ER_TRAUMA1_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRAUMA2_FLR_1 | 27.87 | Yes | 118.96 | 1 | 45.53 | 0 | 41.35 | 4.65 | 43.04
ER_TRIAGE_MULT4_FLR_1 | 27.87 | Yes | 118.96 | 4 | 26.02 | 0 | 41.35 | 4.65 | 29.05
ICU_FLR_2 | 617.96 | Yes | 2637.63 | 1 | 214.68 | 25.03 | 41.35 | 18.59 | 32.28
ICU_NURSESTN_LOBBY_FLR_2 | 668.77 | Yes | 2854.51 | 1 | 0 | 0 | 18.45 | 69.93 | 21.52
IC_PATROOM1_MULT5_FLR_2 | 20.9 | Yes | 89.21 | 5 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
IC_PATROOM2_FLR_2 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 41.35 | 18.59 | 32.28
IC_PATROOM3_MULT6_FLR_2 | 20.9 | Yes | 89.21 | 6 | 19.51 | 4.91 | 41.35 | 18.59 | 32.28
KITCHEN_FLR_5 | 929.03 | Yes | 3965.37 | 1 | 260.2 | 0 | 15.29 | 18.59 | 386.5657
LAB_FLR_3 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LAB_FLR_4 | 264.77 | Yes | 1129.43 | 1 | 0 | 0 | 22.65 | 18.59 | 43.04
LOBBY_RECORDS_FLR_1 | 1474.81 | Yes | 6294.92 | 1 | 409.78 | 62.63 | 15.73 | 69.93 | 1.08
NURSESTN_LOBBY_FLR_3 | 905.8 | Yes | 3866.25 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_4 | 905.8 | Yes | 3866.22 | 1 | 0 | 0 | 15.7 | 69.93 | 11.19
NURSESTN_LOBBY_FLR_5 | 1040.51 | Yes | 4441.23 | 1 | 104.08 | 0 | 15.7 | 69.93 | 11.19
OR1_FLR_2 | 55.74 | Yes | 237.91 | 1 | 65.05 | 0 | 104.9 | 18.59 | 43.04
OR2_MULT5_FLR_2 | 55.74 | Yes | 237.91 | 5 | 26.02 | 0 | 104.9 | 18.59 | 43.04
OR3_FLR_2 | 55.74 | Yes | 237.91 | 1 | 39.03 | 0 | 104.9 | 18.59 | 43.04
OR4_FLR_2 | 222.97 | Yes | 951.7 | 1 | 0 | 0 | 104.9 | 18.59 | 43.04
OR_NURSESTN_LOBBY_FLR_2 | 1012.64 | Yes | 4322.24 | 1 | 182.14 | 35.76 | 15.7 | 69.93 | 11.19
OFFICE1_FLR_5 | 69.7 | Yes | 297.5 | 1 | 71.56 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE1_MULT4_FLR_1 | 13.94 | Yes | 59.5 | 4 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
OFFICE2_MULT5_FLR_5 | 69.68 | Yes | 297.41 | 5 | 32.52 | 8.17 | 25.78 | 13.28 | 10.76
OFFICE3_FLR_5 | 69.68 | Yes | 297.41 | 1 | 71.55 | 17.98 | 25.78 | 13.28 | 10.76
OFFICE4_MULT6_FLR_5 | 13.94 | Yes | 59.5 | 6 | 13.01 | 2.96 | 25.78 | 13.28 | 10.76
PATROOM1_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM1_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM2_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM3_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_3 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM4_FLR_4 | 34.84 | Yes | 148.71 | 1 | 52.04 | 13.08 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_3 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM5_MULT10_FLR_4 | 20.9 | Yes | 89.21 | 10 | 19.51 | 4.91 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM6_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_3 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM7_MULT10_FLR_4 | 20.21 | Yes | 86.26 | 10 | 18.87 | 4.74 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_3 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PATROOM8_FLR_4 | 27.87 | Yes | 118.96 | 1 | 45.53 | 11.44 | 23.56 | 18.59 | 21.52
PHYSTHERAPY_FLR_3 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 26.93 | 18.59 | 16.14
RADIOLOGY_FLR_4 | 487.74 | Yes | 2081.82 | 1 | 0 | 0 | 23.82 | 18.59 | 53.08
Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Conditioned Total | 22422.24 |  | 88862.77 |  | 5184.43 | 845.42 | 22.0987 | 29.29 | 28.6357
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 90 | 90 | E
BASEMENT_WALL_NORTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 0 | 90 | N
BASEMENT_WALL_SOUTH | EXT-SLAB | 0.3 | 4.402 | 12.904 | 170.98 | 180 | 90 | S
BASEMENT_WALL_WEST | EXT-SLAB | 0.3 | 4.402 | 12.904 | 130.1 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 3739.35 | 0 | 180
CORRIDOR_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 45.53 | 0 | 90 | N
CORRIDOR_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 45.53 | 180 | 90 | S
CORRIDOR_FLR_5_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 52.04 | 0 | 90 | N
CORRIDOR_FLR_5_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 26.02 | 180 | 90 | S
CORRIDOR_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 501.68 | 90 | 0
CORRIDOR_NW_FLR_3_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 45.53 | 0 | 90 | N
CORRIDOR_NW_FLR_4_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 45.53 | 0 | 90 | N
CORRIDOR_SE_FLR_3_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 45.53 | 180 | 90 | S
CORRIDOR_SE_FLR_4_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 45.53 | 180 | 90 | S
DINING_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 97.57 | 90 | 90 | E
DINING_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 130.1 | 180 | 90 | S
DINING_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 696.77 | 90 | 0
ER_EXAM1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 104.08 | 180 | 90 | S
ER_EXAM3_MULT4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 78.06 | 90 | 90 | E
ER_NURSESTAT_FLR_1_WALL_1_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 110.58 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 19.51 | 90 | 90 | E
ER_EXAM2_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 26.02 | 180 | 90 | S
ER_EXAM4_FLR_1_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 19.51 | 90 | 90 | E
ER_EXAM4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 26.02 | 0 | 90 | N
ER_EXAM5_MULT4_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 104.08 | 0 | 90 | N
ICU_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 123.59 | 180 | 90 | S
ICU_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 91.09 | 270 | 90 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 97.57 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 26.02 | 0 | 90 | N
IC_PATROOM2_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 19.51 | 270 | 90 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 117.09 | 270 | 90 | W
KITCHEN_FLR_5_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 130.1 | 90 | 90 | E
KITCHEN_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 130.1 | 0 | 90 | N
KITCHEN_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 929.03 | 180 | 0
LOBBY_FLR_1_WALL_1_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 26.02 | 180 | 90 | S
LOBBY_FLR_1_WALL_1_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 227.67 | 270 | 90 | W
LOBBY_FLR_1_WALL_2_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 32.5 | 180 | 90 | S
LOBBY_FLR_1_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 123.59 | 0 | 90 | N
NURSESAT_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 104.08 | 180 | 90 | S
NURSESAT_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 1040.51 | 90 | 0
OR1_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 26.02 | 90 | 90 | E
OR1_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 39.03 | 0 | 90 | N
OR2_MULT5_FLR_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 130.1 | 90 | 90 | E
OR3_FLR_2_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 39.03 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_1_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 52.04 | 0 | 90 | N
OR_NURSESAT_FLR_2_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 130.1 | 180 | 90 | S
OFFICE1_FLR_5_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 39.03 | 180 | 90 | S
OFFICE1_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 32.53 | 270 | 90 | W
OFFICE1_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 69.7 | 180 | 0
OFFICE1_MULT4_FLR_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 52.04 | 180 | 90 | S
OFFICE2_MULT5_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 162.58 | 270 | 90 | W
OFFICE2_MULT5_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 348.39 | 180 | 0
OFFICE3_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 39.03 | 0 | 90 | N
OFFICE3_FLR_5_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 32.52 | 270 | 90 | W
OFFICE3_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 69.68 | 180 | 0
OFFICE4_MULT6_FLR_5_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 78.06 | 0 | 90 | N
OFFICE4_MULT6_FLR_5_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 83.61 | 180 | 0
PATROOM1_MULT10_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 195.15 | 180 | 90 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 195.15 | 180 | 90 | S
PATROOM2_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 19.51 | 90 | 90 | E
PATROOM2_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 32.52 | 180 | 90 | S
PATROOM2_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 19.51 | 90 | 90 | E
PATROOM2_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 32.52 | 180 | 90 | S
PATROOM3_MULT10_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 188.66 | 90 | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 188.66 | 90 | 90 | E
PATROOM4_FLR_3_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 19.51 | 90 | 90 | E
PATROOM4_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 32.52 | 0 | 90 | N
PATROOM4_FLR_4_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 19.51 | 90 | 90 | E
PATROOM4_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 32.52 | 0 | 90 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 195.15 | 0 | 90 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 195.15 | 0 | 90 | N
PATROOM6_FLR_3_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 26.02 | 180 | 90 | S
PATROOM6_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 19.51 | 270 | 90 | W
PATROOM6_FLR_4_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 26.02 | 180 | 90 | S
PATROOM6_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 19.51 | 270 | 90 | W
PATROOM7_MULT10_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 188.66 | 270 | 90 | W
PATROOM7_MULT10_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 188.66 | 270 | 90 | W
PATROOM8_FLR_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 26.02 | 0 | 90 | N
PATROOM8_FLR_3_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 19.51 | 270 | 90 | W
PATROOM8_FLR_4_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 26.02 | 0 | 90 | N
PATROOM8_FLR_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 19.51 | 270 | 90 | W
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
DINING_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 3.525 | 0.407 | 0.316 | No | DINING_FLR_5_WALL_SOUTH | 180 | S
ER_NURSESTAT_FLR_1_WALL_1_EAST_WINDOW | WINDOW-NONRES-FIXED | 30.42 | 30.42 | 3.525 | 0.407 | 0.316 | No | ER_NURSESTAT_FLR_1_WALL_1_EAST | 90 | E
ICU_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 25.03 | 25.03 | 3.525 | 0.407 | 0.316 | No | ICU_FLR_2_WALL_WEST | 270 | W
IC_PATROOM1_MULT5_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 24.53 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM1_MULT5_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM2_FLR_2_WALL_NORTH | 0 | N
IC_PATROOM2_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM2_FLR_2_WALL_WEST | 270 | W
IC_PATROOM3_MULT6_FLR_2_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 4.91 | 29.43 | 3.525 | 0.407 | 0.316 | No | IC_PATROOM3_MULT6_FLR_2_WALL_WEST | 270 | W
LOBBY_FLR_1_WALL_2_WEST | WINDOW-NONRES-FIXED | 62.63 | 62.63 | 3.525 | 0.407 | 0.316 | No | LOBBY_FLR_1_WALL_1_WEST | 270 | W
OR_NURSESAT_FLR_2_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 35.76 | 35.76 | 3.525 | 0.407 | 0.316 | No | OR_NURSESAT_FLR_2_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 3.525 | 0.407 | 0.316 | No | OFFICE1_FLR_5_WALL_SOUTH | 180 | S
OFFICE1_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | OFFICE1_FLR_5_WALL_WEST | 270 | W
OFFICE1_MULT4_FLR_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 11.86 | 3.525 | 0.407 | 0.316 | No | OFFICE1_MULT4_FLR_1_WALL_SOUTH | 180 | S
OFFICE2_MULT5_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 40.87 | 3.525 | 0.407 | 0.316 | No | OFFICE2_MULT5_FLR_5_WALL_WEST | 270 | W
OFFICE3_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 9.81 | 9.81 | 3.525 | 0.407 | 0.316 | No | OFFICE3_FLR_5_WALL_NORTH | 0 | N
OFFICE3_FLR_5_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | OFFICE3_FLR_5_WALL_WEST | 270 | W
OFFICE4_MULT6_FLR_5_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 2.96 | 17.77 | 3.525 | 0.407 | 0.316 | No | OFFICE4_MULT6_FLR_5_WALL_NORTH | 0 | N
PATROOM1_MULT10_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM1_MULT10_FLR_3_WALL_SOUTH | 180 | S
PATROOM1_MULT10_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM1_MULT10_FLR_4_WALL_SOUTH | 180 | S
PATROOM2_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_3_WALL_EAST | 90 | E
PATROOM2_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_3_WALL_SOUTH | 180 | S
PATROOM2_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_4_WALL_EAST | 90 | E
PATROOM2_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM2_FLR_4_WALL_SOUTH | 180 | S
PATROOM3_MULT10_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM3_MULT10_FLR_3_WALL_EAST | 90 | E
PATROOM3_MULT10_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM3_MULT10_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_3_WALL_EAST | 90 | E
PATROOM4_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_3_WALL_NORTH | 0 | N
PATROOM4_FLR_4_WALL_EAST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_4_WALL_EAST | 90 | E
PATROOM4_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 8.17 | 8.17 | 3.525 | 0.407 | 0.316 | No | PATROOM4_FLR_4_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM5_MULT10_FLR_3_WALL_NORTH | 0 | N
PATROOM5_MULT10_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 4.91 | 49.05 | 3.525 | 0.407 | 0.316 | No | PATROOM5_MULT10_FLR_4_WALL_NORTH | 0 | N
PATROOM6_FLR_3_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_3_WALL_SOUTH | 180 | S
PATROOM6_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_3_WALL_WEST | 270 | W
PATROOM6_FLR_4_WALL_SOUTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_4_WALL_SOUTH | 180 | S
PATROOM6_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM6_FLR_4_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM7_MULT10_FLR_3_WALL_WEST | 270 | W
PATROOM7_MULT10_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.74 | 47.41 | 3.525 | 0.407 | 0.316 | No | PATROOM7_MULT10_FLR_4_WALL_WEST | 270 | W
PATROOM8_FLR_3_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_3_WALL_NORTH | 0 | N
PATROOM8_FLR_3_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_3_WALL_WEST | 270 | W
PATROOM8_FLR_4_WALL_NORTH_WINDOW | WINDOW-RES-FIXED | 6.54 | 6.54 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_4_WALL_NORTH | 0 | N
PATROOM8_FLR_4_WALL_WEST_WINDOW | WINDOW-RES-FIXED | 4.91 | 4.91 | 3.525 | 0.407 | 0.316 | No | PATROOM8_FLR_4_WALL_WEST | 270 | W
Total or Average |  |  | 845.42 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 186.18 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 659.24 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 1921379.32 | 5.54
HEATSYS1 BOILER | Boiler:HotWater | 4149644.43 | 0.79
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 1814558.95
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 439548.09 | 298771.28 | 140776.81 | 0.68 | -
CAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 230925.7 | 191927.9 | 38997.8 | 0.83 | -
VAV_1_COOLC | Coil:Cooling:Water:DetailedGeometry | 621992.3 | 425484.43 | 196507.87 | 0.68 | -
VAV_2_COOLC | Coil:Cooling:Water:DetailedGeometry | 1136457.73 | 774792.19 | 361665.54 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 27598.39 | -
CORRIDOR_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 10471.42 | -
CORRIDOR_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 16468.09 | -
CORRIDOR_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 14030.85 | -
CORRIDOR_NW_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16400.89 | -
CORRIDOR_NW_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16400.89 | -
CORRIDOR_SE_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16400.89 | -
CORRIDOR_SE_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 16400.89 | -
DINING_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 45409.16 | -
ER_EXAM1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64527.33 | -
ER_EXAM3_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64527.33 | -
ER_NURSESTN_LOBBY_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 50743.5 | -
ER_TRAUMA1_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16131.83 | -
ER_TRAUMA2_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16131.83 | -
ER_TRIAGE_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 64527.33 | -
ICU_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 180310.25 | -
ICU_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 29821.54 | -
IC_PATROOM1_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30243.75 | -
IC_PATROOM2_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 11496.41 | -
IC_PATROOM3_MULT6_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 57236.24 | -
KITCHEN_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 108924.43 | -
LAB_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 76563.89 | -
LAB_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 76563.89 | -
LOBBY_RECORDS_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 42292.25 | -
NURSESTN_LOBBY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29403.9 | -
NURSESTN_LOBBY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 29963.79 | -
NURSESTN_LOBBY_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 38626.36 | -
OR1_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 50483.81 | -
OR2_MULT5_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 258454.91 | -
OR3_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 50656.35 | -
OR4_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 204656.1 | -
OR_NURSESTN_LOBBY_FLR_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 38974.38 | -
OFFICE1_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6693.57 | -
OFFICE1_MULT4_FLR_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 5527.07 | -
OFFICE2_MULT5_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 27798.96 | -
OFFICE3_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 6516.45 | -
OFFICE4_MULT6_FLR_5 VAV BOX REHEAT COIL | Coil:Heating:Water | 7622.96 | -
PATROOM1_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 73279.87 | -
PATROOM1_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 73008.29 | -
PATROOM2_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 13565.02 | -
PATROOM2_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 13501.16 | -
PATROOM3_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 62741.07 | -
PATROOM3_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 62471.95 | -
PATROOM4_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11701.7 | -
PATROOM4_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11709.94 | -
PATROOM5_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 60487.5 | -
PATROOM5_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 60487.5 | -
PATROOM6_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 11450.29 | -
PATROOM6_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 11395.14 | -
PATROOM7_MULT10_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 73137.79 | -
PATROOM7_MULT10_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 72856.56 | -
PATROOM8_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 10325.88 | -
PATROOM8_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 10333.07 | -
PHYSTHERAPY_FLR_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 42346.5 | -
RADIOLOGY_FLR_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 105866.25 | -
CAV_1_HEATC | Coil:Heating:Water | 183236.42 | -
CAV_2_HEATC | Coil:Heating:Water | 216856.67 | -
VAV_1_HEATC | Coil:Heating:Water | 252257.67 | -
VAV_2_HEATC | Coil:Heating:Water | 464314.14 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
DINING_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.75 | 0 | 1 | Zone Exhaust Fans
KITCHEN_FLR_5 EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.75 | 0 | 1 | Zone Exhaust Fans
CAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.47 | 27732 | 1 | Fan Energy
CAV_2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.23 | 25812.51 | 1 | Fan Energy
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 23.74 | 39966.07 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.61 | 1017.59 | 42.96 | 71176.77 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17606.78 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 22849.71 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 74.8 | 0.9
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 25609.97 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.8 | 0.23 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 632374.9273 | 718.0329 | 3014.1952 | 0 | 0.0106 | 604748.6018 | 241023.1253
February | 563400.1813 | 643.6023 | 2766.7504 | 0 | 0.0097 | 555120.5108 | 215332.2813
March | 570964.3307 | 667.298 | 3118.8592 | 0 | 0.0108 | 625833.8339 | 220540.0361
April | 498405.8958 | 594.6335 | 2976.4125 | 0 | 0.0102 | 597298.3427 | 194381.2706
May | 484550.9843 | 585.9827 | 3058.5121 | 0 | 0.0105 | 613802.3862 | 190190.2578
June | 453199.3714 | 550.5793 | 2913.1551 | 0 | 0.0099 | 584639.7762 | 178270.9233
July | 454422.0829 | 552.0264 | 2920.2121 | 0 | 0.01 | 586055.9264 | 178745.9874
August | 461687.3033 | 559.2425 | 2933.2246 | 0 | 0.01 | 588661.9745 | 181356.0454
September | 449081.5298 | 539.8592 | 2767.0692 | 0 | 0.0095 | 555302.6508 | 175771.2792
October | 511339.365 | 606.8472 | 2986.3492 | 0 | 0.0103 | 599280.7798 | 198930.3701
November | 564337.0779 | 653.5001 | 2956.0332 | 0 | 0.0103 | 593137.0297 | 217048.8027
December | 610011.2683 | 699.0548 | 3041.804 | 0 | 0.0107 | 610316.9384 | 233486.5984
Annual Sum or Average | 6253770 | 7370.6587 | 35452.5768 | 0 | 0.1226 | 7114200 | 2425080
Minimum of Months | 449081.5298 | 539.8592 | 2766.7504 | 0 | 0.0095 | 555120.5108 | 175771.2792
Maximum of Months | 632374.9273 | 718.0329 | 3118.8592 | 0 | 0.0108 | 625833.8339 | 241023.1253
| ELECTRICITYNET:FACILITY [J] | ELECTRICITYNET:FACILITY {Maximum}[W] | ELECTRICITYNET:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 2130900000000 | 1207544.072 | 25-JAN-16:15 | 445952.007 | 310109.712 | 76643.712 | 0 | 89.686 | 6881 | 26277.862 | 0 | 162962.637 | 0 | 0 | 0 | 4909.447 | 0 | 0
February | 1956030000000 | 1211848.665 | 17-FEB-17:00 | 445952.007 | 310109.712 | 77749.243 | 0 | 144.85 | 6881 | 26245.024 | 0 | 162962.637 | 0 | 0 | 0 | 4920.015 | 0 | 0
March | 2205190000000 | 1208447.62 | 22-MAR-15:00 | 445952.007 | 310109.712 | 78106.667 | 0 | 1872.504 | 0 | 26345.776 | 0 | 162962.637 | 0 | 0 | 0 | 4913.754 | 0 | 0
April | 2104650000000 | 1213591.442 | 21-APR-16:00 | 445952.007 | 310109.712 | 83651.209 | 0 | 31380.962 | 0 | 28884.11 | 14810.033 | 162962.637 | 0 | 0 | 0 | 5339.909 | 0 | 0
May | 2162800000000 | 1283473.384 | 24-MAY-15:15 | 445952.007 | 310109.712 | 88475.312 | 0 | 98050.764 | 0 | 33692.021 | 23816.086 | 162962.637 | 0 | 0 | 0 | 5924.801 | 0 | 0
June | 2060040000000 | 1301823.403 | 15-JUN-16:00 | 445952.007 | 310109.712 | 96255.187 | 0 | 131456.115 | 0 | 35357.666 | 23816.086 | 162962.637 | 0 | 0 | 0 | 6286.065 | 0 | 0
July | 2065030000000 | 1264363.357 | 20-JUL-16:00 | 445952.007 | 310109.712 | 94830.335 | 0 | 145705.014 | 0 | 35523.96 | 23816.086 | 162962.637 | 0 | 0 | 0 | 6417.578 | 0 | 0
August | 2074210000000 | 1242428.566 | 18-AUG-16:00 | 445952.007 | 310109.712 | 90621.714 | 0 | 164665.224 | 0 | 38274.417 | 23816.086 | 162962.637 | 0 | 0 | 0 | 6026.768 | 0 | 0
September | 1956670000000 | 1199824.177 | 07-SEP-15:00 | 445952.007 | 310109.712 | 82635.481 | 0 | 77056.318 | 0 | 32142.308 | 23816.086 | 162962.637 | 0 | 0 | 0 | 5777.737 | 0 | 0
October | 2111630000000 | 1196095.074 | 27-OCT-16:00 | 445952.007 | 310109.712 | 78957.64 | 0 | 1315.846 | 6881 | 26343.454 | 0 | 162962.637 | 0 | 0 | 0 | 4938.081 | 0 | 0
November | 2089980000000 | 1196967.131 | 29-NOV-17:30 | 445952.007 | 310109.712 | 77591.793 | 0 | 193.486 | 6881 | 26261.993 | 0 | 162962.637 | 0 | 0 | 0 | 4944.584 | 0 | 0
December | 2150520000000 | 1207129.422 | 13-DEC-17:00 | 445952.007 | 310109.712 | 77447.697 | 0 | 512.168 | 6881 | 26313.11 | 0 | 162962.637 | 0 | 0 | 0 | 4926.422 | 0 | 0
Annual Sum or Average | 25067600000000 | [11 empty] | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 1956030000000 | 1196095.074 |  | 445952.007 | 310109.712 | 76643.712 | 0 | 89.686 | 0 | 26245.024 | 0 | 162962.637 | 0 | 0 | 0 | 4909.447 | 0 | 0
Maximum of Months | 2205190000000 | 1301823.403 |  | 445952.007 | 310109.712 | 96255.187 | 0 | 164665.224 | 6881 | 38274.417 | 23816.086 | 162962.637 | 0 | 0 | 0 | 6417.578 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 607433.96 | 107640.02 | 0 | 715073.98
Cost per Total Building Area ($/m2) | 27.09 | 4.8 | 0 | 31.89
Cost per Net Conditioned Building Area ($/m2) | 27.09 | 4.8 | 0 | 31.89

## Picture
DOE Commercial Building Benchmark - Hospital
Second Floor
Third Floor
Forth Floor
Fifth Floor

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
ER_Exam1_Mult4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam1_Mult4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam1_Mult4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Exam1_Mult4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Trauma1_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Trauma1_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Trauma1_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Trauma1_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Exam3_Mult4_Flr_1 humidity sched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ER_Exam3_Mult4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Exam3_Mult4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Exam3_Mult4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Exam3_Mult4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Trauma2_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Trauma2_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Trauma2_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Trauma2_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
ER_Triage_Mult4_Flr_1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
ER_Triage_Mult4_Flr_1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
ER_Triage_Mult4_Flr_1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
ER_Triage_Mult4_Flr_1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR1_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR1_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR1_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
OR1_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR2_Mult5_Flr_2 humidity sched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OR2_Mult5_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR2_Mult5_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR2_Mult5_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
OR2_Mult5_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR3_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR3_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR3_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
OR3_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
OR4_Flr_2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
OR4_Flr_2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
OR4_Flr_2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
OR4_Flr_2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom1_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom1_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom1_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom1_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom2_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom2_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom2_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom2_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom3_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom3_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom3_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom3_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom4_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom4_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom4_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom4_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom5_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom5_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom5_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom5_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PhysTherapy_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PhysTherapy_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PhysTherapy_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PhysTherapy_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom6_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom6_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom6_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom6_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom7_Mult10_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom7_Mult10_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom7_Mult10_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom7_Mult10_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom8_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom8_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom8_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom8_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Lab_Flr_3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Lab_Flr_3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Lab_Flr_3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Lab_Flr_3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom1_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom1_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom1_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom1_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom2_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom2_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom2_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom2_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom3_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom3_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom3_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom3_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom4_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom4_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom4_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom4_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom5_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom5_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom5_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom5_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Radiology_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Radiology_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Radiology_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Radiology_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom6_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom6_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom6_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom6_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom7_Mult10_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom7_Mult10_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom7_Mult10_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom7_Mult10_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
PatRoom8_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
PatRoom8_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
PatRoom8_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
PatRoom8_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Lab_Flr_4 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Lab_Flr_4 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Lab_Flr_4 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Lab_Flr_4 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_5 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Kitchen_Flr_5 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Kitchen_Flr_5 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Kitchen_Flr_5 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Kitchen_Flr_5_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 70 | 70 | 80 | 70 | 50 | 50 | 80 | 90 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 690 | 4830 | 251850
CAV_1_OAminOAFracSchedule | Fraction | Through 12/31 | All | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 7.92 | 55.44 | 2890.8
CAV_2_OAminOAFracSchedule | Fraction | Through 12/31 | All | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 7.92 | 55.44 | 2890.8
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
Hours_of_operation | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | 13.64 | 82.96 | 4325.77
|  |  | Sat, WinterDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 8.36
|  |  | Sun, Hol, Other | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 6.4
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | 7.83 | 41.88 | 2183.74
|  |  | Sat, WinterDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 2.49
|  |  | Sun, Hol, Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
BLDG_SWH_EXTD_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 11.48 | 57.4 | 2993
|  |  | Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9.8
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
|  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 266.4 | 1864.8 | 97236
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
CRITICAL_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18 | 126 | 6570
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
|  |  | WinterDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 18
ADMIN_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | 13.5 | 74.75 | 3897.68
|  |  | SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | 13.5
|  |  | WinterDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 5.6
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 5.6
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.65
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 10.6 | 60.1 | 3133.79
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 5.5
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.6
CRITICAL_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6 | 130.2 | 6789
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
|  |  | WinterDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 18.6
ADMIN_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 16.4 | 102.6 | 5349.86
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 16.4
|  |  | WinterDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 11.6
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 11.6
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9 | 23.6 | 1230.57
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
|  |  | SummerDesign | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 8.4
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.35 | 0.35 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.35 | 0.35 | 0.35 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 5.9
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 2.72 | 19.04 | 992.8
CRITICAL_OCC_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1 | 119.7 | 6241.5
|  |  | SummerDesign | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
|  |  | WinterDesign | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.4 | 0.4 | 0.65 | 0.65 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.65 | 0.65 | 0.65 | 0.65 | 0.4 | 0.4 | 17.1
ADMIN_OCC_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | 12.5 | 66.7 | 3477.93
|  |  | SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | 12.5
|  |  | WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 3.75
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 3.75
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45
CRITICAL_HTGSETP_SCH | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
CRITICAL_CLGSETP_SCH | Temperature | Through 12/31 | All | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 532.8 | 3729.6 | 194472
ADMIN_HTGSETP_SCH | Temperature | Through 12/31 | WD | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6 | 3278.8 | 170966
|  |  | SummerDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6
|  |  | WinterDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
|  |  | Sat | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
|  |  | Sun, Hol, Other | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2
ADMIN_CLGSETP_SCH | Temperature | Through 12/31 | WD | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6 | 3995.6 | 208342
|  |  | SummerDesign | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6
|  |  | WinterDesign | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
|  |  | Sat | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
|  |  | Sun, Hol, Other | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600
Kitchen_HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 418.6 | 2869 | 149597.86
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 418.6
|  |  | WinterDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 401.6
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 401.6
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
Kitchen_CLGSETP_SCH | Temperature | Through 12/31 | WD | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 668 | 4748 | 247574.29
|  |  | SummerDesign | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 668
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 688
|  |  | Sats | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 688
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
OR_HTGSETP_SCH | Temperature | Through 12/31 | All | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2 | 3074.4 | 160308
OR_CLGSETP_SCH | Temperature | Through 12/31 | All | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 489.9 | 3429.3 | 178813.5
MinRelHumSetSch | Humidity | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
BLDG_OA_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 72 | 3754.29
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Kitchen_SAT_SCH | Temperature | Through 12/31 | All | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4 | 2620.8 | 136656
CAV_SAT_SCH | Temperature | Through 12/31 | All | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 266.4 | 1864.8 | 97236
VAV_SAT_SCH | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 307.2 | 2150.4 | 112128
BLDG_CAV_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6 | 109.2 | 5694
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
|  |  | WinterDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
BLDG_CAV_SCH_HUMID | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18 | 126 | 6570
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
|  |  | WinterDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
BLDG_OA_FRAC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 18 | 938.57
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0