## BuildingSummary
Building Summary Large Office pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Benchmark Large Office
| Available Fuel Types | gas, electricity
| Principal Building Activity | Office
Form
| Total Floor Area (m2) | 46320 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 12 plus basement
Window Fraction (Window to Wall Ratio)
| South | 0.38
| East | 0.38
| North | 0.38
| West | 0.38
| Total | 0.38
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor
| Floor to Ceiling Height (m) | 2.74
| Floor to Floor Height (m) | 3.96
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 11589.72
| Net Dimensions - Total Area (m2) | 6953.64
| Wall to Skin Ratio | 0.765
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 3563
| Net Dimensions - Total Area (m2) | 3563
| Roof to Skin Ratio | 0.235
Window Dimensions (m2)
| South | 1390.85
| East | 927.23
| North | 1390.85
| West | 927.23
| Total Area (m2) | 4636.16
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Basement
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 3563
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Dimensions - Total Area (m2) | 8523.53
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 92640.76
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.36496 | See Benchmark Technical Report
HVAC
| System Type | MZ-VAV | 2003 CBECS
| Heating Type | Gas boiler | 2003 CBECS
| Cooling Type | Water cooled chiller | 2003 CBECS
| Fan Control | Variable | 2003 CBECS
Service Water Heating
| SWH Type | boiler
| Fuel | gas
| Thermal Efficiency (%) | 80 | Winiarski and Halverson, 2008
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 1504.13

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Basement | Yes | 1 | 3563.11 | 8690.42 | 2.439 | 0 | 0 | 37.1613 | 95.8824 | 7.5347 | 4.842 |  |  | 10.001 |  | 958.9195 |  | 0
Perimeter_bot_ZN_3 | Yes | 1 | 313.41 | 860 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8676 | 16.1458 | 8.0701 |  |  | 10.001 |  | 168.6925 |  | 0.95205
Perimeter_bot_ZN_2 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 8.0698 |  |  | 10.001 |  | 108.7155 |  | 0.98489
Perimeter_bot_ZN_1 | Yes | 1 | 313.42 | 860.02 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8681 | 16.1458 | 8.0701 |  |  | 10.001 |  | 168.6979 |  | 0.95203
Perimeter_bot_ZN_4 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 8.0698 |  |  | 10.001 |  | 108.7155 |  | 0.98489
Core_bottom | Yes | 1 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 16.1458 | 8.07 |  | 80.629 | 10.001 |  | 1363.0177 |  | 0
Perimeter_mid_ZN_3 | Yes | 10 | 313.41 | 860 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8676 | 16.1458 | 8.0701 |  |  | 10.001 |  | 168.6925 |  | 0.95205
Perimeter_mid_ZN_2 | Yes | 10 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 8.0698 |  |  | 10.001 |  | 108.7155 |  | 0.98489
Perimeter_mid_ZN_1 | Yes | 10 | 313.42 | 860.02 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8681 | 16.1458 | 8.0701 |  |  | 10.001 |  | 168.6979 |  | 0.95203
Perimeter_mid_ZN_4 | Yes | 10 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 8.0698 |  |  | 10.001 |  | 108.7155 |  | 0.98489
Core_mid | Yes | 10 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 16.1458 | 8.07 |  | 80.629 | 10.001 |  | 1363.0177 |  | 0
Perimeter_top_ZN_3 | Yes | 1 | 313.41 | 860 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8676 | 16.1458 | 8.0701 |  |  | 10.001 |  | 168.6925 |  | 0.95205
Perimeter_top_ZN_2 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 8.0698 |  |  | 10.001 |  | 108.7155 |  | 0.98489
Perimeter_top_ZN_1 | Yes | 1 | 313.42 | 860.02 | 2.744 | 200.6102 | 115.9001 | 18.5806 | 16.8681 | 16.1458 | 8.0701 |  |  | 10.001 |  | 168.6979 |  | 0.95203
Perimeter_top_ZN_4 | Yes | 1 | 201.98 | 554.22 | 2.7439 | 133.7401 | 77.2701 | 18.5806 | 10.8705 | 16.1458 | 8.0698 |  |  | 10.001 |  | 108.7155 |  | 0.98489
Core_top | Yes | 1 | 2532.32 | 6948.69 | 2.744 | 0 | 0 | 18.5806 | 136.2882 | 16.1458 | 8.07 |  | 80.629 | 10.001 |  | 1363.0177 |  | 0
Groundfloor_plenum | No | 1 | 3563.11 | 4344.14 | 1.2192 | 297.1103 | [11 empty] | 0.27914
Midfloor_plenum | No | 10 | 3563.11 | 4344.14 | 1.2192 | 297.1103 | [11 empty] | 0.27914
Topfloor_plenum | No | 1 | 3563.11 | 4344.14 | 1.2192 | 297.1103 | [11 empty] | 3.6267
Total Conditioned Zones |  |  | 46320.43 | 178145.9 |  | 11589.7308 | 4636.0843 |  | 2397.06 |  |  |  | 967.5482 |  |  | 23972.9872
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement | Basement
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| COOLSYS1 CHILLER | 4840.7859 | 4738.1913 | 4763.1204 | 4703.2931 | 4059.8984 | 4561.0382 | 3671.7211 | 4693.571 | 3655.8051 | 3940.4869 | 4422.3962 | 3174.8222 | 4129.9896 | 3174.744 | 3597.9063 | 3282.1812
Heating (kW)
| HEATSYS1 BOILER | 3283.3577 | 3551.3632 | 3541.5274 | 3681.636 | 3135.6487 | 3715.5504 | 3199.1763 | 3840.6572 | 3308.3514 | 3565.4548 | 3928.6223 | 3205.2116 | 3883.1612 | 3568.1503 | 3788.8845 | 4369.8599
HVAC Efficiency
| Air Conditioning (COP) | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11 | 5.11
| Heating Efficiency (%) | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76
HVAC Control - Economizer
| VAV_1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| VAV_5_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| VAV_1_FAN | 18.97 | 20.09 | 20.82 | 20.82 | 18.67 | 22.36 | 18.51 | 20.51 | 21.73 | 19.59 | 18.46 | 18.63 | 17.21 | 18.19 | 16.77 | 16.78
| VAV_2_FAN | 219.67 | 222.72 | 246.17 | 231.87 | 212.18 | 262.22 | 211.18 | 227.04 | 246.61 | 225.35 | 217.96 | 216.16 | 204.97 | 212.38 | 198.19 | 200.9
| VAV_3_FAN | 21.34 | 21.27 | 24.31 | 22.17 | 18.99 | 25.08 | 18.07 | 21.4 | 21.27 | 20.09 | 20.46 | 17.73 | 19.26 | 18.08 | 17.39 | 17.12
| VAV_5_FAN | 5.64 | 5.47 | 4.03 | 5.4 | 5.11 | 4.46 | 3.05 | 5 | 4.79 | 3.7 | 5.64 | 4.66 | 4.74 | 4.27 | 3.63 | 2.45
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.084435 | 0.10797 | 0.078549 | 0.096267 | 0.057025 | 0.097398 | 0.15125 | 0.069628 | 0.036965 | 0.072686 | 0.087242 | 0.036967 | 0.062089 | 0.078137 | 0.061903 | 0.099818
| Total Cost ($/m2) | 12.37 | 15.03 | 10.4 | 12.6 | 6.76 | 12.17 | 16.13 | 8.9 | 4.18 | 7.67 | 9.76 | 3.91 | 6.79 | 8.07 | 6.36 | 10.03
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011354 | 0.0080595 | 0.0082312 | 0.009667 | 0.0085481 | 0.0076816 | 0.008549 | 0.0097026 | 0.0068866 | 0.0084103 | 0.0083665 | 0.0069046 | 0.0078772 | 0.0080753 | 0.0078669 | 0.0041276
| Total Cost ($/m2) | 0.21 | 0.64 | 0.49 | 1.37 | 0.48 | 0.74 | 0.95 | 2.2 | 0.97 | 2.01 | 2.1 | 1.11 | 2.41 | 1.95 | 2.9 | 2.53
Total Utility Costs
| Cost Intensity ($/m2) | 12.58 | 15.67 | 10.89 | 13.97 | 7.24 | 12.91 | 17.08 | 11.1 | 5.14 | 9.68 | 11.86 | 5.03 | 9.2 | 10.02 | 9.26 | 12.57
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 1684072.2222 | 1367422.2222 | 1054219.4444 | 984819.4444 | 610961.1111 | 793202.7778 | 235991.6667 | 845705.5556 | 446047.2222 | 214936.1111 | 450555.5556 | 268966.6667 | 378369.4444 | 187622.2222 | 176669.4444 | 95158.3333
| Interior Lighting | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222 | 2052722.2222
| Exterior Lighting | 13458.3333 | 13452.7778 | 13450 | 13447.2222 | 13438.8889 | 13436.1111 | 13441.6667 | 13433.3333 | 13438.8889 | 13413.8889 | 13436.1111 | 13427.7778 | 13427.7778 | 13425 | 13416.6667 | 13333.3333
| Interior Equipment | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222 | 1605172.2222
| Exterior Equipment | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111 | 526411.1111
| Fans | 214397.2222 | 212441.6667 | 257252.7778 | 223155.5556 | 184175 | 270116.6667 | 176366.6667 | 229186.1111 | 263969.4444 | 215605.5556 | 215797.2222 | 212827.7778 | 208627.7778 | 211272.2222 | 205427.7778 | 219588.8889
| Pumps | 381930.5556 | 380000 | 344738.8889 | 387538.8889 | 272705.5556 | 297502.7778 | 187002.7778 | 410627.7778 | 186569.4444 | 153152.7778 | 195780.5556 | 133088.8889 | 174186.1111 | 116061.1111 | 116433.3333 | 101008.3333
| Heat Rejection | 309052.7778 | 290658.3333 | 278777.7778 | 269861.1111 | 226297.2222 | 231080.5556 | 143747.2222 | 238244.4444 | 138072.2222 | 107983.3333 | 121441.6667 | 90233.3333 | 107016.6667 | 72455.5556 | 62497.2222 | 43194.4444
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 6787216.6667 | 6448280.5556 | 6132741.6667 | 6063127.7778 | 5491877.7778 | 5789644.4444 | 4940855.5556 | 5921502.7778 | 5232400 | 4889394.4444 | 5181313.8889 | 4902850 | 5065930.5556 | 4785141.6667 | 4758747.2222 | 4656588.8889
Gas (MJ)
| Heating | 688690 | 3460310 | 2595290 | 6344320 | 2385740 | 4223400 | 4872050 | 10228300 | 6233250 | 10767690 | 11356500 | 7182260 | 13847160 | 10891740 | 16715480 | 28029560
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 172420 | 206320 | 186720 | 239030 | 232770 | 210250 | 260770 | 264760 | 259880 | 278220 | 287360 | 286180 | 306880 | 310420 | 339080 | 377970
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 861110 | 3666620 | 2782010 | 6583350 | 2618510 | 4433660 | 5132820 | 10493060 | 6493130 | 11045900 | 11643860 | 7468440 | 14154040 | 11202160 | 17054550 | 28407530
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 25295090 | 26880430 | 24859880 | 28410620 | 22389270 | 25276370 | 22919900 | 31810460 | 25329770 | 28647730 | 30296590 | 25118700 | 32391400 | 28428670 | 34186040 | 45171240
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 130.8854 | 106.2755 | 81.9335 | 76.5397 | 47.4836 | 61.6474 | 18.3412 | 65.7279 | 34.6666 | 16.7047 | 35.017 | 20.904 | 29.4067 | 14.5819 | 13.7307 | 7.3957
| Interior Lighting (elec) | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367 | 159.5367
| Exterior Lighting (elec) | 1.046 | 1.0455 | 1.0453 | 1.0451 | 1.0445 | 1.0442 | 1.0447 | 1.044 | 1.0445 | 1.0425 | 1.0442 | 1.0436 | 1.0436 | 1.0434 | 1.0427 | 1.0363
| Interior Equipment (elec) | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533 | 124.7533
| Exterior Equipment (elec) | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124 | 40.9124
| Fans (elec) | 16.6629 | 16.5109 | 19.9936 | 17.3436 | 14.314 | 20.9934 | 13.7071 | 17.8122 | 20.5156 | 16.7568 | 16.7717 | 16.5409 | 16.2145 | 16.42 | 15.9658 | 17.0664
| Pumps (elec) | 29.6835 | 29.5334 | 26.793 | 30.1194 | 21.1946 | 23.1218 | 14.5338 | 31.9138 | 14.5001 | 11.903 | 15.216 | 10.3436 | 13.5377 | 9.0202 | 9.0491 | 7.8503
| Heat Rejection (elec) | 24.0194 | 22.5898 | 21.6665 | 20.9735 | 17.5877 | 17.9595 | 11.172 | 18.5163 | 10.7309 | 8.3924 | 9.4384 | 7.0129 | 8.3173 | 5.6312 | 4.8573 | 3.3571
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 527.4996 | 501.1576 | 476.634 | 471.2237 | 426.8264 | 449.9687 | 384.0012 | 460.2166 | 406.6599 | 380.0016 | 402.6895 | 381.0474 | 393.7219 | 371.8992 | 369.8478 | 361.9081
Gas (MJ/m2)
| Heating (gas) | 14.868 | 74.7038 | 56.0291 | 136.9661 | 51.5052 | 91.178 | 105.1816 | 220.8164 | 134.5682 | 232.4612 | 245.1729 | 155.0562 | 298.9431 | 235.1393 | 360.8666 | 605.1237
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 3.7223 | 4.4542 | 4.0311 | 5.1604 | 5.0252 | 4.539 | 5.6297 | 5.7158 | 5.6105 | 6.0064 | 6.2037 | 6.1783 | 6.6252 | 6.7016 | 7.3203 | 8.1599
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 18.5903 | 79.1578 | 60.0602 | 142.1264 | 56.5304 | 95.7173 | 110.8113 | 226.5323 | 140.1787 | 238.4674 | 251.3766 | 161.2344 | 305.5683 | 241.8408 | 368.1867 | 613.2836
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 546.0899 | 580.3154 | 536.6942 | 613.3503 | 483.3568 | 545.6857 | 494.8124 | 686.7487 | 546.8386 | 618.4692 | 654.0661 | 542.2818 | 699.2905 | 613.74 | 738.0345 | 975.1915
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 1629.9615 | 1554.5383 | 1446.767 | 1422.6933 | 1398.7919 | 1354.4673 | 1240.5004 | 1362.5279 | 1280.2671 | 1187.4036 | 1191.8898 | 1239.4103 | 1185.736 | 1176.4955 | 1179.5531 | 1179.159
| Feb | 1669.1657 | 1515.5292 | 1479.5782 | 1427.5968 | 1381.369 | 1409.2869 | 1372.7082 | 1344.3363 | 1363.8869 | 1276.1006 | 1192.0344 | 1173.6784 | 1185.954 | 1185.2623 | 1165.3711 | 1180.4019
| Mar | 1671.9502 | 1545.9798 | 1554.7187 | 1464.4705 | 1406.2098 | 1442.7071 | 1313.6645 | 1467.8585 | 1363.907 | 1347.9712 | 1372.1277 | 1307.4395 | 1224.9741 | 1306.4822 | 1177.8872 | 1162.8528
| Apr | 1710.274 | 1608.8791 | 1537.0695 | 1541.4372 | 1453.8006 | 1542.6076 | 1367.2872 | 1465.2384 | 1426.9964 | 1309.0596 | 1396.3836 | 1343.289 | 1357.7003 | 1286.3703 | 1217.8368 | 1172.9221
| May | 1807.8799 | 1797.067 | 1637.1177 | 1658.3758 | 1539.5589 | 1584.3932 | 1376.4095 | 1625.7222 | 1491.9042 | 1426.3416 | 1618.3686 | 1402.8245 | 1500.4407 | 1330.4852 | 1347.9908 | 1299.6709
| Jun | 1910.7895 | 1776.0986 | 1838.1477 | 1721.1217 | 1496.4621 | 1743.3368 | 1412.949 | 1789.2188 | 1625.1976 | 1448.2503 | 1657.5531 | 1482.3161 | 1662.9866 | 1488.7351 | 1506.9055 | 1386.4576
| Jul | 1863.5805 | 1911.1032 | 1852.642 | 1815.9867 | 1552.9321 | 1770.658 | 1447.1015 | 1847.15 | 1620.8439 | 1510.4377 | 1678.7376 | 1514.9338 | 1694.2929 | 1486.0212 | 1624.0374 | 1385.986
| Aug | 1902.6806 | 1859.4919 | 1818.9799 | 1758.8054 | 1708.747 | 1765.238 | 1394.3614 | 1899.3108 | 1653.1273 | 1489.3056 | 1765.7943 | 1508.9409 | 1665.4973 | 1455.0765 | 1527.7303 | 1379.3369
| Sep | 1827.9242 | 1833.7933 | 1801.3057 | 1687.4281 | 1575.056 | 1714.126 | 1535.1798 | 1602.7152 | 1533.9227 | 1497.8693 | 1587.0059 | 1428.0674 | 1558.8234 | 1389.0343 | 1487.751 | 1248.2534
| Oct | 1820.8109 | 1677.497 | 1638.1032 | 1556.3742 | 1494.7348 | 1566.6522 | 1414.4317 | 1550.0093 | 1450.7608 | 1377.593 | 1487.7606 | 1379.5917 | 1383.3777 | 1342.6944 | 1290.2489 | 1176.8026
| Nov | 1675.0101 | 1604.5907 | 1525.5938 | 1438.3527 | 1405.2346 | 1409.1517 | 1335.4324 | 1495.9098 | 1337.3084 | 1283.8313 | 1500.472 | 1264.8975 | 1332.1792 | 1189.0294 | 1179.2968 | 1180.4149
| Dec | 1623.0476 | 1540.3699 | 1441.5511 | 1442.4721 | 1383.2306 | 1389.0441 | 1225.2943 | 1312.393 | 1233.9617 | 1186.8524 | 1191.7841 | 1173.8532 | 1185.4094 | 1173.6822 | 1178.0338 | 1177.1413
Time of Peak Electrical Demand
| Jan | 23-JAN-16:10 | 03-JAN-08:00 | 26-JAN-16:10 | 23-JAN-16:10 | 25-JAN-16:10 | 18-JAN-16:10 | 06-JAN-16:10 | 09-JAN-08:00 | 26-JAN-16:10 | 09-JAN-08:00 | 17-JAN-08:30 | 27-JAN-16:10 | 31-JAN-08:09 | 10-JAN-08:09 | 10-JAN-08:50 | 05-JAN-08:30
| Feb | 22-FEB-16:10 | 15-FEB-16:10 | 28-FEB-16:10 | 22-FEB-08:09 | 13-FEB-11:00 | 07-FEB-16:10 | 15-FEB-16:10 | 15-FEB-16:10 | 14-FEB-16:10 | 21-FEB-16:10 | 27-FEB-08:09 | 09-FEB-08:09 | 13-FEB-08:00 | 02-FEB-16:10 | 03-FEB-08:09 | 15-FEB-08:39
| Mar | 13-MAR-15:30 | 28-MAR-15:09 | 17-MAR-15:39 | 28-MAR-15:50 | 31-MAR-15:09 | 31-MAR-15:09 | 20-MAR-15:09 | 09-MAR-16:10 | 02-MAR-16:10 | 29-MAR-15:09 | 31-MAR-15:00 | 30-MAR-15:09 | 23-MAR-15:00 | 30-MAR-15:09 | 20-MAR-07:30 | 24-MAR-07:10
| Apr | 04-APR-15:00 | 20-APR-15:09 | 03-APR-15:30 | 20-APR-15:00 | 11-APR-15:00 | 21-APR-15:09 | 13-APR-15:09 | 04-APR-15:00 | 21-APR-15:50 | 14-APR-15:09 | 10-APR-08:00 | 26-APR-15:00 | 14-APR-15:00 | 06-APR-15:30 | 05-APR-07:00 | 14-APR-07:30
| May | 15-MAY-15:00 | 18-MAY-15:30 | 30-MAY-15:00 | 31-MAY-15:00 | 30-MAY-07:49 | 31-MAY-15:00 | 25-MAY-15:50 | 31-MAY-15:50 | 31-MAY-15:00 | 04-MAY-15:09 | 30-MAY-08:00 | 24-MAY-15:00 | 31-MAY-15:09 | 16-MAY-15:00 | 31-MAY-15:00 | 30-MAY-15:09
| Jun | 27-JUN-15:50 | 29-JUN-15:00 | 28-JUN-15:00 | 08-JUN-15:00 | 28-JUN-15:00 | 27-JUN-15:00 | 16-JUN-15:00 | 30-JUN-15:00 | 29-JUN-15:30 | 28-JUN-15:09 | 08-JUN-12:00 | 27-JUN-15:30 | 29-JUN-15:00 | 26-JUN-15:20 | 14-JUN-15:50 | 21-JUN-15:00
| Jul | 13-JUL-15:39 | 18-JUL-15:00 | 11-JUL-15:00 | 03-JUL-15:00 | 20-JUL-15:09 | 26-JUL-15:09 | 03-JUL-15:09 | 25-JUL-15:30 | 03-JUL-15:30 | 31-JUL-15:00 | 13-JUL-15:09 | 18-JUL-15:09 | 13-JUL-15:00 | 21-JUL-15:00 | 07-JUL-07:00 | 03-JUL-15:00
| Aug | 21-AUG-15:09 | 31-AUG-15:00 | 02-AUG-15:20 | 14-AUG-15:30 | 09-AUG-15:09 | 02-AUG-15:09 | 14-AUG-15:09 | 09-AUG-15:09 | 01-AUG-15:09 | 18-AUG-15:09 | 04-AUG-15:50 | 30-AUG-15:30 | 25-AUG-15:00 | 09-AUG-15:00 | 11-AUG-15:00 | 15-AUG-15:09
| Sep | 11-SEP-15:09 | 15-SEP-15:20 | 12-SEP-15:09 | 05-SEP-15:00 | 07-SEP-08:00 | 01-SEP-15:09 | 28-SEP-15:09 | 13-SEP-15:09 | 13-SEP-15:09 | 01-SEP-15:50 | 07-SEP-12:00 | 01-SEP-15:00 | 22-SEP-15:00 | 01-SEP-15:00 | 07-SEP-15:30 | 07-SEP-15:00
| Oct | 06-OCT-15:50 | 30-OCT-15:09 | 03-OCT-12:50 | 20-OCT-15:00 | 05-OCT-15:00 | 03-OCT-15:09 | 13-OCT-15:09 | 12-OCT-15:09 | 11-OCT-15:50 | 17-OCT-15:09 | 31-OCT-07:00 | 05-OCT-15:30 | 06-OCT-15:09 | 06-OCT-15:20 | 27-OCT-15:09 | 24-OCT-07:10
| Nov | 07-NOV-16:10 | 27-NOV-16:00 | 13-NOV-16:10 | 21-NOV-16:10 | 09-NOV-16:10 | 10-NOV-16:10 | 16-NOV-16:10 | 03-NOV-15:09 | 01-NOV-15:09 | 03-NOV-15:09 | 02-NOV-07:00 | 10-NOV-13:00 | 02-NOV-15:09 | 21-NOV-16:10 | 27-NOV-08:39 | 03-NOV-07:00
| Dec | 15-DEC-16:10 | 19-DEC-16:10 | 11-DEC-16:10 | 26-DEC-08:00 | 19-DEC-13:20 | 05-DEC-16:10 | 20-DEC-08:09 | 08-DEC-08:00 | 05-DEC-16:10 | 04-DEC-08:09 | 11-DEC-08:00 | 28-DEC-08:20 | 08-DEC-08:50 | 28-DEC-08:39 | 07-DEC-08:50 | 18-DEC-08:50
Source Energy
| Total Source Energy (GJ) | 81987.86 | 88316.5 | 72870.26 | 80615.93 | 64049.92 | 79395.96 | 60656.05 | 87689.46 | 69590.48 | 42724.5 | 78857.69 | 66719.09 | 78138 | 72112.1 | 77504.5 | 90901.01
| Total Source Energy (MJ/m2) | 1770.02 | 1906.64 | 1573.18 | 1740.4 | 1382.76 | 1714.06 | 1309.49 | 1893.11 | 1502.37 | 922.37 | 1702.44 | 1440.38 | 1686.9 | 1556.81 | 1673.23 | 1962.44
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 25887.68 | 21772.59 | 33790.99 | 18459.14 | 12271.82 | 29462.28 | 6173.3 | 16286.46 | 14916.06 | 5502.19 | 8876.16 | 9113.73 | 7429.4 | 6313.89 | 3766.23 | 2627.32
| Water Systems | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13 | 1504.13
| Total Building | 27391.81 | 23276.72 | 35295.12 | 19963.28 | 13775.95 | 30966.41 | 7677.44 | 17790.59 | 16420.19 | 7006.32 | 10380.29 | 10617.86 | 8933.53 | 7818.02 | 5270.36 | 4131.45
Emissions
| Carbon Equivalent (kg) | 1876920 | 2217010 | 1901490 | 1986380 | 689031.6075 | 2032650 | 669975.7661 | 1787170 | 2254510 | 555302.3649 | 2972380 | 2137480 | 1989270 | 1950680 | 1936430 | 1822570
| CO2 (kg) | 4355020 | 5588240 | 4498700 | 4581850 | 1849960 | 4855990 | 1809030 | 4130140 | 5318700 | 1421440 | 6980280 | 5055830 | 4735050 | 4650810 | 4643760 | 4762370
| NOX (kg) | 7642.1428 | 7267.571 | 7490.1436 | 8496.6156 | 1590.2529 | 7794.3772 | 1562.0501 | 7661.1018 | 9045.4435 | 1881.6841 | 12156.486 | 8541.2123 | 7964.4276 | 7749.4918 | 7659.276 | 5455.8154
| SO2 (kg) | 29052.2369 | 30759.2787 | 24661.7283 | 21283.3441 | 15981.4082 | 31848.862 | 14378.6727 | 21618.6619 | 22850.5874 | 3782.0719 | 34921.0402 | 21411.7658 | 11960.202 | 12779.9033 | 11235.9749 | 23711.5071
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.1325 | 0.0868 | 0.0672 | 0.0783 | 0.0074 | 0.0601 | 0.007 | 0.0882 | 0.0897 | 0.0159 | 0.1065 | 0.0842 | 0.0887 | 0.0898 | 0.0837 | 0.0833
| Water for Electricity (m3) | 3595.58 | 10492.1 | 182169 | 37855.7 | 96425.1 | 158833 | 86750.3 | 1344.4 | 23759.3 | 49954 | 8038.5 | 22262.9 | 7859.49 | 303111 | 7382.91 | 4757.54

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 25295.09 | 546.09 | 546.09
Net Site Energy | 25295.09 | 546.09 | 546.09
Total Source Energy | 81987.86 | 1770.02 | 1770.02
Net Source Energy | 81987.86 | 1770.02 | 1770.02
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 688.69 | 0 | 0 | 0 | 0
Cooling | 6062.66 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.45 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 771.83 | 0 | 0 | 0 | 0 | 0
Pumps | 1374.95 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1112.59 | 0 | 0 | 0 | 0 | 25887.68
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 172.42 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 24433.98 | 861.11 | 0 | 0 | 0 | 27391.81
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 1390.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4840785.92 | 5.11
HEATSYS1 BOILER | Boiler:HotWater | 3283357.73 | 0.76
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 4630481.71
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 443517.83 | 309304.93 | 134212.9 | 0.7 | -
VAV_2_COOLC | Coil:Cooling:Water | 5103642.64 | 3574497.11 | 1529145.54 | 0.7 | -
VAV_3_COOLC | Coil:Cooling:Water | 496499.78 | 347402.25 | 149097.53 | 0.7 | -
VAV_5_COOLC | Coil:Cooling:Water | 132220.05 | 91244.17 | 40975.88 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 69180.28 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 120463.85 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1526183.57 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 141514.16 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21556.59 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31322.05 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 23410.71 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 36044.13 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 223744.5 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 322206.39 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 243497.5 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 379904.69 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23889.09 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30672.28 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26485 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 39246.76 | -
VAV_1_HEATC | Coil:Heating:Water | 556.25 | -
VAV_2_HEATC | Coil:Heating:Water | 0 | -
VAV_3_HEATC | Coil:Heating:Water | 0 | -
VAV_5_HEATC | Coil:Heating:Water | 22832.51 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.97 | 31936.65 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 219.67 | 362006.19 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 21.34 | 35916.43 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.64 | 10576.62 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 44359.1 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18596.12 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 65352.79 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 345993.6555 | 601.4759 | 2263.4876 | 0 | 0.0103 | 280131.0427 | 148547.7788
February | 312563.2341 | 545.799 | 2063.9793 | 0 | 0.0094 | 255441.6034 | 134439.2168
March | 359431.3778 | 629.3043 | 2386.5649 | 0 | 0.0109 | 295366.6119 | 154764.801
April | 341843.3306 | 601.0369 | 2289.6668 | 0 | 0.0104 | 283376.1865 | 147444.8324
May | 383482.7178 | 674.7552 | 2572.5577 | 0 | 0.0117 | 318388.0162 | 165455.6504
June | 385877.5538 | 679.6068 | 2593.6432 | 0 | 0.0118 | 320998.0968 | 166552.8228
July | 389157.6415 | 685.4857 | 2616.493 | 0 | 0.0119 | 323826.1533 | 167978.8009
August | 411214.8293 | 724.2813 | 2764.343 | 0 | 0.0126 | 342124.5249 | 177493.981
September | 376028.1975 | 661.58 | 2522.0885 | 0 | 0.0115 | 312141.7432 | 162233.4862
October | 370106.9911 | 650.6426 | 2478.2839 | 0 | 0.0113 | 306719.9497 | 159626.7729
November | 346013.4794 | 606.9818 | 2306.6813 | 0 | 0.0105 | 285480.9201 | 149104.5291
December | 333305.5267 | 581.1933 | 2194.4477 | 0 | 0.01 | 271587.9623 | 143278.0936
Annual Sum or Average | 4355020 | 7642.1428 | 29052.2369 | 0 | 0.1325 | 3595580 | 1876920
Minimum of Months | 312563.2341 | 545.799 | 2063.9793 | 0 | 0.0094 | 255441.6034 | 134439.2168
Maximum of Months | 411214.8293 | 724.2813 | 2764.343 | 0 | 0.0126 | 342124.5249 | 177493.981
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1903650000000 | 1629961.485 | 23-JAN-16:10 | 645239.307 | 326066.958 | 51915.622 | 0 | 383320.091 | 0 | 77089.049 | 60775.072 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1735870000000 | 1669165.741 | 22-FEB-16:10 | 645239.307 | 326066.958 | 57297.263 | 0 | 416062.812 | 0 | 78168.943 | 60775.072 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 2007180000000 | 1671950.235 | 13-MAR-15:30 | 645239.307 | 326066.958 | 51578.296 | 0 | 425007.275 | 0 | 77727.942 | 60775.072 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1925700000000 | 1710273.978 | 04-APR-15:00 | 645239.307 | 326066.958 | 60223.873 | 0 | 453322.061 | 0 | 79091.322 | 60775.072 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 2163620000000 | 1807879.948 | 15-MAY-15:00 | 645239.307 | 326066.958 | 61252.624 | 0 | 548142.019 | 0 | 80848.582 | 60775.072 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 2181360000000 | 1910789.528 | 27-JUN-15:50 | 645239.307 | 326066.958 | 65130.158 | 0 | 645475.986 | 0 | 82546.662 | 60775.072 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 2200580000000 | 1863580.539 | 13-JUL-15:39 | 645239.307 | 326066.958 | 63668.172 | 0 | 600539.952 | 0 | 81735.692 | 60775.072 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 2324930000000 | 1902680.59 | 21-AUG-15:09 | 645239.307 | 326066.958 | 68163.372 | 0 | 634329.285 | 0 | 82551.21 | 60775.072 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 2121180000000 | 1827924.151 | 11-SEP-15:09 | 645239.307 | 326066.958 | 67558.625 | 0 | 561310.746 | 0 | 81418.057 | 60775.072 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 2084330000000 | 1820810.874 | 06-OCT-15:50 | 645239.307 | 326066.958 | 65318.275 | 0 | 556532.755 | 0 | 81323.121 | 60775.072 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1940000000000 | 1675010.087 | 07-NOV-16:10 | 645239.307 | 326066.958 | 57363.552 | 0 | 421840.369 | 0 | 78169.443 | 60775.072 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1845590000000 | 1623047.593 | 15-DEC-16:10 | 645239.307 | 326066.958 | 45079.264 | 0 | 383820.357 | 0 | 76511.25 | 60775.072 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 24434000000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1735870000000 | 1623047.593 |  | 645239.307 | 326066.958 | 45079.264 | 0 | 383320.091 | 0 | 76511.25 | 60775.072 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2324930000000 | 1910789.528 |  | 645239.307 | 326066.958 | 68163.372 | 0 | 645475.986 | 0 | 82551.21 | 60775.072 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 573078.72 | 9776.96 | 0 | 582855.67
Cost per Total Building Area ($/m2) | 12.37 | 0.21 | 0 | 12.58
Cost per Net Conditioned Building Area ($/m2) | 12.37 | 0.21 | 0 | 12.58

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 26880.43 | 580.32 | 580.32
Net Site Energy | 26880.43 | 580.32 | 580.32
Total Source Energy | 88316.5 | 1906.64 | 1906.64
Net Source Energy | 88316.5 | 1906.64 | 1906.64
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3460.31 | 0 | 0 | 0 | 0
Cooling | 4922.72 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.43 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 764.79 | 0 | 0 | 0 | 0 | 0
Pumps | 1368 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1046.37 | 0 | 0 | 0 | 0 | 21772.59
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 206.32 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 23213.81 | 3666.62 | 0 | 0 | 0 | 23276.72
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 1390.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4738191.3 | 5.11
HEATSYS1 BOILER | Boiler:HotWater | 3551363.21 | 0.76
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 4532344.25
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 459854.09 | 321366.27 | 138487.82 | 0.7 | -
VAV_2_COOLC | Coil:Cooling:Water | 5081626.66 | 3562878.18 | 1518748.48 | 0.7 | -
VAV_3_COOLC | Coil:Cooling:Water | 486836.83 | 340749.77 | 146087.07 | 0.7 | -
VAV_5_COOLC | Coil:Cooling:Water | 124452.25 | 86406.73 | 38045.52 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 66866.41 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 129714.52 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1513084.98 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 135052.08 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24714.44 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31193.61 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 23111.07 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 36857.04 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 256756.48 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 323850.28 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 241290.75 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 387959.74 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27342.42 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30569.82 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 26794.37 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 40307.38 | -
VAV_1_HEATC | Coil:Heating:Water | 22388.82 | -
VAV_2_HEATC | Coil:Heating:Water | 191726.72 | -
VAV_3_HEATC | Coil:Heating:Water | 20651.03 | -
VAV_5_HEATC | Coil:Heating:Water | 17399.68 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 20.09 | 33815.44 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 222.72 | 367029.46 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 21.27 | 35808.56 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.47 | 10260.4 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 43418.97 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20114.04 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 63967.72 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 451229.3728 | 574.6259 | 2312.787 | 0 | 0.0066 | 788845.9634 | 177442.5197
February | 399394.9763 | 508.5317 | 2045.92 | 0 | 0.0058 | 697822.4927 | 157048.0986
March | 459214.5285 | 595.0668 | 2497.5803 | 0 | 0.0071 | 851924.5848 | 181906.6729
April | 429597.5181 | 561.2202 | 2399.9746 | 0 | 0.0068 | 818651.7793 | 170758.8065
May | 483554.6209 | 634.2327 | 2736.7552 | 0 | 0.0077 | 933541.6266 | 192531.2769
June | 508490.3827 | 667.8461 | 2890.5925 | 0 | 0.0081 | 986021.3944 | 202576.6261
July | 512605.5863 | 673.3258 | 2915.034 | 0 | 0.0082 | 994359.0744 | 204225.7207
August | 541038.6394 | 710.5043 | 3074.3528 | 0 | 0.0086 | 1048700 | 215531.8265
September | 467652.5818 | 613.8432 | 2653.3056 | 0 | 0.0075 | 905077.9617 | 186260.0361
October | 459808.7564 | 601.6285 | 2581.9269 | 0 | 0.0073 | 880721.3997 | 182888.5945
November | 428995.2451 | 557.8324 | 2360.1812 | 0 | 0.0067 | 805066.4481 | 170184.1422
December | 446659.2348 | 568.9135 | 2290.8685 | 0 | 0.0065 | 781370.5031 | 175659.2064
Annual Sum or Average | 5588240 | 7267.571 | 30759.2787 | 0 | 0.0868 | 10492100 | 2217010
Minimum of Months | 399394.9763 | 508.5317 | 2045.92 | 0 | 0.0058 | 697822.4927 | 157048.0986
Maximum of Months | 541038.6394 | 710.5043 | 3074.3528 | 0 | 0.0086 | 1048700 | 215531.8265
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1745320000000 | 1554538.331 | 03-JAN-08:00 | 645239.307 | 326066.958 | 38475.265 | 0 | 290261.005 | 0 | 72786.799 | 59487.018 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1543930000000 | 1515529.201 | 15-FEB-16:10 | 645239.307 | 326066.958 | 41092.326 | 0 | 285296.206 | 0 | 72792.002 | 59487.018 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1884880000000 | 1545979.846 | 28-MAR-15:09 | 645239.307 | 326066.958 | 43243.812 | 0 | 312776.566 | 0 | 73610.8 | 59487.018 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1811270000000 | 1608879.132 | 20-APR-15:09 | 645239.307 | 326066.958 | 44764.964 | 0 | 372937.54 | 0 | 74827.959 | 59487.018 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 2065460000000 | 1797067.006 | 18-MAY-15:30 | 645239.307 | 326066.958 | 61089.274 | 0 | 540300.292 | 0 | 79328.772 | 59487.018 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 2181570000000 | 1776098.577 | 29-JUN-15:00 | 645239.307 | 326066.958 | 55564.283 | 0 | 525710.235 | 0 | 78475.39 | 59487.018 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 2200020000000 | 1911103.213 | 18-JUL-15:00 | 645239.307 | 326066.958 | 68107.18 | 0 | 645037.386 | 0 | 81609.979 | 59487.018 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 2320260000000 | 1859491.941 | 31-AUG-15:00 | 645239.307 | 326066.958 | 68947.53 | 0 | 593345.639 | 0 | 80850.104 | 59487.018 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 2002490000000 | 1833793.27 | 15-SEP-15:20 | 645239.307 | 326066.958 | 53556.735 | 0 | 584799.502 | 0 | 79088.365 | 59487.018 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1948600000000 | 1677497.045 | 30-OCT-15:09 | 645239.307 | 326066.958 | 42547.683 | 0 | 442822.219 | 0 | 75778.475 | 59487.018 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1781210000000 | 1604590.726 | 27-NOV-16:00 | 645239.307 | 326066.958 | 39203.528 | 0 | 374585.264 | 0 | 74453.265 | 59487.018 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1728780000000 | 1540369.872 | 19-DEC-16:10 | 645239.307 | 326066.958 | 43394.945 | 0 | 307242.53 | 0 | 73383.728 | 59487.018 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 23213800000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1543930000000 | 1515529.201 |  | 645239.307 | 326066.958 | 38475.265 | 0 | 285296.206 | 0 | 72786.799 | 59487.018 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2320260000000 | 1911103.213 |  | 645239.307 | 326066.958 | 68947.53 | 0 | 645037.386 | 0 | 81609.979 | 59487.018 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 696222.48 | 29551.26 | 0 | 725773.74
Cost per Total Building Area ($/m2) | 15.03 | 0.64 | 0 | 15.67
Cost per Net Conditioned Building Area ($/m2) | 15.03 | 0.64 | 0 | 15.67

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 24859.88 | 536.69 | 536.69
Net Site Energy | 24859.88 | 536.69 | 536.69
Total Source Energy | 72870.26 | 1573.18 | 1573.18
Net Source Energy | 72870.26 | 1573.18 | 1573.18
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2595.29 | 0 | 0 | 0 | 0
Cooling | 3795.19 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.42 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 926.11 | 0 | 0 | 0 | 0 | 0
Pumps | 1241.06 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 1003.6 | 0 | 0 | 0 | 0 | 33790.99
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 186.72 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 22077.87 | 2782.01 | 0 | 0 | 0 | 35295.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 1390.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4763120.43 | 5.11
HEATSYS1 BOILER | Boiler:HotWater | 3541527.4 | 0.76
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 4556190.34
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 444297.14 | 305147.54 | 139149.6 | 0.69 | -
VAV_2_COOLC | Coil:Cooling:Water | 5213487.8 | 3595691.94 | 1617795.86 | 0.69 | -
VAV_3_COOLC | Coil:Cooling:Water | 515385.66 | 355284.29 | 160101.37 | 0.69 | -
VAV_5_COOLC | Coil:Cooling:Water | 86289.08 | 58037.85 | 28251.23 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 47498.15 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 119912.1 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1571000.04 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 146768.43 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 29783.65 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 32598.58 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 24701.11 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 38447.44 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 315832.06 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 346612.02 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 262109.09 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 406727.24 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 33921.68 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 33624.22 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 29534.08 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 42705.4 | -
VAV_1_HEATC | Coil:Heating:Water | 9071.12 | -
VAV_2_HEATC | Coil:Heating:Water | 34468.85 | -
VAV_3_HEATC | Coil:Heating:Water | 3911.58 | -
VAV_5_HEATC | Coil:Heating:Water | 13203.28 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 20.82 | 35044.89 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 246.17 | 405670.04 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 24.31 | 40914.8 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.03 | 7684.62 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 43647.41 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20058.33 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 64304.27 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 333209.1792 | 537.1692 | 1699.2504 | 0 | 0.0047 | 12551000 | 139058.715
February | 304266.1779 | 493.7997 | 1575.4492 | 0 | 0.0043 | 11636800 | 127312.5493
March | 368567.6492 | 611.8138 | 2007.1963 | 0 | 0.0055 | 14826500 | 155599.0142
April | 352566.4491 | 591.5312 | 1965.4777 | 0 | 0.0053 | 14518700 | 149478.7015
May | 389278.6105 | 656.2861 | 2192.9975 | 0 | 0.0059 | 16199500 | 165363.1939
June | 417904.4665 | 705.6178 | 2362.0108 | 0 | 0.0064 | 17448000 | 177631.6157
July | 434112.2199 | 733.2485 | 2455.5304 | 0 | 0.0067 | 18138900 | 184547.5104
August | 448781.2103 | 758.0002 | 2538.3212 | 0 | 0.0069 | 18750400 | 190780.95
September | 397554.5747 | 671.0376 | 2245.4 | 0 | 0.0061 | 16586600 | 168959.569
October | 375283.5462 | 629.8711 | 2093.7511 | 0 | 0.0057 | 15466200 | 159132.9362
November | 340326.6326 | 564.2747 | 1848.6258 | 0 | 0.005 | 13655200 | 143609.7396
December | 336848.1333 | 537.4937 | 1677.7177 | 0 | 0.0046 | 12391700 | 140016.9609
Annual Sum or Average | 4498700 | 7490.1436 | 24661.7283 | 0 | 0.0672 | 182169000 | 1901490
Minimum of Months | 304266.1779 | 493.7997 | 1575.4492 | 0 | 0.0043 | 11636800 | 127312.5493
Maximum of Months | 448781.2103 | 758.0002 | 2538.3212 | 0 | 0.0069 | 18750400 | 190780.95
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1521110000000 | 1446766.995 | 26-JAN-16:10 | 645239.307 | 326066.958 | 51794.553 | 0 | 207868.259 | 0 | 70442.534 | 59799.998 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1410310000000 | 1479578.231 | 28-FEB-16:10 | 645239.307 | 326066.958 | 56181.697 | 0 | 235531.745 | 0 | 71203.141 | 59799.998 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1796890000000 | 1554718.745 | 17-MAR-15:39 | 645239.307 | 326066.958 | 64981.849 | 0 | 300281.498 | 0 | 72793.75 | 59799.998 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1759580000000 | 1537069.495 | 03-APR-15:30 | 645239.307 | 326066.958 | 59066.52 | 0 | 283841.996 | 0 | 77499.331 | 59799.998 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1963280000000 | 1637117.73 | 30-MAY-15:00 | 645239.307 | 326066.958 | 74424.541 | 0 | 371580.278 | 0 | 74451.263 | 59799.998 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 2114600000000 | 1838147.705 | 28-JUN-15:00 | 645239.307 | 326066.958 | 123562.189 | 0 | 511528.928 | 0 | 86394.94 | 59799.998 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 2198320000000 | 1852642.01 | 11-JUL-15:00 | 645239.307 | 326066.958 | 93655.342 | 0 | 559471.485 | 0 | 82853.535 | 59799.998 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 2272440000000 | 1818979.909 | 02-AUG-15:20 | 645239.307 | 326066.958 | 88201.963 | 0 | 532153.466 | 0 | 81962.833 | 59799.998 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 2010200000000 | 1801305.709 | 12-SEP-15:09 | 645239.307 | 326066.958 | 93335.152 | 0 | 509411.402 | 0 | 81897.506 | 59799.998 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1874420000000 | 1638103.168 | 03-OCT-12:50 | 645239.307 | 326066.958 | 49565.835 | 0 | 442173.426 | 0 | 78591.05 | 59799.998 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
November | 1654930000000 | 1525593.82 | 13-NOV-16:10 | 645239.307 | 326066.958 | 59827.92 | 0 | 277082.628 | 0 | 72021.625 | 59799.998 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1501800000000 | 1441551.072 | 11-DEC-16:10 | 645239.307 | 326066.958 | 49871.519 | 0 | 204831.261 | 0 | 70186.644 | 59799.998 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 22077900000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1410310000000 | 1441551.072 |  | 645239.307 | 326066.958 | 49565.835 | 0 | 204831.261 | 0 | 70186.644 | 59799.998 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2272440000000 | 1852642.01 |  | 645239.307 | 326066.958 | 123562.189 | 0 | 559471.485 | 0 | 86394.94 | 59799.998 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 481720.34 | 22899.15 | 0 | 504619.49
Cost per Total Building Area ($/m2) | 10.4 | 0.49 | 0 | 10.89
Cost per Net Conditioned Building Area ($/m2) | 10.4 | 0.49 | 0 | 10.89

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 28410.62 | 613.35 | 613.35
Net Site Energy | 28410.62 | 613.35 | 613.35
Total Source Energy | 80615.93 | 1740.4 | 1740.4
Net Source Energy | 80615.93 | 1740.4 | 1740.4
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 6344.32 | 0 | 0 | 0 | 0
Cooling | 3545.35 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.41 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 803.36 | 0 | 0 | 0 | 0 | 0
Pumps | 1395.14 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 971.5 | 0 | 0 | 0 | 0 | 18459.14
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 239.03 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 21827.26 | 6583.35 | 0 | 0 | 0 | 19963.28
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.278 | 1.58 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 1390.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4703293.09 | 5.11
HEATSYS1 BOILER | Boiler:HotWater | 3681635.95 | 0.76
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 4498962.16
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 443733.82 | 304850.67 | 138883.16 | 0.69 | -
VAV_2_COOLC | Coil:Cooling:Water | 4934101.64 | 3400020.91 | 1534080.74 | 0.69 | -
VAV_3_COOLC | Coil:Cooling:Water | 472901.01 | 325418.57 | 147482.44 | 0.69 | -
VAV_5_COOLC | Coil:Cooling:Water | 114044.03 | 77381.8 | 36662.23 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 63854.54 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 128941.87 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1515319.04 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 136108.08 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 27271.38 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31094.35 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 22316.93 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 36530.08 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 285297.1 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 325677.77 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 231478.98 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 383675.29 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 29999.15 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 31003 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 25430.1 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 39638.41 | -
VAV_1_HEATC | Coil:Heating:Water | 31029.08 | -
VAV_2_HEATC | Coil:Heating:Water | 277559.39 | -
VAV_3_HEATC | Coil:Heating:Water | 29158.55 | -
VAV_5_HEATC | Coil:Heating:Water | 21490.17 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 20.82 | 35046.23 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 231.87 | 382096.24 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 22.17 | 37327.67 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.4 | 10131.61 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 43099.17 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20851.87 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 63496.57 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 413497.5678 | 708.0342 | 1632.7143 | 0 | 0.0061 | 2903470 | 173838.2296
February | 351869.6758 | 617.5078 | 1462.902 | 0 | 0.0055 | 2601660 | 149314.5291
March | 383309.9416 | 704.5429 | 1749.7929 | 0 | 0.0065 | 3112220 | 165598.4022
April | 352869.3828 | 663.7551 | 1685.1655 | 0 | 0.0062 | 2997420 | 153847.7941
May | 378768.989 | 724.1302 | 1865.9969 | 0 | 0.0068 | 3319180 | 166216.371
June | 390876.588 | 752.5243 | 1951.3649 | 0 | 0.0071 | 3471070 | 172014.1422
July | 397693.2218 | 765.5051 | 1984.6959 | 0 | 0.0072 | 3530360 | 175000.7773
August | 421671.9241 | 811.6515 | 2104.3164 | 0 | 0.0077 | 3743140 | 185551.4964
September | 377526.0917 | 724.5503 | 1873.5816 | 0 | 0.0068 | 3332690 | 165929.1938
October | 363733.5681 | 686.7301 | 1749.4962 | 0 | 0.0064 | 3111870 | 158818.9851
November | 359041.4098 | 655.1006 | 1615.3041 | 0 | 0.006 | 2872970 | 154667.2839
December | 390988.5248 | 682.5836 | 1608.0135 | 0 | 0.006 | 2859690 | 165584.288
Annual Sum or Average | 4581850 | 8496.6156 | 21283.3441 | 0 | 0.0783 | 37855700 | 1986380
Minimum of Months | 351869.6758 | 617.5078 | 1462.902 | 0 | 0.0055 | 2601660 | 149314.5291
Maximum of Months | 421671.9241 | 811.6515 | 2104.3164 | 0 | 0.0077 | 3743140 | 185551.4964
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1674110000000 | 1422693.295 | 23-JAN-16:10 | 645239.307 | 326066.958 | 50118.19 | 0 | 183722.235 | 0 | 72942.342 | 59048.878 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1500090000000 | 1427596.773 | 22-FEB-08:09 | 645239.307 | 326066.958 | 39998.034 | 0 | 165697.334 | 0 | 69324.284 | 59048.878 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
March | 1794480000000 | 1464470.465 | 28-MAR-15:50 | 645239.307 | 326066.958 | 50691.047 | 0 | 223752.786 | 0 | 74116.103 | 59048.878 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1728280000000 | 1541437.203 | 20-APR-15:00 | 645239.307 | 326066.958 | 51539.808 | 0 | 300261.337 | 0 | 73725.529 | 59048.878 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1913810000000 | 1658375.777 | 31-MAY-15:00 | 645239.307 | 326066.958 | 55796.38 | 0 | 410228.144 | 0 | 76440.724 | 59048.878 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 2001390000000 | 1721121.672 | 08-JUN-15:00 | 645239.307 | 326066.958 | 55170.066 | 0 | 472567.847 | 0 | 77473.23 | 59048.878 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 2035570000000 | 1815986.691 | 03-JUL-15:00 | 645239.307 | 326066.958 | 73821.435 | 0 | 545701.523 | 0 | 80553.204 | 59048.878 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 2158260000000 | 1758805.39 | 14-AUG-15:30 | 645239.307 | 326066.958 | 66203.638 | 0 | 497785.577 | 0 | 78905.647 | 59048.878 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1921600000000 | 1687428.075 | 05-SEP-15:00 | 645239.307 | 326066.958 | 60590.298 | 0 | 433556.496 | 0 | 77370.752 | 59048.878 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1794270000000 | 1556374.234 | 20-OCT-15:00 | 645239.307 | 326066.958 | 46129.332 | 0 | 320603.395 | 0 | 73730.979 | 59048.878 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1656530000000 | 1438352.663 | 21-NOV-16:10 | 645239.307 | 326066.958 | 43727.682 | 0 | 207972.553 | 0 | 70741.9 | 59048.878 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1648870000000 | 1442472.147 | 26-DEC-08:00 | 645239.307 | 326066.958 | 39998.034 | 0 | 179649.97 | 0 | 70247.021 | 59048.878 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 21827300000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1500090000000 | 1422693.295 |  | 645239.307 | 326066.958 | 39998.034 | 0 | 165697.334 | 0 | 69324.284 | 59048.878 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2158260000000 | 1815986.691 |  | 645239.307 | 326066.958 | 73821.435 | 0 | 545701.523 | 0 | 80553.204 | 59048.878 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 583677.54 | 63641.44 | 0 | 647318.98
Cost per Total Building Area ($/m2) | 12.6 | 1.37 | 0 | 13.97
Cost per Net Conditioned Building Area ($/m2) | 12.6 | 1.37 | 0 | 13.97

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 22389.27 | 483.36 | 483.36
Net Site Energy | 22389.27 | 483.36 | 483.36
Total Source Energy | 64049.92 | 1382.76 | 1382.76
Net Source Energy | 64049.92 | 1382.76 | 1382.76
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2385.74 | 0 | 0 | 0 | 0
Cooling | 2199.46 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.38 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 663.03 | 0 | 0 | 0 | 0 | 0
Pumps | 981.74 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 814.67 | 0 | 0 | 0 | 0 | 12271.82
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 232.77 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 19770.76 | 2618.51 | 0 | 0 | 0 | 13775.95
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 1390.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4059898.38 | 5.11
HEATSYS1 BOILER | Boiler:HotWater | 3135648.66 | 0.76
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3883519.23
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 416806.19 | 295258.22 | 121547.97 | 0.71 | -
VAV_2_COOLC | Coil:Cooling:Water | 4719211.54 | 3351652.58 | 1367558.96 | 0.71 | -
VAV_3_COOLC | Coil:Cooling:Water | 423980.47 | 300382.98 | 123597.49 | 0.71 | -
VAV_5_COOLC | Coil:Cooling:Water | 113614.45 | 79846.78 | 33767.67 | 0.7 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 62467.5 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 117777.1 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1448520.54 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 120182.47 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31174.24 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 28669.02 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16429.76 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 34221 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 322285.91 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 296495.75 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 170513.04 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 356541.33 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31490.34 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 27150.31 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 17713.3 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 35656.96 | -
VAV_1_HEATC | Coil:Heating:Water | 4249.96 | -
VAV_2_HEATC | Coil:Heating:Water | 3019.41 | -
VAV_3_HEATC | Coil:Heating:Water | 3756.76 | -
VAV_5_HEATC | Coil:Heating:Water | 8419.55 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.67 | 31426.99 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 212.18 | 349655.85 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.99 | 31966.98 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.11 | 9584.27 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 37203.35 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 17759.53 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 54810.46 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 153226.8414 | 132.3124 | 1217.0425 | 0 | 0.0006 | 7342740 | 56745.2161
February | 135604.9839 | 116.9544 | 1102.3753 | 0 | 0.0005 | 6651020 | 50296.4163
March | 156884.9033 | 135.1221 | 1308.5464 | 0 | 0.0006 | 7895050 | 58290.4521
April | 143799.5482 | 123.6336 | 1238.4703 | 0 | 0.0006 | 7472390 | 53547.7892
May | 156660.2106 | 134.5224 | 1379.3572 | 0 | 0.0006 | 8322550 | 58428.7265
June | 156139.5253 | 133.9579 | 1395.7711 | 0 | 0.0006 | 8421660 | 58298.5944
July | 157965.3891 | 135.3728 | 1439.2129 | 0 | 0.0007 | 8683870 | 59063.0683
August | 174115.2639 | 149.2096 | 1586.9527 | 0 | 0.0007 | 9575300 | 65103.3152
September | 155976.0873 | 133.7352 | 1409.0711 | 0 | 0.0006 | 8501960 | 58282.6062
October | 157867.9459 | 135.5248 | 1396.1901 | 0 | 0.0006 | 8424140 | 58898.0821
November | 150574.8254 | 129.5341 | 1283.3417 | 0 | 0.0006 | 7743080 | 56029.6251
December | 151140.7116 | 130.3735 | 1225.077 | 0 | 0.0006 | 7391310 | 56047.7161
Annual Sum or Average | 1849960 | 1590.2529 | 15981.4082 | 0 | 0.0074 | 96425100 | 689031.6075
Minimum of Months | 135604.9839 | 116.9544 | 1102.3753 | 0 | 0.0005 | 6651020 | 50296.4163
Maximum of Months | 174115.2639 | 149.2096 | 1586.9527 | 0 | 0.0007 | 9575300 | 65103.3152
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1505540000000 | 1398791.851 | 25-JAN-16:10 | 645239.307 | 326066.958 | 42625.387 | 0 | 188315.089 | 0 | 60018.535 | 50971.19 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1363710000000 | 1381369.015 | 13-FEB-11:00 | 645239.307 | 326066.958 | 50020.376 | 0 | 211521.566 | 0 | 60883.025 | 50971.19 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
March | 1618780000000 | 1406209.761 | 31-MAR-15:09 | 645239.307 | 326066.958 | 47229.783 | 0 | 190770.484 | 0 | 60376.654 | 50971.19 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1532120000000 | 1453800.552 | 11-APR-15:00 | 645239.307 | 326066.958 | 45936.271 | 0 | 234906.775 | 0 | 65124.666 | 50971.19 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1706440000000 | 1539558.904 | 30-MAY-07:49 | 645239.307 | 326066.958 | 40785.583 | 0 | 289521.995 | 0 | 64751.894 | 50971.19 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
June | 1726760000000 | 1496462.061 | 28-JUN-15:00 | 645239.307 | 326066.958 | 43467.742 | 0 | 280579.81 | 0 | 64581.669 | 50971.19 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1780520000000 | 1552932.068 | 20-JUL-15:09 | 645239.307 | 326066.958 | 43308.684 | 0 | 335865.471 | 0 | 65925.073 | 50971.19 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1963300000000 | 1708747.011 | 09-AUG-15:09 | 645239.307 | 326066.958 | 49499.389 | 0 | 481597.711 | 0 | 69817.07 | 50971.19 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1743220000000 | 1575055.978 | 07-SEP-08:00 | 645239.307 | 326066.958 | 43630.317 | 0 | 356919.788 | 0 | 66673.033 | 50971.19 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1727260000000 | 1494734.784 | 05-OCT-15:00 | 645239.307 | 326066.958 | 47725.6 | 0 | 274384.713 | 0 | 64791.631 | 50971.19 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1587620000000 | 1405234.623 | 09-NOV-16:10 | 645239.307 | 326066.958 | 40590.135 | 0 | 194891.34 | 0 | 61920.308 | 50971.19 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1515500000000 | 1383230.642 | 19-DEC-13:20 | 645239.307 | 326066.958 | 50053.803 | 0 | 213277.126 | 0 | 60955.664 | 50971.19 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 19770800000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1363710000000 | 1381369.015 |  | 645239.307 | 326066.958 | 40590.135 | 0 | 188315.089 | 0 | 60018.535 | 50971.19 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1963300000000 | 1708747.011 |  | 645239.307 | 326066.958 | 50053.803 | 0 | 481597.711 | 0 | 69817.07 | 50971.19 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 313173.33 | 22383.32 | 0 | 335556.65
Cost per Total Building Area ($/m2) | 6.76 | 0.48 | 0 | 7.24
Cost per Net Conditioned Building Area ($/m2) | 6.76 | 0.48 | 0 | 7.24

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 25276.37 | 545.69 | 545.69
Net Site Energy | 25276.37 | 545.69 | 545.69
Total Source Energy | 79395.96 | 1714.06 | 1714.06
Net Source Energy | 79395.96 | 1714.06 | 1714.06
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4223.4 | 0 | 0 | 0 | 0
Cooling | 2855.53 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.37 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 972.42 | 0 | 0 | 0 | 0 | 0
Pumps | 1071.01 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 831.89 | 0 | 0 | 0 | 0 | 29462.28
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 210.25 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 20842.72 | 4433.66 | 0 | 0 | 0 | 30966.41
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.306 | 1.623 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 1390.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4561038.23 | 5.11
HEATSYS1 BOILER | Boiler:HotWater | 3715550.44 | 0.76
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 4362887.45
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 432047.76 | 296452.29 | 135595.46 | 0.69 | -
VAV_2_COOLC | Coil:Cooling:Water | 5051015.52 | 3474349.63 | 1576665.88 | 0.69 | -
VAV_3_COOLC | Coil:Cooling:Water | 484249.26 | 332732.49 | 151516.77 | 0.69 | -
VAV_5_COOLC | Coil:Cooling:Water | 85595.18 | 57775.07 | 27820.11 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 50602.53 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 131932.13 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1689403.38 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 152695.69 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 30092.33 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30610.1 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 23463.73 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 37463.26 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 316742.21 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 324806.82 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 249691.6 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 393104.33 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 32838.97 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30674.23 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 27583.04 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 40652.23 | -
VAV_1_HEATC | Coil:Heating:Water | 16203.76 | -
VAV_2_HEATC | Coil:Heating:Water | 107967.75 | -
VAV_3_HEATC | Coil:Heating:Water | 12400.52 | -
VAV_5_HEATC | Coil:Heating:Water | 16454.19 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 22.36 | 37637.99 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 262.22 | 432122.19 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 25.08 | 42222.12 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.46 | 8511.12 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 41795.6 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21043.95 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 61576.07 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 381910.7715 | 579.1712 | 2186.7964 | 0 | 0.0042 | 10904500 | 156345.9071
February | 333020.814 | 524.5027 | 2089.893 | 0 | 0.004 | 10422100 | 138355.4635
March | 387116.5743 | 612.7959 | 2458.449 | 0 | 0.0047 | 12260200 | 161151.3751
April | 381423.8367 | 619.1617 | 2566.8319 | 0 | 0.0048 | 12801300 | 160379.8452
May | 417975.0502 | 682.4801 | 2850.2645 | 0 | 0.0053 | 14214900 | 176162.9846
June | 450105.2593 | 737.3064 | 3091.5808 | 0 | 0.0058 | 15418500 | 189950.4658
July | 462252.0314 | 757.5588 | 3178.3497 | 0 | 0.006 | 15851300 | 195113.4767
August | 484117.2734 | 793.3015 | 3327.8348 | 0 | 0.0062 | 16596800 | 204333.1852
September | 422154.9647 | 691.2385 | 2896.9401 | 0 | 0.0054 | 14447800 | 178125.6281
October | 400548.6045 | 650.3157 | 2696.5576 | 0 | 0.0051 | 13448200 | 168432.6839
November | 365891.2847 | 580.2101 | 2333.1786 | 0 | 0.0044 | 11635500 | 152420.8957
December | 369476.2554 | 566.3347 | 2172.1857 | 0 | 0.0042 | 10831900 | 151881.2469
Annual Sum or Average | 4855990 | 7794.3772 | 31848.862 | 0 | 0.0601 | 158833000 | 2032650
Minimum of Months | 333020.814 | 524.5027 | 2089.893 | 0 | 0.004 | 10422100 | 138355.4635
Maximum of Months | 484117.2734 | 793.3015 | 3327.8348 | 0 | 0.0062 | 16596800 | 204333.1852
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1430930000000 | 1354467.272 | 18-JAN-16:10 | 645239.307 | 326066.958 | 47418.761 | 0 | 127281.387 | 0 | 65642.576 | 57262.898 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1367630000000 | 1409286.882 | 07-FEB-16:10 | 645239.307 | 326066.958 | 54358.365 | 0 | 173560.871 | 0 | 67243.098 | 57262.898 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1608830000000 | 1442707.107 | 31-MAR-15:09 | 645239.307 | 326066.958 | 52072.264 | 0 | 208697.6 | 0 | 67812.695 | 57262.898 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1679830000000 | 1542607.62 | 21-APR-15:09 | 645239.307 | 326066.958 | 63983.825 | 0 | 294449.975 | 0 | 70049.273 | 57262.898 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1865340000000 | 1584393.235 | 31-MAY-15:00 | 645239.307 | 326066.958 | 69832.657 | 0 | 329189.743 | 0 | 71246.288 | 57262.898 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 2023280000000 | 1743336.775 | 27-JUN-15:00 | 645239.307 | 326066.958 | 98293.054 | 0 | 455142.13 | 0 | 75777.044 | 57262.898 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 2080070000000 | 1770658.016 | 26-JUL-15:09 | 645239.307 | 326066.958 | 123290.981 | 0 | 451462.986 | 0 | 81779.501 | 57262.898 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 2177900000000 | 1765237.971 | 02-AUG-15:09 | 645239.307 | 326066.958 | 87911.261 | 0 | 484277.013 | 0 | 78925.149 | 57262.898 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1895900000000 | 1714126.042 | 01-SEP-15:09 | 645239.307 | 326066.958 | 89501.482 | 0 | 424538.547 | 0 | 85961.465 | 57262.898 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1764730000000 | 1566652.189 | 03-OCT-15:09 | 645239.307 | 326066.958 | 71413.166 | 0 | 310150.111 | 0 | 70964.364 | 57262.898 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1526860000000 | 1409151.737 | 10-NOV-16:10 | 645239.307 | 326066.958 | 48415.27 | 0 | 179728.11 | 0 | 66883.809 | 57262.898 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1421410000000 | 1389044.104 | 05-DEC-16:10 | 645239.307 | 326066.958 | 47335.229 | 0 | 161142.819 | 0 | 66441.509 | 57262.898 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 20842700000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1367630000000 | 1354467.272 |  | 645239.307 | 326066.958 | 47335.229 | 0 | 127281.387 | 0 | 65642.576 | 57262.898 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2177900000000 | 1770658.016 |  | 645239.307 | 326066.958 | 123290.981 | 0 | 484277.013 | 0 | 85961.465 | 57262.898 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 563901.9 | 34057.74 | 0 | 597959.65
Cost per Total Building Area ($/m2) | 12.17 | 0.74 | 0 | 12.91
Cost per Net Conditioned Building Area ($/m2) | 12.17 | 0.74 | 0 | 12.91

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 22919.9 | 494.81 | 494.81
Net Site Energy | 22919.9 | 494.81 | 494.81
Total Source Energy | 60656.05 | 1309.49 | 1309.49
Net Source Energy | 60656.05 | 1309.49 | 1309.49
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4872.05 | 0 | 0 | 0 | 0
Cooling | 849.57 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.39 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 634.92 | 0 | 0 | 0 | 0 | 0
Pumps | 673.21 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 517.49 | 0 | 0 | 0 | 0 | 6173.3
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 260.77 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 17787.08 | 5132.82 | 0 | 0 | 0 | 7677.44
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.272 | 1.571 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 1390.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3671721.07 | 5.11
HEATSYS1 BOILER | Boiler:HotWater | 3199176.27 | 0.76
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3512205.99
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 404484.95 | 289345.93 | 115139.02 | 0.72 | -
VAV_2_COOLC | Coil:Cooling:Water | 4603133.6 | 3298007.01 | 1305126.59 | 0.72 | -
VAV_3_COOLC | Coil:Cooling:Water | 395358.51 | 282651.24 | 112707.27 | 0.71 | -
VAV_5_COOLC | Coil:Cooling:Water | 63344.6 | 45452.98 | 17891.62 | 0.72 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 37365.01 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 112571.83 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1393745.55 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 107968.42 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 42391.01 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 25490.3 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14557.1 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 32071.45 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 453585 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 260086.25 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 152797.76 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 330213.2 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 43622.18 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22857.07 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14979.56 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 32261.42 | -
VAV_1_HEATC | Coil:Heating:Water | 12262.05 | -
VAV_2_HEATC | Coil:Heating:Water | 82961.4 | -
VAV_3_HEATC | Coil:Heating:Water | 12926.11 | -
VAV_5_HEATC | Coil:Heating:Water | 13473.93 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.51 | 31163.59 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 211.18 | 348013.61 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.07 | 30423.48 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.57 | 622 | 3.05 | 3331.36 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 33646.24 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18119.34 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 49569.89 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 165659.8626 | 144.2569 | 1099.5665 | 0 | 0.0006 | 6633130 | 60689.8912
February | 136026.761 | 117.6793 | 1041.1877 | 0 | 0.0005 | 6281610 | 50255.7134
March | 158435.5643 | 137.1929 | 1189.9338 | 0 | 0.0006 | 7178920 | 58465.2563
April | 143064.043 | 123.5348 | 1136.6668 | 0 | 0.0006 | 6857810 | 52982.6312
May | 151039.1521 | 130.0924 | 1258.872 | 0 | 0.0006 | 7595340 | 56115.6732
June | 148716.4874 | 127.9623 | 1262.6904 | 0 | 0.0006 | 7618460 | 55323.4448
July | 145697.3744 | 125.2194 | 1263.0369 | 0 | 0.0006 | 7620650 | 54279.5819
August | 157820.1012 | 135.6724 | 1362.011 | 0 | 0.0006 | 8217790 | 58777.2441
September | 145327.4234 | 124.8579 | 1267.612 | 0 | 0.0006 | 7648280 | 54165.4995
October | 148475.6887 | 127.767 | 1258.5232 | 0 | 0.0006 | 7593310 | 55227.3899
November | 149334.7545 | 129.0694 | 1165.0446 | 0 | 0.0006 | 7028940 | 55239.5148
December | 159428.9715 | 138.7454 | 1073.5277 | 0 | 0.0006 | 6476120 | 58453.9258
Annual Sum or Average | 1809030 | 1562.0501 | 14378.6727 | 0 | 0.007 | 86750300 | 669975.7661
Minimum of Months | 136026.761 | 117.6793 | 1041.1877 | 0 | 0.0005 | 6281610 | 50255.7134
Maximum of Months | 165659.8626 | 144.2569 | 1362.011 | 0 | 0.0006 | 8217790 | 60689.8912
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1360040000000 | 1240500.423 | 06-JAN-16:10 | 645239.307 | 326066.958 | 35549.737 | 0 | 49729.787 | 0 | 52261.546 | 46097.704 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1287970000000 | 1372708.197 | 15-FEB-16:10 | 645239.307 | 326066.958 | 41947.881 | 0 | 171352.911 | 0 | 56448.052 | 46097.704 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1471950000000 | 1313664.539 | 20-MAR-15:09 | 645239.307 | 326066.958 | 38721.943 | 0 | 115924.624 | 0 | 56058.618 | 46097.704 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1406110000000 | 1367287.164 | 13-APR-15:09 | 645239.307 | 326066.958 | 44459.089 | 0 | 165317.834 | 0 | 54550.887 | 46097.704 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1557330000000 | 1376409.528 | 25-MAY-15:50 | 645239.307 | 326066.958 | 39454.177 | 0 | 177879.02 | 0 | 56116.978 | 46097.704 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1562070000000 | 1412948.979 | 16-JUN-15:00 | 645239.307 | 326066.958 | 44138.102 | 0 | 207811.017 | 0 | 58040.507 | 46097.704 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1562520000000 | 1447101.499 | 03-JUL-15:09 | 645239.307 | 326066.958 | 45920.348 | 0 | 240232.241 | 0 | 57989.556 | 46097.704 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1684960000000 | 1394361.364 | 14-AUG-15:09 | 645239.307 | 326066.958 | 40262.76 | 0 | 194009.83 | 0 | 57129.42 | 46097.704 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1568180000000 | 1535179.755 | 28-SEP-15:09 | 645239.307 | 326066.958 | 63321.081 | 0 | 305587.132 | 0 | 63312.189 | 46097.704 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1556910000000 | 1414431.746 | 13-OCT-15:09 | 645239.307 | 326066.958 | 46951.109 | 0 | 206391.426 | 0 | 58129.857 | 46097.704 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1441200000000 | 1335432.353 | 16-NOV-16:10 | 645239.307 | 326066.958 | 35549.737 | 0 | 141871.035 | 0 | 55052.228 | 46097.704 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1327850000000 | 1225294.305 | 20-DEC-08:09 | 645239.307 | 326066.958 | 35549.737 | 0 | 0 | 0 | 50118.622 | 46097.704 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 17787100000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1287970000000 | 1225294.305 |  | 645239.307 | 326066.958 | 35549.737 | 0 | 0 | 0 | 50118.622 | 46097.704 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1684960000000 | 1535179.755 |  | 645239.307 | 326066.958 | 63321.081 | 0 | 305587.132 | 0 | 63312.189 | 46097.704 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 747285.77 | 43880.72 | 0 | 791166.49
Cost per Total Building Area ($/m2) | 16.13 | 0.95 | 0 | 17.08
Cost per Net Conditioned Building Area ($/m2) | 16.13 | 0.95 | 0 | 17.08

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 31810.46 | 686.75 | 686.75
Net Site Energy | 31810.46 | 686.75 | 686.75
Total Source Energy | 87689.46 | 1893.11 | 1893.11
Net Source Energy | 87689.46 | 1893.11 | 1893.11
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 10228.3 | 0 | 0 | 0 | 0
Cooling | 3044.54 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.36 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 825.07 | 0 | 0 | 0 | 0 | 0
Pumps | 1478.26 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 857.68 | 0 | 0 | 0 | 0 | 16286.46
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 264.76 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 21317.41 | 10493.06 | 0 | 0 | 0 | 17790.59
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.011 | 1.191 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 1390.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4693570.96 | 5.11
HEATSYS1 BOILER | Boiler:HotWater | 3840657.16 | 0.76
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 4489662.4
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 468184.75 | 326791.25 | 141393.5 | 0.7 | -
VAV_2_COOLC | Coil:Cooling:Water | 5167214.19 | 3617588.57 | 1549625.63 | 0.7 | -
VAV_3_COOLC | Coil:Cooling:Water | 488723.8 | 341528.83 | 147194.97 | 0.7 | -
VAV_5_COOLC | Coil:Cooling:Water | 113642 | 78527.06 | 35114.94 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 61058.9 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 129425.47 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1511433.14 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 134543.88 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 31801.8 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30757.91 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 21905.91 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 36389.9 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 329905.44 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 322666 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 226693.25 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 380451.59 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 33209.16 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 30414.5 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 24321.61 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 38761.28 | -
VAV_1_HEATC | Coil:Heating:Water | 40435.89 | -
VAV_2_HEATC | Coil:Heating:Water | 374088.56 | -
VAV_3_HEATC | Coil:Heating:Water | 39200.97 | -
VAV_5_HEATC | Coil:Heating:Water | 25579.09 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 20.51 | 34518.37 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 227.04 | 374146.47 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 21.4 | 36031.25 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5 | 9384.79 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 43010.08 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21752.53 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 63365.32 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 399317.2129 | 659.7557 | 1643.2151 | 0 | 0.0069 | 102159.5657 | 165388.2447
February | 346125.9605 | 588.4361 | 1515.7861 | 0 | 0.0063 | 94244.3503 | 144872.1346
March | 356470.3781 | 643.894 | 1770.1983 | 0 | 0.0073 | 110077.7767 | 152664.7004
April | 309371.9015 | 580.9216 | 1658.3481 | 0 | 0.0068 | 103130.3685 | 134514.8727
May | 320719.8225 | 624.8602 | 1844.1306 | 0 | 0.0075 | 114691.3902 | 141518.1761
June | 336529.3801 | 668.2059 | 2004.297 | 0 | 0.0081 | 124656.4215 | 149641.1465
July | 341153.3139 | 679.6511 | 2044.3367 | 0 | 0.0082 | 127147.3447 | 151904.2333
August | 366200.7291 | 728.5557 | 2188.9361 | 0 | 0.0088 | 136140.4008 | 162966.0112
September | 312508.8969 | 613.4816 | 1822.4208 | 0 | 0.0074 | 113342.622 | 138317.4178
October | 319122.3049 | 610.7468 | 1774.2027 | 0 | 0.0072 | 110339.0056 | 139807.3781
November | 337990.7751 | 614.1769 | 1698.6543 | 0 | 0.007 | 105630.1999 | 145085.3951
December | 384633.6238 | 648.4165 | 1654.1362 | 0 | 0.0069 | 102844.0855 | 160488.1028
Annual Sum or Average | 4130140 | 7661.1018 | 21618.6619 | 0 | 0.0882 | 1344400 | 1787170
Minimum of Months | 309371.9015 | 580.9216 | 1515.7861 | 0 | 0.0063 | 94244.3503 | 134514.8727
Maximum of Months | 399317.2129 | 728.5557 | 2188.9361 | 0 | 0.0088 | 136140.4008 | 165388.2447
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1619880000000 | 1362527.893 | 09-JAN-08:00 | 645239.307 | 326066.958 | 39092.281 | 0 | 101547.19 | 0 | 69433.36 | 58926.819 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1494380000000 | 1344336.326 | 15-FEB-16:10 | 645239.307 | 326066.958 | 39092.281 | 0 | 122274.448 | 0 | 67181.128 | 58926.819 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1745440000000 | 1467858.539 | 09-MAR-16:10 | 645239.307 | 326066.958 | 40153.307 | 0 | 240854.678 | 0 | 71062.086 | 58926.819 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1635280000000 | 1465238.393 | 04-APR-15:00 | 645239.307 | 326066.958 | 41039.081 | 0 | 237319.129 | 0 | 71091.714 | 58926.819 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1818590000000 | 1625722.232 | 31-MAY-15:50 | 645239.307 | 326066.958 | 42968.747 | 0 | 392388.945 | 0 | 74576.071 | 58926.819 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1976600000000 | 1789218.787 | 30-JUN-15:00 | 645239.307 | 326066.958 | 58085.993 | 0 | 537197.608 | 0 | 78146.717 | 58926.819 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 2016100000000 | 1847149.992 | 25-JUL-15:30 | 645239.307 | 326066.958 | 64700.561 | 0 | 587044.294 | 0 | 79616.668 | 58926.819 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 2158700000000 | 1899310.784 | 09-AUG-15:09 | 645239.307 | 326066.958 | 59194.096 | 0 | 644325.225 | 0 | 80002.994 | 58926.819 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1797210000000 | 1602715.175 | 13-SEP-15:09 | 645239.307 | 326066.958 | 58788.81 | 0 | 353290.05 | 0 | 74847.846 | 58926.819 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1749580000000 | 1550009.335 | 12-OCT-15:09 | 645239.307 | 326066.958 | 52358.215 | 0 | 308260.678 | 0 | 73601.973 | 58926.819 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1674920000000 | 1495909.793 | 03-NOV-15:09 | 645239.307 | 326066.958 | 44342.857 | 0 | 263827.471 | 0 | 71950.995 | 58926.819 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1630740000000 | 1312393.002 | 08-DEC-08:00 | 645239.307 | 326066.958 | 39092.281 | 0 | 54609.088 | 0 | 66236.571 | 58926.819 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 21317400000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1494380000000 | 1312393.002 |  | 645239.307 | 326066.958 | 39092.281 | 0 | 54609.088 | 0 | 66236.571 | 58926.819 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 2158700000000 | 1899310.784 |  | 645239.307 | 326066.958 | 64700.561 | 0 | 644325.225 | 0 | 80002.994 | 58926.819 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 412299.62 | 101809.75 | 0 | 514109.38
Cost per Total Building Area ($/m2) | 8.9 | 2.2 | 0 | 11.1
Cost per Net Conditioned Building Area ($/m2) | 8.9 | 2.2 | 0 | 11.1

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 25329.77 | 546.84 | 546.84
Net Site Energy | 25329.77 | 546.84 | 546.84
Total Source Energy | 69590.48 | 1502.37 | 1502.37
Net Source Energy | 69590.48 | 1502.37 | 1502.37
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 6233.25 | 0 | 0 | 0 | 0
Cooling | 1605.77 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.38 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 950.29 | 0 | 0 | 0 | 0 | 0
Pumps | 671.65 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 497.06 | 0 | 0 | 0 | 0 | 14916.06
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 259.88 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 18836.64 | 6493.13 | 0 | 0 | 0 | 16420.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.045 | 1.238 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 1390.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3655805.09 | 5.11
HEATSYS1 BOILER | Boiler:HotWater | 3308351.42 | 0.76
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3496981.46
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 337802.83 | 219050.26 | 118752.57 | 0.65 | -
VAV_2_COOLC | Coil:Cooling:Water | 3832819.21 | 2490951.04 | 1341868.17 | 0.65 | -
VAV_3_COOLC | Coil:Cooling:Water | 331101.53 | 214547.54 | 116553.99 | 0.65 | -
VAV_5_COOLC | Coil:Cooling:Water | 69074.63 | 44358.15 | 24716.48 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 48354.86 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 115249.5 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1407761.16 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 109172.25 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24426.12 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 26956.43 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 19019.04 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 33796.97 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 251988.47 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 280483.1 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 196229.95 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 354389.27 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 24534.94 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 24893.67 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 20549.33 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 35668.09 | -
VAV_1_HEATC | Coil:Heating:Water | 28484.58 | -
VAV_2_HEATC | Coil:Heating:Water | 250247.88 | -
VAV_3_HEATC | Coil:Heating:Water | 29009.57 | -
VAV_5_HEATC | Coil:Heating:Water | 19811.28 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 21.73 | 36573.42 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 246.61 | 406388.24 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 21.27 | 35801.82 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.79 | 9131.57 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 33500.39 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18737.68 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 49355.01 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 444987.1716 | 714.8558 | 1684.8507 | 0 | 0.0067 | 1751570 | 184510.4143
February | 385462.0539 | 632.2281 | 1529.8188 | 0 | 0.0061 | 1590500 | 161103.6842
March | 435491.4048 | 730.0773 | 1813.8491 | 0 | 0.0071 | 1885910 | 183562.4543
April | 398792.8442 | 686.0439 | 1755.6606 | 0 | 0.0069 | 1825530 | 169809.3311
May | 456648.5872 | 796.8051 | 2071.1591 | 0 | 0.0081 | 2153660 | 195546.5123
June | 478698.5794 | 837.8143 | 2184.8849 | 0 | 0.0085 | 2271930 | 205237.3638
July | 487870.5805 | 854.749 | 2231.5215 | 0 | 0.0087 | 2320430 | 209256.2801
August | 513970.7442 | 899.9221 | 2347.9033 | 0 | 0.0091 | 2441450 | 220396.724
September | 448217.2357 | 782.7001 | 2036.2028 | 0 | 0.0079 | 2117310 | 191995.5556
October | 423038.2875 | 727.5411 | 1861.2507 | 0 | 0.0073 | 1935320 | 180112.4213
November | 410128.1602 | 683.0595 | 1683.8657 | 0 | 0.0066 | 1750730 | 172430.5037
December | 435394.7046 | 699.6472 | 1649.6204 | 0 | 0.0066 | 1714940 | 180552.7197
Annual Sum or Average | 5318700 | 9045.4435 | 22850.5874 | 0 | 0.0897 | 23759300 | 2254510
Minimum of Months | 385462.0539 | 632.2281 | 1529.8188 | 0 | 0.0061 | 1590500 | 161103.6842
Maximum of Months | 513970.7442 | 899.9221 | 2347.9033 | 0 | 0.0091 | 2441450 | 220396.724
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1388660000000 | 1280267.103 | 26-JAN-16:10 | 645239.307 | 326066.958 | 53888.778 | 0 | 71143.327 | 0 | 52475.466 | 45897.882 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1260970000000 | 1363886.928 | 14-FEB-16:10 | 645239.307 | 326066.958 | 57905.44 | 0 | 147900.56 | 0 | 55321.396 | 45897.882 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1495170000000 | 1363907.043 | 02-MAR-16:10 | 645239.307 | 326066.958 | 57375.375 | 0 | 148510.001 | 0 | 55262.135 | 45897.882 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1447300000000 | 1426996.397 | 21-APR-15:50 | 645239.307 | 326066.958 | 63774.766 | 0 | 202588.895 | 0 | 57873.204 | 45897.882 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1707450000000 | 1491904.205 | 31-MAY-15:00 | 645239.307 | 326066.958 | 72309.737 | 0 | 256738.623 | 0 | 60096.313 | 45897.882 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1801210000000 | 1625197.593 | 29-JUN-15:30 | 645239.307 | 326066.958 | 115742.942 | 0 | 327238.35 | 0 | 79456.769 | 45897.882 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1839670000000 | 1620843.904 | 03-JUL-15:30 | 645239.307 | 326066.958 | 114375.654 | 0 | 334312.736 | 0 | 69395.982 | 45897.882 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1935610000000 | 1653127.321 | 01-AUG-15:09 | 645239.307 | 326066.958 | 113953.493 | 0 | 368816.769 | 0 | 67597.528 | 45897.882 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1678630000000 | 1533922.667 | 13-SEP-15:09 | 645239.307 | 326066.958 | 102163.049 | 0 | 262072.44 | 0 | 66927.646 | 45897.882 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1534350000000 | 1450760.768 | 11-OCT-15:50 | 645239.307 | 326066.958 | 62292.886 | 0 | 218511.158 | 0 | 67197.193 | 45897.882 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1388000000000 | 1337308.355 | 01-NOV-15:09 | 645239.307 | 326066.958 | 53718.432 | 0 | 126783.573 | 0 | 54046.818 | 45897.882 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1359630000000 | 1233961.68 | 05-DEC-16:10 | 645239.307 | 326066.958 | 47335.455 | 0 | 32662.335 | 0 | 51204.358 | 45897.882 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 18836600000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1260970000000 | 1233961.68 |  | 645239.307 | 326066.958 | 47335.455 | 0 | 32662.335 | 0 | 51204.358 | 45897.882 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1935610000000 | 1653127.321 |  | 645239.307 | 326066.958 | 115742.942 | 0 | 368816.769 | 0 | 79456.769 | 45897.882 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 193413.4 | 44715.36 | 0 | 238128.76
Cost per Total Building Area ($/m2) | 4.18 | 0.97 | 0 | 5.14
Cost per Net Conditioned Building Area ($/m2) | 4.18 | 0.97 | 0 | 5.14

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 28647.73 | 618.47 | 618.47
Net Site Energy | 28647.73 | 618.47 | 618.47
Total Source Energy | 42724.5 | 922.37 | 922.37
Net Source Energy | 42724.5 | 922.37 | 922.37
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 10767.69 | 0 | 0 | 0 | 0
Cooling | 773.77 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.29 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 776.18 | 0 | 0 | 0 | 0 | 0
Pumps | 551.35 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 388.74 | 0 | 0 | 0 | 0 | 5502.19
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 278.22 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 17601.82 | 11045.9 | 0 | 0 | 0 | 7006.32
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.994 | 1.167 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 5.835 | 0.54 | 0.384 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 5.835 | 0.54 | 0.384 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 1390.85 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 3245.31 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3940486.88 | 5.11
HEATSYS1 BOILER | Boiler:HotWater | 3565454.81 | 0.76
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3769295.48
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 419638.47 | 297265.12 | 122373.35 | 0.71 | -
VAV_2_COOLC | Coil:Cooling:Water | 4813702.54 | 3416009.96 | 1397692.58 | 0.71 | -
VAV_3_COOLC | Coil:Cooling:Water | 430501.16 | 304987.42 | 125513.74 | 0.71 | -
VAV_5_COOLC | Coil:Cooling:Water | 76902.14 | 54392.42 | 22509.72 | 0.71 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 44739.82 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 115848.48 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1449059.5 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 119134.57 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 42277.42 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 28153.62 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16854.73 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 33842.06 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 453498.7 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 289984.71 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 178176.43 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 355476.12 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 44296.77 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 26156.7 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 18041.9 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 35447.66 | -
VAV_1_HEATC | Coil:Heating:Water | 27437.52 | -
VAV_2_HEATC | Coil:Heating:Water | 232171.67 | -
VAV_3_HEATC | Coil:Heating:Water | 26720.8 | -
VAV_5_HEATC | Coil:Heating:Water | 20251.78 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 19.59 | 32974.94 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 225.35 | 371360.26 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 20.09 | 33823.93 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.7 | 7054.15 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 36109.11 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20193.85 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 53198.35 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 166050.0825 | 196.547 | 293.2491 | 0 | 0.0014 | 3869460 | 62377.5366
February | 128167.9334 | 158.0567 | 266.888 | 0 | 0.0012 | 3523190 | 48826.9465
March | 138312.2611 | 174.2381 | 311.4527 | 0 | 0.0014 | 4112250 | 53084.7403
April | 110992.7688 | 145.9819 | 289.2614 | 0 | 0.0012 | 3820440 | 43259.1045
May | 96224.9034 | 138.9664 | 329.9962 | 0 | 0.0013 | 4360510 | 38832.2596
June | 91386.0581 | 136.7583 | 343.9214 | 0 | 0.0014 | 4545130 | 37391.4554
July | 87461.8141 | 134.4949 | 352.1969 | 0 | 0.0014 | 4654910 | 36172.3598
August | 95070.8408 | 145.7306 | 379.8679 | 0 | 0.0015 | 5020580 | 39269.4815
September | 93625.9543 | 136.7036 | 330.5998 | 0 | 0.0013 | 4368680 | 37943.0688
October | 108925.0307 | 147.0764 | 308.2246 | 0 | 0.0013 | 4071530 | 42861.6956
November | 139607.6834 | 171.9577 | 289.3907 | 0 | 0.0013 | 3820200 | 53162.9229
December | 165609.9195 | 195.1726 | 287.0233 | 0 | 0.0013 | 3787100 | 62120.7934
Annual Sum or Average | 1421440 | 1881.6841 | 3782.0719 | 0 | 0.0159 | 49954000 | 555302.3649
Minimum of Months | 87461.8141 | 134.4949 | 266.888 | 0 | 0.0012 | 3523190 | 36172.3598
Maximum of Months | 166050.0825 | 196.547 | 379.8679 | 0 | 0.0015 | 5020580 | 62377.5366
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1363450000000 | 1187403.605 | 09-JAN-08:00 | 645239.307 | 326066.958 | 38328.86 | 0 | 0 | 0 | 55546.502 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1241430000000 | 1276100.584 | 21-FEB-16:10 | 645239.307 | 326066.958 | 38328.86 | 0 | 75383.627 | 0 | 56054.444 | 49472.003 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1449000000000 | 1347971.168 | 29-MAR-15:09 | 645239.307 | 326066.958 | 40978.902 | 0 | 143310.894 | 0 | 57347.718 | 49472.003 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1346170000000 | 1309059.629 | 14-APR-15:09 | 645239.307 | 326066.958 | 38328.86 | 0 | 107833.959 | 0 | 56563.156 | 49472.003 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1536470000000 | 1426341.613 | 04-MAY-15:09 | 645239.307 | 326066.958 | 47228.139 | 0 | 210433.558 | 0 | 62346.262 | 49472.003 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1601520000000 | 1448250.265 | 28-JUN-15:09 | 645239.307 | 326066.958 | 47049.947 | 0 | 232944.459 | 0 | 61922.207 | 49472.003 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1640210000000 | 1510437.657 | 31-JUL-15:00 | 645239.307 | 326066.958 | 50247.549 | 0 | 290755.076 | 0 | 63101.378 | 49472.003 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1769060000000 | 1489305.568 | 18-AUG-15:09 | 645239.307 | 326066.958 | 49437.513 | 0 | 270856.351 | 0 | 62678.051 | 49472.003 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1539350000000 | 1497869.313 | 01-SEP-15:50 | 645239.307 | 326066.958 | 49012.929 | 0 | 279794.923 | 0 | 62727.808 | 49472.003 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1434650000000 | 1377593.034 | 17-OCT-15:09 | 645239.307 | 326066.958 | 43289.665 | 0 | 169971.81 | 0 | 57997.906 | 49472.003 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1346090000000 | 1283831.34 | 03-NOV-15:09 | 645239.307 | 326066.958 | 38328.86 | 0 | 82306.443 | 0 | 56862.384 | 49472.003 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1334430000000 | 1186852.415 | 04-DEC-08:09 | 645239.307 | 326066.958 | 38328.86 | 0 | 0.544 | 0 | 54994.767 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 17601800000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1241430000000 | 1186852.415 |  | 645239.307 | 326066.958 | 38328.86 | 0 | 0 | 0 | 54994.767 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1769060000000 | 1510437.657 |  | 645239.307 | 326066.958 | 50247.549 | 0 | 290755.076 | 0 | 63101.378 | 49472.003 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 355390.19 | 92899.65 | 0 | 448289.84
Cost per Total Building Area ($/m2) | 7.67 | 2.01 | 0 | 9.68
Cost per Net Conditioned Building Area ($/m2) | 7.67 | 2.01 | 0 | 9.68

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 30296.59 | 654.07 | 654.07
Net Site Energy | 30296.59 | 654.07 | 654.07
Total Source Energy | 78857.69 | 1702.44 | 1702.44
Net Source Energy | 78857.69 | 1702.44 | 1702.44
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 11356.5 | 0 | 0 | 0 | 0
Cooling | 1622 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.37 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 776.87 | 0 | 0 | 0 | 0 | 0
Pumps | 704.81 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 437.19 | 0 | 0 | 0 | 0 | 8876.16
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 287.36 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 18652.73 | 11643.86 | 0 | 0 | 0 | 10380.29
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.886 | 1.021 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 1390.85 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 3245.31 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4422396.16 | 5.11
HEATSYS1 BOILER | Boiler:HotWater | 3928622.31 | 0.76
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 4230268.57
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 402810.63 | 280565.68 | 122244.96 | 0.7 | -
VAV_2_COOLC | Coil:Cooling:Water | 4735790.29 | 3312464.52 | 1423325.77 | 0.7 | -
VAV_3_COOLC | Coil:Cooling:Water | 446719.69 | 311699.41 | 135020.28 | 0.7 | -
VAV_5_COOLC | Coil:Cooling:Water | 121870.62 | 84316.49 | 37554.13 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 67683.6 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 134840.88 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1662076.62 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 152130.93 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20522.67 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22757.3 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 17188.37 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 26268.17 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 224601.95 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 246581.85 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 200030.34 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 282270.55 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22389.78 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 23091.12 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 19001.1 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 28955.23 | -
VAV_1_HEATC | Coil:Heating:Water | 61890.89 | -
VAV_2_HEATC | Coil:Heating:Water | 579551.11 | -
VAV_3_HEATC | Coil:Heating:Water | 59556.67 | -
VAV_5_HEATC | Coil:Heating:Water | 32770.21 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.46 | 31081.85 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 217.96 | 359174.64 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 20.46 | 34447.16 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.59 | 1109.65 | 5.64 | 10580.79 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 40525.14 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 22250.74 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 59704.34 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 608461.5705 | 983.9441 | 2590.0986 | 0 | 0.0081 | 596109.1943 | 251858.9815
February | 527858.7939 | 869.6645 | 2343.2842 | 0 | 0.0073 | 539331.8644 | 220031.1015
March | 579244.5879 | 979.4279 | 2721.8867 | 0 | 0.0084 | 626511.4593 | 243850.7767
April | 507854.8713 | 888.078 | 2562.4351 | 0 | 0.0078 | 589854.0187 | 216604.3004
May | 573672.5989 | 1029.7697 | 3053.9686 | 0 | 0.0092 | 703038.9354 | 247219.084
June | 632905.8757 | 1148.9483 | 3446.3441 | 0 | 0.0104 | 793382.8833 | 273973.9309
July | 640508.8164 | 1164.1651 | 3496.2251 | 0 | 0.0105 | 804867.8441 | 277400.3754
August | 680822.1043 | 1236.4431 | 3710.3172 | 0 | 0.0112 | 854152.8159 | 294764.7774
September | 579036.8242 | 1045.5471 | 3119.3829 | 0 | 0.0094 | 718105.8392 | 250118.5953
October | 540845.863 | 957.9963 | 2802.1949 | 0 | 0.0085 | 645062.2105 | 231844.3057
November | 528922.2252 | 902.4532 | 2534.061 | 0 | 0.0078 | 583290.861 | 223441.8071
December | 580150.3104 | 950.0487 | 2540.8417 | 0 | 0.0079 | 584792.6058 | 241276.6815
Annual Sum or Average | 6980280 | 12156.486 | 34921.0402 | 0 | 0.1065 | 8038500 | 2972380
Minimum of Months | 507854.8713 | 869.6645 | 2343.2842 | 0 | 0.0073 | 539331.8644 | 216604.3004
Maximum of Months | 680822.1043 | 1236.4431 | 3710.3172 | 0 | 0.0112 | 854152.8159 | 294764.7774
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1383230000000 | 1191889.83 | 17-JAN-08:30 | 645239.307 | 326066.958 | 37474.077 | 0 | 0 | 0 | 60887.51 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1251480000000 | 1192034.362 | 27-FEB-08:09 | 645239.307 | 326066.958 | 37474.077 | 0 | 0.085 | 0 | 61031.956 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
March | 1453770000000 | 1372127.691 | 31-MAR-15:00 | 645239.307 | 326066.958 | 37474.077 | 0 | 158417.927 | 0 | 63851.762 | 55522.275 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1368710000000 | 1396383.626 | 10-APR-08:00 | 645239.307 | 326066.958 | 37474.077 | 0 | 179913.391 | 0 | 66612.233 | 55522.275 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1631350000000 | 1618368.625 | 30-MAY-08:00 | 645239.307 | 326066.958 | 37474.077 | 0 | 396793.805 | 0 | 71716.819 | 55522.275 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1840990000000 | 1657553.134 | 08-JUN-12:00 | 645239.307 | 326066.958 | 44582.836 | 0 | 477061.852 | 0 | 72413.313 | 55522.275 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
July | 1867640000000 | 1678737.595 | 13-JUL-15:09 | 645239.307 | 326066.958 | 49180.485 | 0 | 444940.396 | 0 | 72232.789 | 55522.275 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1982000000000 | 1765794.266 | 04-AUG-15:50 | 645239.307 | 326066.958 | 47728.063 | 0 | 531887.576 | 0 | 73794.702 | 55522.275 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1666310000000 | 1587005.905 | 07-SEP-12:00 | 645239.307 | 326066.958 | 39369.193 | 0 | 411742.788 | 0 | 72398.79 | 55522.275 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
October | 1496820000000 | 1487760.58 | 31-OCT-07:00 | 645239.307 | 326066.958 | 37474.077 | 0 | 233461.794 | 0 | 67774.191 | 55522.275 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
November | 1353480000000 | 1500472.047 | 02-NOV-07:00 | 645239.307 | 326066.958 | 37474.077 | 0 | 245580.711 | 0 | 68366.741 | 55522.275 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
December | 1356970000000 | 1191784.066 | 11-DEC-08:00 | 645239.307 | 326066.958 | 37474.077 | 0 | 0 | 0 | 60781.745 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 18652700000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1251480000000 | 1191784.066 |  | 645239.307 | 326066.958 | 37474.077 | 0 | 0 | 0 | 60781.745 | 0 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1982000000000 | 1765794.266 |  | 645239.307 | 326066.958 | 49180.485 | 0 | 531887.576 | 0 | 73794.702 | 55522.275 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 452026.62 | 97417.89 | 0 | 549444.51
Cost per Total Building Area ($/m2) | 9.76 | 2.1 | 0 | 11.86
Cost per Net Conditioned Building Area ($/m2) | 9.76 | 2.1 | 0 | 11.86

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 25118.7 | 542.28 | 542.28
Net Site Energy | 25118.7 | 542.28 | 542.28
Total Source Energy | 66719.09 | 1440.38 | 1440.38
Net Source Energy | 66719.09 | 1440.38 | 1440.38
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 7182.26 | 0 | 0 | 0 | 0
Cooling | 968.28 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.34 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 766.18 | 0 | 0 | 0 | 0 | 0
Pumps | 479.12 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 324.84 | 0 | 0 | 0 | 0 | 9113.73
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 286.18 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 17650.26 | 7468.44 | 0 | 0 | 0 | 10617.86
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.914 | 1.059 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 1390.85 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 3245.31 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3174822.21 | 5.11
HEATSYS1 BOILER | Boiler:HotWater | 3205211.57 | 0.76
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3036894.52
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 287687.23 | 183935.86 | 103751.37 | 0.64 | -
VAV_2_COOLC | Coil:Cooling:Water | 3344922.82 | 2144344.74 | 1200578.07 | 0.64 | -
VAV_3_COOLC | Coil:Cooling:Water | 274098.95 | 175016.99 | 99081.97 | 0.64 | -
VAV_5_COOLC | Coil:Cooling:Water | 65606.58 | 41779.41 | 23827.17 | 0.64 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 46975.87 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 114038.44 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1386554.48 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 104167 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16324.99 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19397.08 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14018.3 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24015.02 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 178682.12 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 205864.67 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 149518.64 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 258683.16 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 16768.62 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 17243.1 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16093.16 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 25882.41 | -
VAV_1_HEATC | Coil:Heating:Water | 48455.14 | -
VAV_2_HEATC | Coil:Heating:Water | 454103.77 | -
VAV_3_HEATC | Coil:Heating:Water | 49306.18 | -
VAV_5_HEATC | Coil:Heating:Water | 26041.9 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.63 | 31355.51 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 216.16 | 356212.79 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.73 | 29851.47 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.66 | 8887.49 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 29092.85 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 18153.52 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 42861.53 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 446518.7989 | 711.9416 | 1661.5594 | 0 | 0.0066 | 1727310 | 184618.2926
February | 387077.4024 | 627.8684 | 1498.293 | 0 | 0.006 | 1557670 | 161091.2997
March | 430700.1884 | 715.886 | 1760.5569 | 0 | 0.007 | 1830460 | 180938.778
April | 383258.0221 | 654.3753 | 1660.5096 | 0 | 0.0065 | 1726560 | 162709.5103
May | 412596.8611 | 714.3889 | 1841.3179 | 0 | 0.0072 | 1914630 | 176138.1993
June | 429710.9608 | 749.7574 | 1948.742 | 0 | 0.0076 | 2026360 | 184006.9095
July | 450100.6448 | 788.239 | 2056.9374 | 0 | 0.008 | 2138890 | 193023.029
August | 468238.8018 | 819.5802 | 2137.5367 | 0 | 0.0083 | 2222700 | 200759.9494
September | 404225.0873 | 703.9621 | 1825.9776 | 0 | 0.0071 | 1898700 | 172963.3555
October | 405466.3846 | 695.2101 | 1772.5139 | 0 | 0.0069 | 1843040 | 172423.9648
November | 402659.054 | 666.0783 | 1628.6184 | 0 | 0.0064 | 1693260 | 168844.7799
December | 435281.9197 | 693.925 | 1619.203 | 0 | 0.0065 | 1683280 | 179962.4474
Annual Sum or Average | 5055830 | 8541.2123 | 21411.7658 | 0 | 0.0842 | 22262900 | 2137480
Minimum of Months | 383258.0221 | 627.8684 | 1498.293 | 0 | 0.006 | 1557670 | 161091.2997
Maximum of Months | 468238.8018 | 819.5802 | 2137.5367 | 0 | 0.0083 | 2222700 | 200759.9494
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1369440000000 | 1239410.281 | 27-JAN-16:10 | 645239.307 | 326066.958 | 36808.847 | 0 | 60571.692 | 0 | 45308.851 | 39859.241 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
February | 1234940000000 | 1173678.389 | 09-FEB-08:09 | 645239.307 | 326066.958 | 36721.847 | 0 | 0.464 | 0 | 43427.835 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
March | 1451210000000 | 1307439.54 | 30-MAR-15:09 | 645239.307 | 326066.958 | 40025.099 | 0 | 123345.947 | 0 | 47347.604 | 39859.241 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1368840000000 | 1343288.983 | 26-APR-15:00 | 645239.307 | 326066.958 | 45211.283 | 0 | 152899.54 | 0 | 48457.27 | 39859.241 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1517940000000 | 1402824.508 | 24-MAY-15:00 | 645239.307 | 326066.958 | 53142.097 | 0 | 199108.773 | 0 | 53852.748 | 39859.241 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1606530000000 | 1482316.102 | 27-JUN-15:30 | 645239.307 | 326066.958 | 83045.603 | 0 | 238905.22 | 0 | 63644.388 | 39859.241 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1695740000000 | 1514933.841 | 18-JUL-15:09 | 645239.307 | 326066.958 | 88709.731 | 0 | 270054.408 | 0 | 59448.811 | 39859.241 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1762180000000 | 1508940.926 | 30-AUG-15:30 | 645239.307 | 326066.958 | 90028.863 | 0 | 261223.912 | 0 | 60967.261 | 39859.241 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1505310000000 | 1428067.416 | 01-SEP-15:00 | 645239.307 | 326066.958 | 59678.142 | 0 | 219923.779 | 0 | 51744.604 | 39859.241 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1461180000000 | 1379591.732 | 05-OCT-15:30 | 645239.307 | 326066.958 | 52209.066 | 0 | 180707.744 | 0 | 49954.032 | 39859.241 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1342430000000 | 1264897.489 | 10-NOV-13:00 | 645239.307 | 326066.958 | 45101.603 | 0 | 124301.404 | 0 | 47662.383 | 39859.241 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
December | 1334530000000 | 1173853.165 | 28-DEC-08:20 | 645239.307 | 326066.958 | 36721.847 | 0 | 0.392 | 0 | 43602.683 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 17650300000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1234940000000 | 1173678.389 |  | 645239.307 | 326066.958 | 36721.847 | 0 | 0.392 | 0 | 43427.835 | 0 | 36666.593 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1762180000000 | 1514933.841 |  | 645239.307 | 326066.958 | 90028.863 | 0 | 270054.408 | 0 | 63644.388 | 39859.241 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 181243.83 | 51566.9 | 0 | 232810.73
Cost per Total Building Area ($/m2) | 3.91 | 1.11 | 0 | 5.03
Cost per Net Conditioned Building Area ($/m2) | 3.91 | 1.11 | 0 | 5.03

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 32391.4 | 699.29 | 699.29
Net Site Energy | 32391.4 | 699.29 | 699.29
Total Source Energy | 78138 | 1686.9 | 1686.9
Net Source Energy | 78138 | 1686.9 | 1686.9
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 13847.16 | 0 | 0 | 0 | 0
Cooling | 1362.13 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.34 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 751.06 | 0 | 0 | 0 | 0 | 0
Pumps | 627.07 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 385.26 | 0 | 0 | 0 | 0 | 7429.4
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 306.88 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 18237.35 | 14154.04 | 0 | 0 | 0 | 8933.53
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 1390.85 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 3245.31 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 4129989.62 | 5.11
HEATSYS1 BOILER | Boiler:HotWater | 3883161.21 | 0.76
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3950565.41
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 374172.07 | 255865.4 | 118306.67 | 0.68 | -
VAV_2_COOLC | Coil:Cooling:Water | 4420941.4 | 3039974.56 | 1380966.85 | 0.69 | -
VAV_3_COOLC | Coil:Cooling:Water | 417380.01 | 286252.09 | 131127.92 | 0.69 | -
VAV_5_COOLC | Coil:Cooling:Water | 100898.53 | 68433.21 | 32465.32 | 0.68 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 56446.96 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 117335.39 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1496419.6 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 136773.57 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 22313.42 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22691.3 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 16668.05 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 25910.42 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 243614.61 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 242911.5 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 179794.93 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 278043.26 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 23765.43 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 22763.79 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 20701.65 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 28021.81 | -
VAV_1_HEATC | Coil:Heating:Water | 72340.62 | -
VAV_2_HEATC | Coil:Heating:Water | 697942.16 | -
VAV_3_HEATC | Coil:Heating:Water | 71060.45 | -
VAV_5_HEATC | Coil:Heating:Water | 35982.2 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.21 | 28967.8 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 204.97 | 337771.4 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 19.26 | 32415.48 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.74 | 9041.62 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 37845.64 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21993.26 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 55756.72 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 489973.2956 | 721.1967 | 902.4095 | 0 | 0.007 | 592556.9949 | 196005.0824
February | 402523.0318 | 615.5465 | 816.4633 | 0 | 0.0062 | 536259.5523 | 163227.2274
March | 398529.6491 | 651.0743 | 943.9322 | 0 | 0.0071 | 620208.5195 | 165587.5806
April | 332302.8888 | 574.1194 | 888.7914 | 0 | 0.0066 | 584123.8958 | 141056.6576
May | 369333.4305 | 662.3626 | 1066.8476 | 0 | 0.0078 | 701244.4696 | 159094.9288
June | 394373.8192 | 716.3803 | 1168.8432 | 0 | 0.0085 | 768321.5358 | 170752.2081
July | 399546.0218 | 727.4514 | 1189.6291 | 0 | 0.0087 | 781991.0598 | 173151.7989
August | 428382.8546 | 779.0474 | 1272.5358 | 0 | 0.0093 | 836485.6105 | 185562.1519
September | 350089.1416 | 629.77 | 1017.5112 | 0 | 0.0074 | 668822.7495 | 150988.7519
October | 345054.1279 | 595.9593 | 922.2765 | 0 | 0.0068 | 606129.8981 | 146451.1335
November | 381533.772 | 618.2207 | 887.1109 | 0 | 0.0066 | 582850.5446 | 158039.5547
December | 443411.5136 | 673.2989 | 883.8514 | 0 | 0.0068 | 580494.6526 | 179351.4885
Annual Sum or Average | 4735050 | 7964.4276 | 11960.202 | 0 | 0.0887 | 7859490 | 1989270
Minimum of Months | 332302.8888 | 574.1194 | 816.4633 | 0 | 0.0062 | 536259.5523 | 141056.6576
Maximum of Months | 489973.2956 | 779.0474 | 1272.5358 | 0 | 0.0093 | 836485.6105 | 196005.0824
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1374980000000 | 1185735.969 | 31-JAN-08:09 | 645239.307 | 326066.958 | 35176.837 | 0 | 0 | 0 | 57030.889 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1244350000000 | 1185954.039 | 13-FEB-08:00 | 645239.307 | 326066.958 | 35176.837 | 0 | 0 | 0 | 57248.959 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
March | 1439150000000 | 1224974.127 | 23-MAR-15:00 | 645239.307 | 326066.958 | 35341.737 | 0 | 74054.491 | 0 | 58716.248 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1355420000000 | 1357700.349 | 14-APR-15:00 | 645239.307 | 326066.958 | 35550.773 | 0 | 153637.726 | 0 | 59799.029 | 51851.171 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1627180000000 | 1500440.672 | 31-MAY-15:09 | 645239.307 | 326066.958 | 38370.934 | 0 | 288148.28 | 0 | 65208.637 | 51851.171 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1782830000000 | 1662986.591 | 29-JUN-15:00 | 645239.307 | 326066.958 | 50664.389 | 0 | 435015.074 | 0 | 68594.307 | 51851.171 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1814550000000 | 1694292.936 | 13-JUL-15:00 | 645239.307 | 326066.958 | 45568.893 | 0 | 471234.187 | 0 | 68777.035 | 51851.171 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1941000000000 | 1665497.32 | 25-AUG-15:00 | 645239.307 | 326066.958 | 45345.622 | 0 | 443153.231 | 0 | 68285.647 | 51851.171 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1551950000000 | 1558823.415 | 22-SEP-15:00 | 645239.307 | 326066.958 | 35176.837 | 0 | 348433.932 | 0 | 66499.825 | 51851.171 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1406480000000 | 1383377.747 | 06-OCT-15:09 | 645239.307 | 326066.958 | 39014.023 | 0 | 170841.516 | 0 | 64809.387 | 51851.171 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1352460000000 | 1332179.219 | 02-NOV-15:09 | 645239.307 | 326066.958 | 39199.124 | 0 | 124833.491 | 0 | 59433.783 | 51851.171 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1346990000000 | 1185409.441 | 08-DEC-08:50 | 645239.307 | 326066.958 | 35176.837 | 0 | 0.617 | 0 | 56703.744 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 18237400000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1244350000000 | 1185409.441 |  | 645239.307 | 326066.958 | 35176.837 | 0 | 0 | 0 | 56703.744 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1941000000000 | 1694292.936 |  | 645239.307 | 326066.958 | 50664.389 | 0 | 471234.187 | 0 | 68777.035 | 51851.171 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 314536.62 | 111494.41 | 0 | 426031.03
Cost per Total Building Area ($/m2) | 6.79 | 2.41 | 0 | 9.2
Cost per Net Conditioned Building Area ($/m2) | 6.79 | 2.41 | 0 | 9.2

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 28428.67 | 613.74 | 613.74
Net Site Energy | 28428.67 | 613.74 | 613.74
Total Source Energy | 72112.1 | 1556.81 | 1556.81
Net Source Energy | 72112.1 | 1556.81 | 1556.81
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 10891.74 | 0 | 0 | 0 | 0
Cooling | 675.44 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.33 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 760.58 | 0 | 0 | 0 | 0 | 0
Pumps | 417.82 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 260.84 | 0 | 0 | 0 | 0 | 6313.89
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 310.42 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 17226.51 | 11202.16 | 0 | 0 | 0 | 7818.02
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.823 | 0.939 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 1390.85 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 3245.31 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3174744 | 5.11
HEATSYS1 BOILER | Boiler:HotWater | 3568150.32 | 0.76
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3036819.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 305390.08 | 202823.53 | 102566.55 | 0.66 | -
VAV_2_COOLC | Coil:Cooling:Water | 3567758.01 | 2373541.8 | 1194216.21 | 0.67 | -
VAV_3_COOLC | Coil:Cooling:Water | 303691.33 | 201635.08 | 102056.25 | 0.66 | -
VAV_5_COOLC | Coil:Cooling:Water | 65634.79 | 43725.47 | 21909.33 | 0.67 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 45446.55 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 114182.98 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1400590.61 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 111899.04 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 20943.11 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19956.25 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14382.4 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24190.15 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 229858.64 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 214708.1 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 154491.68 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 261309.58 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21266.15 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 18711.48 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 19830.04 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 25843.43 | -
VAV_1_HEATC | Coil:Heating:Water | 66187.75 | -
VAV_2_HEATC | Coil:Heating:Water | 639252.61 | -
VAV_3_HEATC | Coil:Heating:Water | 66233.77 | -
VAV_5_HEATC | Coil:Heating:Water | 32415.15 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.19 | 30621.78 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 212.38 | 349988.66 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.08 | 30428.2 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 4.27 | 8142.81 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 29092.13 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 20209.12 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 42860.47 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 457898.3255 | 695.9833 | 1015.9567 | 0 | 0.0073 | 24085400 | 185578.648
February | 387146.7497 | 603.9355 | 915.0011 | 0 | 0.0065 | 21695200 | 158401.6285
March | 402507.3095 | 661.3226 | 1072.187 | 0 | 0.0076 | 25428400 | 167917.4239
April | 343983.4989 | 579.6945 | 968.8299 | 0 | 0.0068 | 22979500 | 144906.7777
May | 363576.4843 | 631.2434 | 1091.0275 | 0 | 0.0076 | 25880800 | 154951.7183
June | 380567.381 | 668.3141 | 1169.3946 | 0 | 0.0081 | 27740900 | 162924.8652
July | 384307.5572 | 680.486 | 1201.1534 | 0 | 0.0083 | 28495100 | 165067.7589
August | 400890.0016 | 708.3712 | 1247.6403 | 0 | 0.0087 | 29597700 | 172047.4761
September | 353563.2483 | 618.6716 | 1078.3867 | 0 | 0.0075 | 25581700 | 151149.4713
October | 361497.5264 | 614.2663 | 1036.4448 | 0 | 0.0072 | 24584100 | 152773.5266
November | 381501.1931 | 619.5674 | 990.0412 | 0 | 0.007 | 23479000 | 158454.093
December | 433371.9228 | 667.636 | 993.8401 | 0 | 0.0071 | 23562900 | 176501.8619
Annual Sum or Average | 4650810 | 7749.4918 | 12779.9033 | 0 | 0.0898 | 303111000 | 1950680
Minimum of Months | 343983.4989 | 579.6945 | 915.0011 | 0 | 0.0065 | 21695200 | 144906.7777
Maximum of Months | 457898.3255 | 708.3712 | 1247.6403 | 0 | 0.0087 | 29597700 | 185578.648
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1368830000000 | 1176495.485 | 10-JAN-08:09 | 645239.307 | 326066.958 | 36161.913 | 0 | 0.374 | 3079 | 43725.954 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1232990000000 | 1185262.262 | 02-FEB-16:10 | 645239.307 | 326066.958 | 36161.913 | 0 | 47015.754 | 0 | 45222.946 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
March | 1445160000000 | 1306482.176 | 30-MAR-15:09 | 645239.307 | 326066.958 | 40018.689 | 0 | 122728.93 | 0 | 47014.649 | 39858.259 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
April | 1305980000000 | 1286370.346 | 06-APR-15:30 | 645239.307 | 326066.958 | 36824.991 | 0 | 106436.51 | 0 | 46388.936 | 39858.259 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
May | 1470870000000 | 1330485.183 | 16-MAY-15:00 | 645239.307 | 326066.958 | 38942.385 | 0 | 147362.558 | 0 | 47460.333 | 39858.259 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1576580000000 | 1488735.111 | 26-JUN-15:20 | 645239.307 | 326066.958 | 79119.868 | 0 | 256535.757 | 0 | 56359.577 | 39858.259 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1619450000000 | 1486021.163 | 21-JUL-15:00 | 645239.307 | 326066.958 | 63779.891 | 0 | 264537.989 | 0 | 60983.374 | 39858.259 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1682110000000 | 1455076.546 | 09-AUG-15:00 | 645239.307 | 326066.958 | 56819.269 | 0 | 241853.754 | 0 | 59683.614 | 39858.259 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1453870000000 | 1389034.317 | 01-SEP-15:00 | 645239.307 | 326066.958 | 45749.564 | 0 | 197560.872 | 0 | 49003.972 | 39858.259 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1397170000000 | 1342694.429 | 06-OCT-15:20 | 645239.307 | 326066.958 | 44196.133 | 0 | 153817.61 | 0 | 47960.777 | 39858.259 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1334370000000 | 1189029.45 | 21-NOV-16:10 | 645239.307 | 326066.958 | 36161.913 | 0 | 12361.087 | 0 | 43786.542 | 39858.259 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
December | 1339140000000 | 1173682.19 | 28-DEC-08:39 | 645239.307 | 326066.958 | 36161.913 | 0 | 0 | 0 | 43992.034 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 17226500000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1232990000000 | 1173682.19 |  | 645239.307 | 326066.958 | 36161.913 | 0 | 0 | 0 | 43725.954 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1682110000000 | 1488735.111 |  | 645239.307 | 326066.958 | 79119.868 | 0 | 264537.989 | 3079 | 60983.374 | 39858.259 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 373894.39 | 90461.13 | 0 | 464355.52
Cost per Total Building Area ($/m2) | 8.07 | 1.95 | 0 | 10.02
Cost per Net Conditioned Building Area ($/m2) | 8.07 | 1.95 | 0 | 10.02

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 34186.04 | 738.03 | 738.03
Net Site Energy | 34186.04 | 738.03 | 738.03
Total Source Energy | 77504.5 | 1673.23 | 1673.23
Net Source Energy | 77504.5 | 1673.23 | 1673.23
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 16715.48 | 0 | 0 | 0 | 0
Cooling | 636.01 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48.3 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 739.54 | 0 | 0 | 0 | 0 | 0
Pumps | 419.16 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 224.99 | 0 | 0 | 0 | 0 | 3766.23
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 339.08 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 17131.49 | 17054.55 | 0 | 0 | 0 | 5270.36
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.772 | 0.873 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 1390.85 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 3245.31 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3597906.31 | 5.11
HEATSYS1 BOILER | Boiler:HotWater | 3788884.53 | 0.76
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3441598.05
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 337865.25 | 233436.94 | 104428.31 | 0.69 | -
VAV_2_COOLC | Coil:Cooling:Water | 3980039.35 | 2760817.24 | 1219222.1 | 0.69 | -
VAV_3_COOLC | Coil:Cooling:Water | 350109.27 | 242085.65 | 108023.62 | 0.69 | -
VAV_5_COOLC | Coil:Cooling:Water | 68827.03 | 47320.8 | 21506.23 | 0.69 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 42369.02 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 114844.48 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1432689.11 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 119838.06 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21282.59 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20671.57 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 14812.38 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24366.65 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 234002.83 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 224283.05 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 159492.07 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 263577.65 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 21851.91 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20063.58 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 21935.03 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 26050.75 | -
VAV_1_HEATC | Coil:Heating:Water | 76030.73 | -
VAV_2_HEATC | Coil:Heating:Water | 744736.95 | -
VAV_3_HEATC | Coil:Heating:Water | 75772.56 | -
VAV_5_HEATC | Coil:Heating:Water | 35475.91 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.77 | 28237.11 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 198.19 | 326595.3 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.39 | 29269.3 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.58 | 1109.65 | 3.63 | 6931.2 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 32969.83 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 21459.3 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 48573.36 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 488518.4102 | 718.6939 | 898.5533 | 0 | 0.0069 | 590022.7483 | 195388.5419
February | 417725.7963 | 627.6684 | 811.0705 | 0 | 0.0062 | 532657.0605 | 168328.5656
March | 426332.5319 | 674.6573 | 938.6751 | 0 | 0.0071 | 616652.683 | 175052.1187
April | 342678.3232 | 572.5382 | 853.0245 | 0 | 0.0063 | 560537.0235 | 143596.2484
May | 344420.0787 | 602.345 | 944.9403 | 0 | 0.0069 | 621055.6411 | 146897.0833
June | 352152.2827 | 635.4139 | 1029.8001 | 0 | 0.0075 | 676907.7382 | 152063.2781
July | 372347.652 | 675.1651 | 1099.6395 | 0 | 0.008 | 722827.0357 | 161100.3766
August | 377981.3928 | 682.7897 | 1107.8412 | 0 | 0.0081 | 728208.6149 | 163290.2286
September | 323502.816 | 571.1405 | 905.061 | 0 | 0.0066 | 594866.8237 | 138489.7303
October | 345596.8083 | 586.9018 | 891.1824 | 0 | 0.0066 | 585653.2481 | 145726.0943
November | 395206.5206 | 627.3592 | 876.5185 | 0 | 0.0066 | 575829.3789 | 162458.9197
December | 457302.052 | 684.6031 | 879.6684 | 0 | 0.0068 | 577693.1963 | 184034.3534
Annual Sum or Average | 4643760 | 7659.276 | 11235.9749 | 0 | 0.0837 | 7382910 | 1936430
Minimum of Months | 323502.816 | 571.1405 | 811.0705 | 0 | 0.0062 | 532657.0605 | 138489.7303
Maximum of Months | 488518.4102 | 718.6939 | 1107.8412 | 0 | 0.0081 | 728208.6149 | 195388.5419
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1369100000000 | 1179553.067 | 10-JAN-08:50 | 645239.307 | 326066.958 | 33804.01 | 0 | 0 | 0 | 52220.814 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1235990000000 | 1165371.065 | 03-FEB-08:09 | 645239.307 | 326066.958 | 33804.01 | 0 | 0 | 0 | 38038.812 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
March | 1430900000000 | 1177887.175 | 20-MAR-07:30 | 645239.307 | 326066.958 | 33804.01 | 0 | 0 | 0 | 50554.921 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
April | 1300680000000 | 1217836.826 | 05-APR-07:00 | 645239.307 | 326066.958 | 33804.01 | 0 | 0 | 0 | 48964.416 | 41540.157 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
May | 1441110000000 | 1347990.802 | 31-MAY-15:00 | 645239.307 | 326066.958 | 36550.124 | 0 | 156425.584 | 0 | 52982.47 | 45170.974 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1570710000000 | 1506905.508 | 14-JUN-15:50 | 645239.307 | 326066.958 | 39763.417 | 0 | 306849.105 | 0 | 58260.361 | 45170.974 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1677270000000 | 1624037.444 | 07-JUL-07:00 | 645239.307 | 326066.958 | 39701.716 | 0 | 384389.244 | 0 | 61247.267 | 45170.974 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
August | 1689750000000 | 1527730.328 | 11-AUG-15:00 | 645239.307 | 326066.958 | 41555.563 | 0 | 325325.288 | 0 | 58816.854 | 45170.974 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1380340000000 | 1487750.99 | 07-SEP-15:30 | 645239.307 | 326066.958 | 38009.371 | 0 | 289360.823 | 0 | 58348.172 | 45170.974 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1358960000000 | 1290248.863 | 27-OCT-15:09 | 645239.307 | 326066.958 | 34292.171 | 0 | 102274.079 | 0 | 51649.99 | 45170.974 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
November | 1336170000000 | 1179296.806 | 27-NOV-08:39 | 645239.307 | 326066.958 | 33804.01 | 0 | 0 | 0 | 51964.553 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
December | 1340490000000 | 1178033.76 | 07-DEC-08:50 | 645239.307 | 326066.958 | 33804.01 | 0 | 0 | 0 | 50701.506 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 17131500000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1235990000000 | 1165371.065 |  | 645239.307 | 326066.958 | 33804.01 | 0 | 0 | 0 | 38038.812 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1689750000000 | 1624037.444 |  | 645239.307 | 326066.958 | 41555.563 | 0 | 384389.244 | 0 | 61247.267 | 45170.974 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 294578.5 | 134165.89 | 0 | 428744.39
Cost per Total Building Area ($/m2) | 6.36 | 2.9 | 0 | 9.26
Cost per Net Conditioned Building Area ($/m2) | 6.36 | 2.9 | 0 | 9.26

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 45171.24 | 975.19 | 975.19
Net Site Energy | 45171.24 | 975.19 | 975.19
Total Source Energy | 90901.01 | 1962.44 | 1962.44
Net Source Energy | 90901.01 | 1962.44 | 1962.44
Area [m2]
Total Building Area | 46320.38
Net Conditioned Building Area | 46320.38
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 28029.56 | 0 | 0 | 0 | 0
Cooling | 342.57 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 7389.8 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 48 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 5778.62 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 1895.08 | 0 | 0 | 0 | 0 | 0
Fans | 790.52 | 0 | 0 | 0 | 0 | 0
Pumps | 363.63 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 155.5 | 0 | 0 | 0 | 0 | 2627.32
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 377.97 | 0 | 0 | 0 | 1504.13
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 16763.72 | 28407.53 | 0 | 0 | 0 | 4131.45
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BASEMENT | 3563.11 | Yes | 8690.42 | 1 | 0 | 0 | 7.53 | 37.16 | 4.84
CORE_BOTTOM | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_MID | 2532.32 | Yes | 6948.69 | 10 | 0 | 0 | 16.14 | 18.58 | 8.07
CORE_TOP | 2532.32 | Yes | 6948.69 | 1 | 0 | 0 | 16.14 | 18.58 | 8.07
GROUNDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
MIDFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 10 | 297.11 | 0 | 0 |  | 0
PERIMETER_BOT_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_BOT_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_1 | 313.42 | Yes | 860.02 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_2 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_3 | 313.41 | Yes | 860 | 10 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_MID_ZN_4 | 201.98 | Yes | 554.22 | 10 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_1 | 313.42 | Yes | 860.02 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_2 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_3 | 313.41 | Yes | 860 | 1 | 200.61 | 115.9 | 16.14 | 18.58 | 8.07
PERIMETER_TOP_ZN_4 | 201.98 | Yes | 554.22 | 1 | 133.74 | 77.27 | 16.14 | 18.58 | 8.07
TOPFLOOR_PLENUM | 3563.11 | Yes | 4344.14 | 1 | 297.11 | 0 | 0 |  | 0
Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Conditioned Total | 89077.65 |  | 178146.04 |  | 11589.54 | 4636.15 | 8.0484 | 37.16 | 4.0672
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BASEMENT_WALL_EAST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 90 | 90 | E
BASEMENT_WALL_NORTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 0 | 90 | N
BASEMENT_WALL_SOUTH | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 178.31 | 180 | 90 | S
BASEMENT_WALL_WEST | BELOW-GRADE-WALL-NONRES | 0.3 | 3.26 | 6.368 | 118.87 | 270 | 90 | W
BASEMENT_FLOOR | EXT-SLAB | 0.3 | 1.862 | 3.401 | 3563.11 | 0 | 180
GROUNDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 59.42 | 90 | 90 | E
GROUNDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 89.13 | 0 | 90 | N
GROUNDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 89.13 | 180 | 90 | S
GROUNDFLOOR_PLENUM_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 59.42 | 270 | 90 | W
MIDFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 594.21 | 90 | 90 | E
MIDFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 891.32 | 0 | 90 | N
MIDFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 891.32 | 180 | 90 | S
MIDFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 594.21 | 270 | 90 | W
PERIMETER_BOT_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 200.61 | 180 | 90 | S
PERIMETER_BOT_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 133.74 | 90 | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 200.61 | 0 | 90 | N
PERIMETER_BOT_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 133.74 | 270 | 90 | W
PERIMETER_MID_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 2006.06 | 180 | 90 | S
PERIMETER_MID_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 1337.37 | 90 | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 2006.06 | 0 | 90 | N
PERIMETER_MID_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 1337.37 | 270 | 90 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 200.61 | 180 | 90 | S
PERIMETER_TOP_ZN_2_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 133.74 | 90 | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 200.61 | 0 | 90 | N
PERIMETER_TOP_ZN_4_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 133.74 | 270 | 90 | W
TOPFLOOR_PLENUM_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 59.42 | 90 | 90 | E
TOPFLOOR_PLENUM_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 89.13 | 180 | 90 | S
TOPFLOOR_PLENUM_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 89.13 | 0 | 90 | N
TOPFLOOR_PLENUM_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.71 | 0.794 | 59.42 | 270 | 90 | W
BUILDING_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 3563.11 | 0 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
PERIMETER_BOT_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_BOT_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_2_WALL_EAST | 90 | E
PERIMETER_BOT_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_3_WALL_NORTH | 0 | N
PERIMETER_BOT_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_BOT_ZN_4_WALL_WEST | 270 | W
PERIMETER_MID_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_MID_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_2_WALL_EAST | 90 | E
PERIMETER_MID_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 1159.04 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_3_WALL_NORTH | 0 | N
PERIMETER_MID_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 772.69 | 3.525 | 0.407 | 0.316 | No | PERIMETER_MID_ZN_4_WALL_WEST | 270 | W
PERIMETER_TOP_ZN_1_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_1_WALL_SOUTH | 180 | S
PERIMETER_TOP_ZN_2_WALL_EAST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_2_WALL_EAST | 90 | E
PERIMETER_TOP_ZN_3_WALL_NORTH_WINDOW | WINDOW-NONRES-FIXED | 115.9 | 115.9 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_3_WALL_NORTH | 0 | N
PERIMETER_TOP_ZN_4_WALL_WEST_WINDOW | WINDOW-NONRES-FIXED | 77.27 | 77.27 | 3.525 | 0.407 | 0.316 | No | PERIMETER_TOP_ZN_4_WALL_WEST | 270 | W
Total or Average |  |  | 4636.15 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 1390.85 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 3245.31 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
COOLSYS1 CHILLER | Chiller:Electric:EIR | 3282181.21 | 5.11
HEATSYS1 BOILER | Boiler:HotWater | 4369859.9 | 0.76
TOWERWATERSYS COOLTOWER | CoolingTower:SingleSpeed | 3139589.39
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
VAV_1_COOLC | Coil:Cooling:Water | 348574.28 | 248812.46 | 99761.82 | 0.71 | -
VAV_2_COOLC | Coil:Cooling:Water | 4174946.14 | 2982440.54 | 1192505.6 | 0.71 | -
VAV_3_COOLC | Coil:Cooling:Water | 355831.64 | 253975.03 | 101856.61 | 0.71 | -
VAV_5_COOLC | Coil:Cooling:Water | 45007.96 | 32807.89 | 12200.07 | 0.73 | -
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
BASEMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 29565.98 | -
CORE_BOTTOM VAV BOX REHEAT COIL | Coil:Heating:Water | 113143.27 | -
CORE_MID VAV BOX REHEAT COIL | Coil:Heating:Water | 1439708.02 | -
CORE_TOP VAV BOX REHEAT COIL | Coil:Heating:Water | 114799.74 | -
PERIMETER_BOT_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 32193.66 | -
PERIMETER_BOT_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 20679.9 | -
PERIMETER_BOT_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 19430.53 | -
PERIMETER_BOT_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 22944.01 | -
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 359288.55 | -
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 226435.41 | -
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 202356.09 | -
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 253085.12 | -
PERIMETER_TOP_ZN_1 VAV BOX REHEAT COIL | Coil:Heating:Water | 33664.62 | -
PERIMETER_TOP_ZN_2 VAV BOX REHEAT COIL | Coil:Heating:Water | 19770.13 | -
PERIMETER_TOP_ZN_3 VAV BOX REHEAT COIL | Coil:Heating:Water | 28052.85 | -
PERIMETER_TOP_ZN_4 VAV BOX REHEAT COIL | Coil:Heating:Water | 24569.37 | -
VAV_1_HEATC | Coil:Heating:Water | 100641.76 | -
VAV_2_HEATC | Coil:Heating:Water | 1004016.99 | -
VAV_3_HEATC | Coil:Heating:Water | 100662.57 | -
VAV_5_HEATC | Coil:Heating:Water | 32990.08 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
VAV_1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.78 | 28252.08 | 1 | Fan Energy
VAV_2_FAN | Fan:VariableVolume | 0.62 | 1017.59 | 200.9 | 331068.33 | 1 | Fan Energy
VAV_3_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.12 | 28824.66 | 1 | Fan Energy
VAV_5_FAN | Fan:VariableVolume | 0.57 | 622 | 2.45 | 2677.85 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
COOLSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 30076.65 | 0.9
HEATSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 24749.8 | 0.88
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 72.71 | 0.85
TOWERWATERSYS PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 44310.92 | 0.87
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.76 | 845000 | 0.8 | 0.9 | 0.59
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 571407.4756 | 611.7396 | 1948.102 | 0 | 0.0072 | 390686.4619 | 212081.8229
February | 476444.4574 | 516.4096 | 1756.8985 | 0 | 0.0064 | 352381.3128 | 177810.6562
March | 455923.7889 | 510.8655 | 2030.5656 | 0 | 0.0072 | 407368.6173 | 172721.8474
April | 340561.032 | 396.903 | 1836.9081 | 0 | 0.0064 | 368591.6399 | 131372.6971
May | 304980.3974 | 372.6904 | 2005.9762 | 0 | 0.0068 | 402585.7793 | 120302.5582
June | 311102.0151 | 386.3847 | 2176.2359 | 0 | 0.0074 | 436776.17 | 123673.4808
July | 307629.2607 | 382.8044 | 2167.2757 | 0 | 0.0073 | 434980.101 | 122405.7243
August | 320462.6638 | 395.6873 | 2193.112 | 0 | 0.0074 | 440156.0707 | 127037.1431
September | 299534.4447 | 360.4518 | 1853.3417 | 0 | 0.0064 | 371934.7261 | 117295.113
October | 384460.7797 | 441.1491 | 1928.9952 | 0 | 0.0068 | 387042.0093 | 147242.8544
November | 471466.8034 | 518.9996 | 1905.6018 | 0 | 0.0069 | 382253.5561 | 177181.7883
December | 518394.5104 | 561.7306 | 1908.4944 | 0 | 0.007 | 382786.0462 | 193443.7843
Annual Sum or Average | 4762370 | 5455.8154 | 23711.5071 | 0 | 0.0833 | 4757540 | 1822570
Minimum of Months | 299534.4447 | 360.4518 | 1756.8985 | 0 | 0.0064 | 352381.3128 | 117295.113
Maximum of Months | 571407.4756 | 611.7396 | 2193.112 | 0 | 0.0074 | 440156.0707 | 212081.8229
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY {AT MAX/MIN} [W] | EXTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 1376630000000 | 1179159.018 | 05-JAN-08:30 | 645239.307 | 326066.958 | 34592.14 | 0 | 0 | 3079 | 47959.635 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
February | 1241650000000 | 1180401.933 | 15-FEB-08:39 | 645239.307 | 326066.958 | 34592.14 | 0 | 0 | 3079 | 49202.55 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
March | 1435410000000 | 1162852.821 | 24-MAR-07:10 | 645239.307 | 326066.958 | 34592.14 | 0 | 0 | 0 | 34732.438 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
April | 1298770000000 | 1172922.131 | 14-APR-07:30 | 645239.307 | 326066.958 | 34592.14 | 0 | 0.628 | 0 | 44801.12 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
May | 1418550000000 | 1299670.887 | 30-MAY-15:09 | 645239.307 | 326066.958 | 34592.14 | 0 | 119218.263 | 0 | 47791.724 | 41207.111 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
June | 1539030000000 | 1386457.632 | 21-JUN-15:00 | 645239.307 | 326066.958 | 39662.356 | 0 | 197221.845 | 0 | 51504.671 | 41207.111 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
July | 1532700000000 | 1385986.019 | 03-JUL-15:00 | 645239.307 | 326066.958 | 34592.14 | 0 | 200679.162 | 0 | 52645.956 | 41207.111 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
August | 1550940000000 | 1379336.891 | 15-AUG-15:09 | 645239.307 | 326066.958 | 38964.494 | 0 | 189655.728 | 0 | 52647.908 | 41207.111 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
September | 1310550000000 | 1248253.428 | 07-SEP-15:00 | 645239.307 | 326066.958 | 34715.049 | 0 | 68555.617 | 0 | 46914 | 41207.111 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
October | 1363780000000 | 1176802.566 | 24-OCT-07:10 | 645239.307 | 326066.958 | 34592.14 | 0 | 0 | 3079 | 45603.183 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
November | 1346910000000 | 1180414.916 | 03-NOV-07:00 | 645239.307 | 326066.958 | 34592.14 | 0 | 0 | 3079 | 49215.533 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
December | 1348790000000 | 1177141.289 | 18-DEC-08:50 | 645239.307 | 326066.958 | 34592.14 | 0 | 0.152 | 3079 | 45941.754 | 0 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 16763700000000 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 1241650000000 | 1162852.821 |  | 645239.307 | 326066.958 | 34592.14 | 0 | 0 | 0 | 34732.438 | 0 | 85555.385 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 1550940000000 | 1386457.632 |  | 645239.307 | 326066.958 | 39662.356 | 0 | 200679.162 | 3079 | 52647.908 | 41207.111 | 122221.978 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 464810.61 | 117255.09 | 0 | 582065.7
Cost per Total Building Area ($/m2) | 10.03 | 2.53 | 0 | 12.57
Cost per Net Conditioned Building Area ($/m2) | 10.03 | 2.53 | 0 | 12.57

## Picture
DOE Commercial Building Benchmark - Large Office

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.1 | 0.05 | 10.5 | 56.5 | 2946.07
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 2.8
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 14.1 | 86.15 | 4492.11
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 8.45
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.3 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 9.1 | 47.4 | 2471.57
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.05 | 0.05 | 16.1
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.69 | 0.43 | 0.37 | 0.43 | 0.58 | 0.48 | 0.37 | 0.37 | 0.46 | 0.62 | 0.12 | 0.04 | 0.04 | 0 | 0 | 0 | 5.35 | 28.26 | 1473.56
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.14 | 0.21 | 0.18 | 0.25 | 0.21 | 0.13 | 0.08 | 0.04 | 0.05 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 1.51
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8 | 76 | 3962.86
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 12
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16 | 122 | 6361.43
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 18
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
INFIL_QUARTER_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 12 | 99 | 5162.14
|  |  | Sat, WinterDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1 | 15
|  |  | Sun, Hol, Other | [24 empty] | 24 | bar: 1 to 24
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.19 | 0.35 | 0.38 | 0.39 | 0.47 | 0.57 | 0.54 | 0.34 | 0.33 | 0.44 | 0.26 | 0.21 | 0.15 | 0.17 | 0.08 | 0.05 | 0.05 | 5.37 | 30.55 | 1592.96
|  |  | Sat, WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.08 | 0.07 | 0.11 | 0.15 | 0.21 | 0.19 | 0.23 | 0.2 | 0.19 | 0.15 | 0.13 | 0.14 | 0.07 | 0.07 | 0.07 | 0.07 | 0.09 | 0.05 | 0.05 | 2.57
|  |  | Sun, Hol, Other | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.06 | 0.09 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.07 | 0.04 | 0.04 | 1.13
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 92 | 4797.14
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 450 | 3058.2 | 159463.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624 | 4488 | 234017.14
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 30 | 648
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 15 | 86 | 4484.29
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 11
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Core_bottom Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_bottom Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_bottom Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_bottom Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Core_mid Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_mid Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_mid Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_mid Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Core_top Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Core_top Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Core_top Water Equipment Temp Sched | Temperature | Through 12/31 | All | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 48.8 | 1171.2 | 8198.4 | 427488
Core_top Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720