## BuildingSummary
Building Summary Outpatient Health Care post-1980 construction
|  | Value | Data Source
Program
| Building Name | Outpatient Health Care
| Available Fuel Types | gas, electricity
| Principal Building Activity | Health care, outpatient
Form
| Total Floor Area (m2) | 3804.01 | Doebber, I.; Bonnema, E.; Pless, S.; Torcellini, P. (2009). Technical Support Document: Development of the Advanced Energy Design Guide for Small Hospitals and Health Care Facilities – 30% Energy Savings. Golden, CO: National Renewable Energy Laboratory, NREL/TP-550-46314. Available at www.nrel.gov/docs/fy10osti/46314.pdf
| Building Shape | Irregular
| Aspect Ratio | 1.43
| Number of Floors | 3
Window Fraction (Window to Wall Ratio)
| South | 0.2408
| East | 0.1914
| North | 0.2052
| West | 0.1288
| Total | 0.1985
| Skylight/TDD Percentage | 0
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Zoned By Use
| Floor to Ceiling Height (m) | 3.05
| Floor to Floor Height (m) | 3.05
| Roof type | Built-up flat roof, insulation entirely above deck | Doebber, et al. 2009
Fabric
Exterior walls
| Construction Type | Steel frame | Doebber, et al. 2009
| Gross Dimensions - Total Area (m2) | 1553.34
| Net Dimensions - Total Area (m2) | 1245.05
| Wall to Skin Ratio | 0.53076
Roof
| Construction Type | IEAD | Doebber, et al. 2009
| Gross Dimensions - Total Area (m2) | 1373.29
| Net Dimensions - Total Area (m2) | 1373.29
| Roof to Skin Ratio | 0.46924
Window Dimensions (m2)
| South | 114.08
| East | 57.97
| North | 97.22
| West | 39.02
| Total Area (m2) | 308.29
| Operable area (m2) | 0
Skylights/TDD
| Dimensions - Total Area (m2) | 0
| Operable area (m2) | 0
Foundation
| Foundation Type | Mass Floor | Doebber, et al. 2009
| Construction | 8in slab w/carpet | Doebber, et al. 2009
| Dimensions - Total Area (m2) | 1373.29
Interior Partitions
| Construction | Gypsum Board
Dimensions - Total Area (m2)
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 2746.58
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ft3/min per ft2 of exterior wall) | 0.93401
HVAC
| System Type | Packaged VAV With Reheat | Doebber, et al. 2009
| Heating Type | Hot Water Boiler, Furnace | Doebber, et al. 2009
| Cooling Type | DX Cooling Coil | Doebber, et al. 2009
| Fan Control | VAV | Doebber, et al. 2009
Service Water Heating
| SWH Type | Gas Water Heater
| Fuel | Gas
| Thermal Efficiency (%) | 78 | Standard 90.1-1989
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 240.48

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Floor 1 Anesthesia | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 8.36 | 2.23 |  | 0 | 22.6042 | 21.53 |  | 3.7854 |  | 6 | 60.2012 | 67.9604 | 1.1157
Floor 1 Bio Haz | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 3.9019 |  | 0
Floor 1 Café | Yes | 1 | 39.0193 | 118.9309 | 3.048 | 18.58 | 8.92 | 1 | 39.0193 | 13.9931 | 10.76 |  |  | 10 |  | 390.1928 |  | 0.63761
Floor 1 Clean | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 5 | 2.3412 | 13.9931 | 21.53 |  |  |  | 1.5 | 17.5587 |  | 0
Floor 1 Clean Work | Yes | 1 | 15.329 | 46.7228 | 3.048 | 0 | 0 | 5 | 3.0658 | 13.9931 | 21.53 |  |  |  | 1.5 | 22.9935 |  | 0
Floor 1 Dictation | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 20 | 0.58529 | 19.375 | 11.84 |  |  | 10 |  | 5.8529 |  | 0
Floor 1 Dressing Room | Yes | 1 | 4.1806 | 12.7426 | 3.048 | 8.36 | 2.32 | 20 | 0.20903 | 19.375 | 11.84 |  |  | 10 |  | 2.0903 |  | 2.6777
Floor 1 Electrical Room | Yes | 1 | 9.1045 | 27.7505 | 3.048 | 6.5 | 0 |  | 0 | 7.5347 | 53.82 |  |  |  | 0.25 | 2.2761 |  | 0.95598
Floor 1 Elevator Pump Room | Yes | 1 | 8.4542 | 25.7684 | 3.048 | 18.58 | 0 |  | 0 | 7.5347 | 53.82 |  |  |  | 0.25 | 2.1135 |  | 2.9428
Floor 1 Humid | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 | 20 | 0.25084 | 19.375 | 11.84 |  |  | 10 |  | 2.5084 |  | 0
Floor 1 IT Hall | Yes | 1 | 13.0064 | 39.6436 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 3.2516 |  | 0
Floor 1 IT Room | Yes | 1 | 10.4051 | 31.7149 | 3.048 | 0 | 0 | 20 | 0.52026 | 19.375 | 11.84 |  |  | 10 |  | 5.2026 |  | 0
Floor 1 Lobby | Yes | 1 | 57.7857 | 176.1309 | 3.048 | 20.44 | 8.92 | 3.3333 | 17.3357 | 10.7639 | 11.84 |  |  | 8 |  | 138.6857 |  | 0.47364
Floor 1 Lobby Hall | Yes | 1 | 22.2967 | 67.9605 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 5.5742 |  | 0
Floor 1 Lobby Toilet | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 10 | 50.1676 | 42.4752 | 1.4867
Floor 1 Locker Room | Yes | 1 | 61.316 | 186.8913 | 3.048 | 20.44 | 5.57 | 6.6667 | 9.1974 | 9.6875 | 32.29 |  |  | 8 |  | 73.5792 |  | 0.44637
Floor 1 Locker Room Hall | Yes | 1 | 46.0799 | 140.4517 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 11.52 |  | 0
Floor 1 Lounge | Yes | 1 | 33.4451 | 101.9407 | 3.048 | 0 | 0 | 6.6667 | 5.0168 | 9.6875 | 32.29 |  |  | 8 | 0 | 40.1341 |  | 0
Floor 1 Med Gas | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 13.94 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 3.9019 |  | 4.9269
Floor 1 MRI Control Room | Yes | 1 | 15.6077 | 47.5723 | 3.048 | 4.65 | 0 | 5 | 3.1215 | 22.6042 | 11.84 |  | 3.7854 |  | 1.5 | 23.4116 | 79.2871 | 0.39894
Floor 1 MRI Hall | Yes | 1 | 13.6567 | 41.6258 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 3.4142 |  | 0
Floor 1 MRI Room | Yes | 1 | 40.8773 | 124.5942 | 3.048 | 0 | 0 | 5 | 8.1755 | 22.6042 | 571.116 |  | 3.7854 |  | 1.5 | 61.316 | 207.6567 | 0
Floor 1 MRI Toilet | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 10 | 50.1676 | 42.4752 | 1.4867
Floor 1 Nourishment | Yes | 1 | 16.9084 | 51.5367 | 3.048 | 0 | 0 | 5 | 3.3817 | 22.6042 | 21.53 |  |  | 10 |  | 33.8167 |  | 0
Floor 1 Nurse Hall | Yes | 1 | 46.0799 | 140.4517 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 11.52 |  | 0
Floor 1 Nurse Janitor | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 3.7626 |  | 0
Floor 1 Nurse Station | Yes | 1 | 24.2477 | 73.907 | 3.048 | 0 | 0 | 5 | 4.8495 | 22.6042 | 21.53 |  |  | 10 |  | 48.4954 |  | 0
Floor 1 Nurse Toilet | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 10 | 50.1676 | 42.4752 | 0
Floor 1 Office | Yes | 1 | 44.8722 | 136.7705 | 3.048 | 0 | 0 | 20 | 2.2436 | 19.375 | 11.84 |  |  | 10 |  | 22.4361 |  | 0
Floor 1 Operating Room 1 | Yes | 1 | 42.7354 | 130.2576 | 3.048 | 39.95 | 8.92 | 5 | 8.5471 | 75.3473 | 43.07 | 75.29 | 22.7124 |  |  | 108.5479 |  | 1.2518
Floor 1 Operating Room 2 | Yes | 1 | 44.5935 | 135.921 | 3.048 | 22.3 | 6.69 | 5 | 8.9187 | 75.3473 | 43.07 | 75.29 | 22.7124 |  |  | 113.2674 |  | 0.66961
Floor 1 Operating Room 3 | Yes | 1 | 44.2218 | 134.7883 | 3.048 | 0 | 0 | 5 | 8.8444 | 75.3473 | 43.07 | 75.29 | 22.7124 |  |  | 112.3235 |  | 0
Floor 1 PACU | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 | 5 | 2.0067 | 24.757 | 32.29 |  | 3.7854 |  |  | 16.9901 |  | 0
Floor 1 Pre-Op Hall | Yes | 1 | 49.0528 | 149.5131 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 12.2632 |  | 0
Floor 1 Pre-Op Room 1 | Yes | 1 | 17.5587 | 53.5189 | 3.048 | 3.72 | 0 | 10 | 1.7559 | 15.0695 | 21.53 |  | 3.7854 |  |  | 29.7327 |  | 0.28369
Floor 1 Pre-Op Room 2 | Yes | 1 | 31.4012 | 95.711 | 3.048 | 0 | 0 | 10 | 3.1401 | 15.0695 | 21.53 |  | 3.7854 |  |  | 53.1727 |  | 0
Floor 1 Pre-Op Toilet | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 10 | 50.1676 | 42.4752 | 1.4867
Floor 1 Procedure Room | Yes | 1 | 26.4774 | 80.7031 | 3.048 | 17.65 | 5.57 | 5 | 5.2955 | 17.2222 | 32.29 |  | 3.7854 |  |  | 67.2525 |  | 0.89261
Floor 1 Reception | Yes | 1 | 47.2876 | 144.1329 | 3.048 | 12.08 | 3.34 | 3.3333 | 14.1863 | 10.7639 | 11.84 |  |  | 8 |  | 113.4904 |  | 0.34207
Floor 1 Reception Hall | Yes | 1 | 11.8916 | 36.2456 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 2.9729 |  | 0
Floor 1 Recovery Room | Yes | 1 | 50.1676 | 152.9111 | 3.048 | 41.81 | 8.92 | 5 | 10.0335 | 24.757 | 32.29 |  | 3.7854 |  |  | 84.9505 |  | 1.116
Floor 1 Scheduling | Yes | 1 | 11.0555 | 33.6971 | 3.048 | 6.5 | 0.74 | 20 | 0.55277 | 19.375 | 11.84 |  |  | 10 |  | 5.5277 |  | 0.78728
Floor 1 Scrub | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 1.951 |  | 0
Floor 1 Soil | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 | 5 | 2.3412 | 9.6875 | 21.53 |  |  |  | 7.5 | 87.7934 | 99.1089 | 0
Floor 1 Soil Hold | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 | 5 | 1.0405 | 9.6875 | 21.53 |  |  |  | 7.5 | 39.0193 | 44.0468 | 0
Floor 1 Soil Work | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 0 | 0 | 5 | 3.3445 | 9.6875 | 21.53 |  |  |  | 7.5 | 125.4191 | 141.5841 | 0
Floor 1 Step Down | Yes | 1 | 27.8709 | 84.9506 | 3.048 | 34.37 | 6.69 | 5 | 5.5742 | 24.757 | 32.29 |  | 3.7854 |  |  | 47.1947 |  | 1.6513
Floor 1 Sterile Hall | Yes | 1 | 57.2283 | 174.4319 | 3.048 | 7.43 | 2.23 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 14.3071 |  | 0.17385
Floor 1 Sterile Storage | Yes | 1 | 36.7896 | 112.1348 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 27.5922 |  | 0
Floor 1 Storage | Yes | 1 | 85.4708 | 260.5152 | 3.048 | 58.5301 | 8.36 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 64.1031 |  | 2.256
Floor 1 Sub-Sterile | Yes | 1 | 18.209 | 55.5011 | 3.048 | 13.01 | 2.97 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5522 |  | 0.95671
Floor 1 Utility Hall | Yes | 1 | 23.7832 | 72.4912 | 3.048 | 14.86 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 5.9458 |  | 0.83664
Floor 1 Utility Janitor | Yes | 1 | 3.9019 | 11.8931 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 2.9264 |  | 0
Floor 1 Utility Room | Yes | 1 | 33.4451 | 101.9407 | 3.048 | 16.72 | 2.23 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 25.0838 |  | 2.0084
Floor 1 Vestibule | Yes | 1 | 6.689 | 20.3881 | 3.048 | 7.43 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 1.6723 |  | 1.4874
Floor 2 Conference | Yes | 1 | 31.2154 | 95.1447 | 3.048 | 37.16 | 8.92 | 2 | 15.6077 | 19.375 | 10.76 |  |  | 10 |  | 156.0771 |  | 1.594
Floor 2 Conference Toilet | Yes | 1 | 5.9458 | 18.1228 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 10 | 59.4579 | 50.3426 | 0
Floor 2 Dictation | Yes | 1 | 6.5032 | 19.8218 | 3.048 | 0 | 0 | 20 | 0.32516 | 19.375 | 11.84 |  |  | 10 |  | 3.2516 |  | 0
Floor 2 Exam 1 | Yes | 1 | 33.4451 | 101.9407 | 3.048 | 39.02 | 8.92 | 5 | 6.689 | 17.2222 | 11.84 |  |  |  | 1.5 | 50.1676 |  | 1.5622
Floor 2 Exam 2 | Yes | 1 | 50.1676 | 152.9111 | 3.048 | 16.72 | 3.72 | 5 | 10.0335 | 17.2222 | 11.84 |  |  |  | 1.5 | 75.2515 |  | 0.44628
Floor 2 Exam 3 | Yes | 1 | 66.8902 | 203.8815 | 3.048 | 22.3 | 5.95 | 5 | 13.378 | 17.2222 | 11.84 |  |  |  | 1.5 | 100.3353 |  | 0.44641
Floor 2 Exam 4 | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 6.5 | 2.23 | 5 | 1.5608 | 17.2222 | 11.84 |  |  |  | 1.5 | 11.7058 |  | 1.1153
Floor 2 Exam 5 | Yes | 1 | 32.5161 | 99.109 | 3.048 | 23.23 | 5.95 | 5 | 6.5032 | 17.2222 | 11.84 |  |  |  | 1.5 | 48.7741 |  | 0.95663
Floor 2 Exam 6 | Yes | 1 | 20.9032 | 63.713 | 3.048 | 13.94 | 4.18 | 5 | 4.1806 | 17.2222 | 11.84 |  |  |  | 1.5 | 31.3548 |  | 0.89298
Floor 2 Exam 7 | Yes | 1 | 73.5792 | 224.2696 | 3.048 | 22.3 | 5.57 | 5 | 14.7158 | 17.2222 | 11.84 |  |  |  | 1.5 | 110.3688 |  | 0.40583
Floor 2 Exam 8 | Yes | 1 | 25.0838 | 76.4556 | 3.048 | 16.72 | 5.57 | 5 | 5.0168 | 17.2222 | 11.84 |  |  |  | 1.5 | 37.6257 |  | 0.89255
Floor 2 Exam 9 | Yes | 1 | 36.7896 | 112.1348 | 3.048 | 11.15 | 2.79 | 5 | 7.3579 | 17.2222 | 11.84 |  |  |  | 1.5 | 55.1844 |  | 0.40583
Floor 2 Exam Hall 1 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.44601
Floor 2 Exam Hall 2 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.44601
Floor 2 Exam Hall 3 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.1806 |  | 0.44601
Floor 2 Exam Hall 4 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.40546
Floor 2 Exam Hall 5 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.40546
Floor 2 Exam Hall 6 | Yes | 1 | 18.3948 | 56.0674 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.5987 |  | 0.40546
Floor 2 Janitor | Yes | 1 | 5.8529 | 17.8396 | 3.048 | 14.86 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 4.3897 |  | 3.3997
Floor 2 Lounge | Yes | 1 | 7.4322 | 22.6535 | 3.048 | 0 | 0 | 6.6667 | 1.1148 | 9.6875 | 32.29 |  |  | 8 |  | 8.9187 |  | 0
Floor 2 Nurse Station 1 | Yes | 1 | 13.9355 | 42.4753 | 3.048 | 0 | 0 | 5 | 2.7871 | 22.6042 | 21.53 |  |  | 10 |  | 27.8709 |  | 0
Floor 2 Nurse Station 2 | Yes | 1 | 16.7225 | 50.9704 | 3.048 | 0 | 0 | 5 | 3.3445 | 22.6042 | 21.53 |  |  | 10 |  | 33.4451 |  | 0
Floor 2 Office | Yes | 1 | 52.0257 | 158.5745 | 3.048 | 37.16 | 8.92 | 20 | 2.6013 | 19.375 | 11.84 |  |  | 10 |  | 26.0129 |  | 0.95642
Floor 2 Office Hall | Yes | 1 | 41.2489 | 125.7269 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 10.3122 |  | 0
Floor 2 Reception | Yes | 1 | 91.4166 | 278.638 | 3.048 | 45.52 | 16.72 | 3.3333 | 27.425 | 10.7639 | 11.84 |  |  | 8 |  | 219.3998 |  | 0.66676
Floor 2 Reception Hall | Yes | 1 | 52.3973 | 159.7072 | 3.048 | 87.3301 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 13.0993 |  | 2.2318
Floor 2 Reception Toilet | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 10 | 117.0578 | 99.1089 | 0
Floor 2 Scheduling 1 | Yes | 1 | 30.1006 | 91.7467 | 3.048 | 0 | 0 | 20 | 1.505 | 19.375 | 11.84 |  |  | 10 |  | 15.0503 |  | 0
Floor 2 Scheduling 2 | Yes | 1 | 31.7728 | 96.8437 | 3.048 | 0 | 0 | 20 | 1.5886 | 19.375 | 11.84 |  |  | 10 |  | 15.8864 |  | 0
Floor 2 Storage 1 | Yes | 1 | 5.2026 | 15.8574 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 3.9019 |  | 0
Floor 2 Storage 2 | Yes | 1 | 11.1484 | 33.9802 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 8.3613 |  | 0
Floor 2 Storage 3 | Yes | 1 | 13.378 | 40.7763 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 10.0335 |  | 0
Floor 2 Utility | Yes | 1 | 11.7058 | 35.6793 | 3.048 | 8.36 | 2.23 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 8.7793 |  | 0.95631
Floor 2 Work | Yes | 1 | 157.0061 | 478.5551 | 3.048 | 24.15 | 5.57 | 20 | 7.8503 | 19.375 | 11.84 |  |  | 10 |  | 78.5031 |  | 0.20596
Floor 2 Work Hall | Yes | 1 | 77.4811 | 236.1627 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 19.3703 |  | 0.096261
Floor 2 Work Toilet | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 10 | 50.1676 | 42.4752 | 1.4867
Floor 2 X-Ray | Yes | 1 | 83.6127 | 254.8518 | 3.048 | 0 | 0 | 5 | 16.7225 | 22.6042 | 14.0206 |  | 3.7854 |  | 1.5 | 125.4191 |  | 0
Floor 3 Dressing Room | Yes | 1 | 3.9019 | 11.8931 | 3.048 | 0 | 0 | 20 | 0.1951 | 19.375 | 11.84 |  |  | 10 |  | 1.951 |  | 1.339
Floor 3 Elevator Hall | Yes | 1 | 34.3741 | 104.7724 | 3.048 | 3.72 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 8.5935 |  | 1.4839
Floor 3 Humid | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 | 20 | 0.50168 | 19.375 | 11.84 |  |  | 10 | 0 | 5.0168 |  | 1.339
Floor 3 Janitor | Yes | 1 | 5.8529 | 17.8396 | 3.048 | 14.86 | 0 |  | 0 | 8.6111 | 1.08 |  |  |  | 0.75 | 4.3897 |  | 4.7387
Floor 3 Locker | Yes | 1 | 11.1484 | 33.9802 | 3.048 | 0 | 0 | 6.6667 | 1.6723 | 9.6875 | 32.29 |  |  | 8 |  | 13.378 |  | 1.339
Floor 3 Lounge | Yes | 1 | 70.5134 | 214.925 | 3.048 | 21.37 | 5.57 | 6.6667 | 10.577 | 9.6875 | 32.29 |  |  | 8 |  | 84.6161 |  | 1.7448
Floor 3 Lounge Toilet | Yes | 1 | 17.8374 | 54.3684 | 3.048 | 11.15 | 4.18 |  | 0 | 8.6111 | 4.31 |  |  |  | 10 | 178.3738 | 151.023 | 2.1761
Floor 3 Mechanical | Yes | 1 | 32.5161 | 99.109 | 3.048 | 23.23 | 5.95 |  | 0 | 7.5347 | 53.82 |  |  |  | 0.25 | 8.129 |  | 2.2957
Floor 3 Mechanical Hall | Yes | 1 | 27.8709 | 84.9506 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 6.9677 |  | 1.339
Floor 3 Office | Yes | 1 | 282.0536 | 859.7002 | 3.048 | 68.7501 | 19.51 | 20 | 14.1027 | 19.375 | 11.84 |  |  | 10 |  | 141.0268 |  | 1.6654
Floor 3 Office Hall | Yes | 1 | 77.4811 | 236.1627 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 19.3703 |  | 1.4353
Floor 3 Office Toilet | Yes | 1 | 5.0168 | 15.2911 | 3.048 | 5.57 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 10 | 50.1676 | 42.4752 | 2.8257
Floor 3 Physical Therapy 1 | Yes | 1 | 120.774 | 368.1193 | 3.048 | 78.9701 | 28.99 | 5 | 24.1548 | 17.2222 | 16.15 |  | 3.7854 | 8 |  | 193.2383 |  | 2.2146
Floor 3 Physical Therapy 2 | Yes | 1 | 54.9986 | 167.6359 | 3.048 | 0 | 0 | 5 | 10.9997 | 17.2222 | 16.15 |  | 3.7854 | 8 |  | 87.9978 |  | 1.339
Floor 3 Physical Therapy Toilet | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 10 | 78.0386 | 66.0726 | 1.339
Floor 3 Storage 1 | Yes | 1 | 10.0335 | 30.5822 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 7.5251 |  | 1.339
Floor 3 Storage 2 | Yes | 1 | 7.8039 | 23.7862 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 5.8529 |  | 1.339
Floor 3 Treatment | Yes | 1 | 44.2218 | 134.7883 | 3.048 | 0 | 0 | 5 | 8.8444 | 17.2222 | 11.84 |  |  |  | 1.5 | 66.3328 |  | 1.339
Floor 3 Undeveloped 1 | Yes | 1 | 210.7041 | 642.2266 | 3.048 | 66.8901 | 25.64 | 20 | 10.5352 | 19.375 | 11.84 |  |  |  | 0.75 | 158.0281 |  | 1.7641
Floor 3 Undeveloped 2 | Yes | 1 | 107.0243 | 326.2103 | 3.048 | 52.03 | 13.38 | 20 | 5.3512 | 19.375 | 11.84 |  |  |  | 0.75 | 80.2682 |  | 1.99
Floor 3 Utility | Yes | 1 | 20.0671 | 61.1644 | 3.048 | 0 | 0 |  | 0 | 10.7639 | 1.08 |  |  |  | 0.75 | 15.0503 |  | 1.339
Floor 3 Work | Yes | 1 | 53.3263 | 162.5388 | 3.048 | 38.09 | 8.92 | 20 | 2.6663 | 19.375 | 11.84 |  |  | 10 |  | 26.6632 |  | 2.2955
NE Stair | Yes | 1 | 15.6077 | 142.717 | 9.144 | 97.5501 | 12.02 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 3.9019 |  | 1
NW Elevator | Yes | 1 | 13.0064 | 118.9309 | 9.144 | 75.2501 | 0 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 3.2516 |  | 1
NW Stair | Yes | 1 | 17.8374 | 163.1052 | 9.144 | 111.4801 | 11.15 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 4.4593 |  | 1
SW Stair | Yes | 1 | 8.9187 | 81.5526 | 9.144 | 55.7401 | 1.11 |  | 0 | 8.6111 | 4.31 |  |  |  | 0.25 | 2.2297 |  | 1
Total Conditioned Zones |  |  | 3804.0079 | 11932.163 |  | 1634.1215 | 308.28 |  | 414.8028
Data Source | [7 empty] | 1 |  | 2 | 5 | 5 | 5 | 3, 4 | 3, 4 | 3, 4 | 5 | 6
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] AIA Guidelines for Design and Construction of Hospital and Health Care Facilities: 2001 Edition. Washington, D.C.: American Institute of Architects.
[4] Green Guide for Health Care: Best Practices for Creating High Performance Healing Environments, Version 2.2. www.gghc.org.
[5] Doebber, I.; Bonnema, E.; Pless, S.; Torcellini, P. (2009). Technical Support Document: Development of the Advanced Energy Design Guide for Small Hospitals and Health
[6] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet | 8in slab w/carpet
| R-value (m2·K / W) | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463 | 0.61463
HVAC
HVAC Sizing
Air Conditioning (kW)
| AHU-1_COOLC DXCOIL | 467.2303 | 439.1778 | 423.9217 | 415.705 | 373.6607 | 379.5113 | 323.4509 | 413.3697 | 331.9888 | 337.4255 | 410.3962 | 326.5513 | 399.4116 | 316.3156 | 361.0025 | 312.3371
| AHU-2_COOLC DXCOIL | 447.1223 | 391.7273 | 388.5484 | 366.5701 | 327.0639 | 331.5523 | 278.3421 | 353.276 | 306.4029 | 275.6836 | 350.831 | 286.4849 | 329.0467 | 274.4998 | 289.9183 | 266.0202
Heating (kW)
| HEATSYS1 BOILER | 183.888 | 177.0135 | 171.2432 | 176.9943 | 166.0147 | 165.8347 | 161.9802 | 183.077 | 164.5394 | 173.0589 | 194.953 | 175.0135 | 200.4843 | 190.6818 | 201.2038 | 227.4881
HVAC Efficiency
Air Conditioning (COP)
| AHU-1_COOLC DXCOIL | 2.75 | 2.75 | 2.8 | 2.79 | 2.86 | 2.88 | 2.91 | 2.76 | 3.07 | 2.9 | 2.77 | 3.07 | 2.79 | 3.05 | 2.85 | 2.96
| AHU-2_COOLC DXCOIL | 2.86 | 2.81 | 2.91 | 2.87 | 3.01 | 3.01 | 3.07 | 2.83 | 3.07 | 3.07 | 2.83 | 3.07 | 2.85 | 3.07 | 2.93 | 3.07
Heating Efficiency (%)
| HEATSYS1 BOILER | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
HVAC Control - Economizer
| AHU-1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| AHU-2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| AHU-1_FAN | 19.54 | 18.1 | 19.02 | 18.3 | 18.18 | 18.87 | 16.76 | 17.47 | 20.06 | 17.3 | 17.63 | 19.73 | 17.59 | 18.82 | 17.42 | 17
| AHU-2_FAN | 21.71 | 17.91 | 20.1 | 18.01 | 18.78 | 19.11 | 16.81 | 16.45 | 18.51 | 16.65 | 16.4 | 17.31 | 15.67 | 16.58 | 15.31 | 16.07
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.078506 | 0.10554 | 0.074559 | 0.098748 | 0.1221 | 0.08924 | 0.14574 | 0.067497 | 0.037018 | 0.072475 | 0.096924 | 0.037022 | 0.053557 | 0.070109 | 0.053828 | 0.089376
| Total Cost ($/m2) | 54.02 | 64.34 | 45.45 | 56.21 | 63.67 | 53.72 | 60.28 | 36.87 | 20.73 | 31.24 | 50.05 | 19.99 | 27.59 | 36.58 | 26.55 | 47.07
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011446 | 0.0081929 | 0.0086196 | 0.010906 | 0.0083917 | 0.0082015 | 0.0083915 | 0.010147 | 0.0072481 | 0.0082684 | 0.0090174 | 0.0072449 | 0.0080023 | 0.0088712 | 0.0080023 | 0.0041936
| Total Cost ($/m2) | 18.48 | 12.9 | 14 | 17.86 | 14.25 | 12.81 | 13.42 | 16.72 | 10.85 | 13.77 | 15.32 | 11.05 | 14.15 | 14.5 | 14.41 | 9.22
Total Utility Costs
| Cost Intensity ($/m2) | 72.5 | 77.24 | 59.45 | 74.07 | 77.92 | 66.54 | 73.71 | 53.59 | 31.58 | 45.01 | 65.37 | 31.04 | 41.75 | 51.07 | 40.96 | 56.29
Energy - End Uses
Electricity (kWh)
| Heating | 52186.1111 | 76322.2222 | 78541.6667 | 108241.6667 | 95794.4444 | 84244.4444 | 108869.4444 | 123297.2222 | 91613.8889 | 144330.5556 | 150444.4444 | 106322.2222 | 155950 | 142202.7778 | 175522.2222 | 267975
| Cooling | 1425000 | 1096400 | 865433.3333 | 828333.3333 | 695583.3333 | 619522.2222 | 326530.5556 | 688283.3333 | 396341.6667 | 257097.2222 | 417383.3333 | 294894.4444 | 377661.1111 | 208900 | 202619.4444 | 124419.4444
| Interior Lighting | 244377.7778 | 244377.7778 | 244377.7778 | 244377.7778 | 244377.7778 | 244377.7778 | 244377.7778 | 244377.7778 | 244377.7778 | 244377.7778 | 244377.7778 | 244377.7778 | 244377.7778 | 244377.7778 | 244377.7778 | 244377.7778
| Exterior Lighting | 8850 | 8847.2222 | 8847.2222 | 8844.4444 | 8838.8889 | 8836.1111 | 8841.6667 | 8836.1111 | 8838.8889 | 8822.2222 | 8836.1111 | 8830.5556 | 8830.5556 | 8827.7778 | 8825 | 8769.4444
| Interior Equipment | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600 | 551600
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 324119.4444 | 294580.5556 | 314725 | 296536.1111 | 297008.3333 | 310041.6667 | 272016.6667 | 282211.1111 | 325361.1111 | 279358.3333 | 284775 | 318325 | 283891.6667 | 303422.2222 | 281463.8889 | 276433.3333
| Pumps | 8941.6667 | 8608.3333 | 8330.5556 | 8608.3333 | 8077.7778 | 8069.4444 | 7883.3333 | 8902.7778 | 8008.3333 | 8419.4444 | 9475 | 8513.8889 | 9741.6667 | 9269.4444 | 9775 | 11044.4444
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 2533.3333 | 38375 | 246950 | 118733.3333 | 82311.1111 | 463363.8889 | 53347.2222 | 170350 | 503797.2222 | 145916.6667 | 297497.2222 | 521205.5556 | 327877.7778 | 516044.4444 | 402141.6667 | 518788.8889
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2617608.3333 | 2319113.8889 | 2318805.5556 | 2165272.2222 | 1983594.4444 | 2290055.5556 | 1573469.4444 | 2077858.3333 | 2129938.8889 | 1639922.2222 | 1964388.8889 | 2054069.4444 | 1959930.5556 | 1984647.2222 | 1876325 | 2003408.3333
Gas (MJ)
| Heating | 5918120 | 5757670 | 5952680 | 5994230 | 6223600 | 5711770 | 5846190 | 6028920 | 5454800 | 6093210 | 6217880 | 5558270 | 6482060 | 5969310 | 6596750 | 8101310
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370 | 188370
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 36140 | 41700 | 38470 | 47070 | 46030 | 42350 | 50630 | 51280 | 50470 | 53480 | 55000 | 54810 | 58180 | 58760 | 63470 | 69860
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 6142640 | 5987750 | 6179520 | 6229680 | 6458010 | 5942490 | 6085190 | 6268580 | 5693640 | 6335060 | 6461250 | 5801450 | 6728620 | 6216450 | 6848590 | 8359540
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 15566030 | 14336560 | 14527220 | 14024660 | 13598960 | 14186690 | 11749680 | 13748870 | 13361420 | 12238780 | 13533060 | 13196110 | 13784370 | 13361180 | 13603360 | 15571810
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 49.3874 | 72.229 | 74.3295 | 102.4366 | 90.657 | 79.7264 | 103.0307 | 116.6848 | 86.7006 | 136.5901 | 142.3761 | 100.6201 | 147.5864 | 134.5764 | 166.1089 | 253.6034
| Cooling (elec) | 1348.5769 | 1037.5998 | 819.0199 | 783.9096 | 658.279 | 586.2971 | 309.0186 | 651.3705 | 375.0858 | 243.309 | 394.999 | 279.0792 | 357.4071 | 197.6966 | 191.7529 | 117.7468
| Interior Lighting (elec) | 231.2717 | 231.2717 | 231.2717 | 231.2717 | 231.2717 | 231.2717 | 231.2717 | 231.2717 | 231.2717 | 231.2717 | 231.2717 | 231.2717 | 231.2717 | 231.2717 | 231.2717 | 231.2717
| Exterior Lighting (elec) | 8.3754 | 8.3727 | 8.3727 | 8.3701 | 8.3649 | 8.3622 | 8.3675 | 8.3622 | 8.3649 | 8.3491 | 8.3622 | 8.357 | 8.357 | 8.3543 | 8.3517 | 8.2991
| Interior Equipment (elec) | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176 | 522.0176
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 306.7368 | 278.7821 | 297.8462 | 280.6328 | 281.0797 | 293.4141 | 257.4283 | 267.0761 | 307.9119 | 264.3763 | 269.5024 | 301.2532 | 268.6665 | 287.1496 | 266.3689 | 261.6081
| Pumps (elec) | 8.4621 | 8.1467 | 7.8838 | 8.1467 | 7.6446 | 7.6367 | 7.4605 | 8.4253 | 7.5788 | 7.9679 | 8.9669 | 8.0573 | 9.2192 | 8.7723 | 9.2508 | 10.4521
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 2.3975 | 36.3169 | 233.706 | 112.3656 | 77.8967 | 438.5136 | 50.4862 | 161.2141 | 476.7785 | 138.0911 | 281.5424 | 493.2532 | 310.2936 | 488.3689 | 380.5747 | 490.9661
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2477.2253 | 2194.7392 | 2194.4474 | 2049.1481 | 1877.2138 | 2167.2393 | 1489.0839 | 1966.4223 | 2015.7097 | 1551.9728 | 1859.0382 | 1943.9092 | 1854.819 | 1878.2101 | 1775.6972 | 1895.965
Gas (MJ/m2)
| Heating (gas) | 1555.7583 | 1513.5791 | 1564.8434 | 1575.7661 | 1636.063 | 1501.5129 | 1536.8493 | 1584.8854 | 1433.9605 | 1601.786 | 1634.5593 | 1461.1607 | 1704.0071 | 1569.2151 | 1734.1569 | 2129.6763
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188 | 49.5188
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 9.5005 | 10.9621 | 10.113 | 12.3738 | 12.1004 | 11.133 | 13.3096 | 13.4805 | 13.2676 | 14.0588 | 14.4584 | 14.4085 | 15.2944 | 15.4469 | 16.685 | 18.3648
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1614.7802 | 1574.0626 | 1624.4752 | 1637.6613 | 1697.6848 | 1562.1647 | 1599.6777 | 1647.8874 | 1496.7469 | 1665.3637 | 1698.5365 | 1525.088 | 1768.8229 | 1634.1834 | 1800.3607 | 2197.5599
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 4092.0055 | 3768.8019 | 3818.9227 | 3686.8094 | 3574.9012 | 3729.404 | 3088.7616 | 3614.3096 | 3512.4566 | 3217.3364 | 3557.5774 | 3468.9998 | 3623.6419 | 3512.3935 | 3576.0579 | 4093.525
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 434.7615 | 405.7336 | 399.9788 | 365.8684 | 398.3721 | 393.0944 | 357.889 | 370.9692 | 375.6002 | 355.879 | 377.2492 | 382.1833 | 390.0803 | 393.1939 | 404.7797 | 422.0817
| Feb | 442.2383 | 380.451 | 405.2012 | 374.5604 | 386.8445 | 390.7535 | 325.5927 | 364.3657 | 383.036 | 372.7626 | 351.6851 | 367.1596 | 365.6864 | 393.5582 | 387.0629 | 414.082
| Mar | 446.0101 | 394.4591 | 442.0171 | 378.4003 | 396.6779 | 388.1806 | 360.7037 | 359.4009 | 394.8448 | 349.8913 | 351.6842 | 402.4215 | 356.2028 | 380.1833 | 360.9073 | 387.5256
| Apr | 453.6783 | 414.2294 | 435.4916 | 384.5763 | 425.0584 | 390.958 | 371.2663 | 352.7071 | 427.6184 | 338.4509 | 385.4906 | 383.2712 | 366.0635 | 380.7022 | 355.2688 | 362.4607
| May | 477.7693 | 454.4561 | 475.6149 | 416.967 | 372.723 | 472.6604 | 335.2734 | 402.6587 | 418.1023 | 341.9469 | 397.5479 | 393.9432 | 389.3982 | 380.0024 | 381.5387 | 383.7538
| Jun | 491.6888 | 458.3569 | 552.1887 | 430.0625 | 372.0888 | 505.1923 | 340.7326 | 447.8082 | 462.0906 | 346.0538 | 434.8056 | 414.8417 | 423.1042 | 392.8119 | 382.0211 | 366.1429
| Jul | 478.943 | 463.8568 | 521.594 | 456.2848 | 374.0154 | 482.3697 | 361.1959 | 451.0246 | 448.606 | 368.5389 | 438.3782 | 408.7333 | 422.2598 | 389.997 | 394.4161 | 344.2298
| Aug | 487.8221 | 467.7164 | 518.3489 | 436.9374 | 394.0318 | 459.9451 | 356.515 | 451.2665 | 396.3528 | 362.228 | 433.6181 | 406.8375 | 421.9956 | 378.1785 | 387.75 | 374.1829
| Sep | 478.0167 | 456.7288 | 478.4528 | 415.8105 | 393.9016 | 458.5678 | 384.6192 | 409.8233 | 402.4755 | 368.2996 | 398.6045 | 421.5566 | 391.0512 | 373.2242 | 371.0719 | 351.6962
| Oct | 473.0052 | 433.8296 | 430.5132 | 401.3568 | 394.6717 | 415.4957 | 336.4778 | 384.4785 | 388.7312 | 315.9832 | 387.3544 | 398.5492 | 360.2645 | 381.4727 | 358.4189 | 368.1197
| Nov | 452.3849 | 407.8453 | 408.5687 | 355.9445 | 393.388 | 392.3605 | 348.9575 | 364.5319 | 386.0102 | 356.3425 | 365.6579 | 383.1971 | 369.2983 | 360.3014 | 360.2302 | 390.4967
| Dec | 432.3471 | 395.9126 | 403.6384 | 382.7749 | 393.1642 | 391.3838 | 343.5832 | 351.5967 | 366.7339 | 346.4444 | 361.2387 | 382.1761 | 363.3124 | 407.318 | 369.8236 | 407.1248
Time of Peak Electrical Demand
| Jan | 06-JAN-13:00 | 03-JAN-11:00 | 27-JAN-09:09 | 30-JAN-07:10 | 25-JAN-09:09 | 17-JAN-13:00 | 17-JAN-14:00 | 17-JAN-07:10 | 26-JAN-15:00 | 03-JAN-09:09 | 27-JAN-07:10 | 23-JAN-13:00 | 09-JAN-07:10 | 17-JAN-07:10 | 09-JAN-07:10 | 13-JAN-09:09
| Feb | 23-FEB-11:00 | 23-FEB-13:00 | 28-FEB-16:00 | 02-FEB-07:10 | 10-FEB-08:50 | 07-FEB-11:00 | 15-FEB-15:00 | 21-FEB-09:09 | 13-FEB-15:00 | 22-FEB-13:00 | 09-FEB-07:10 | 07-FEB-14:00 | 07-FEB-08:09 | 27-FEB-07:10 | 02-FEB-07:10 | 03-FEB-09:09
| Mar | 13-MAR-15:50 | 24-MAR-15:00 | 30-MAR-15:00 | 22-MAR-16:00 | 30-MAR-08:09 | 30-MAR-09:39 | 13-MAR-12:00 | 09-MAR-15:00 | 02-MAR-14:00 | 23-MAR-15:30 | 20-MAR-08:09 | 30-MAR-13:00 | 06-MAR-07:10 | 27-MAR-13:20 | 27-MAR-06:10 | 14-MAR-08:09
| Apr | 03-APR-14:30 | 20-APR-14:00 | 26-APR-15:00 | 14-APR-16:00 | 11-APR-15:00 | 21-APR-15:30 | 05-APR-09:00 | 04-APR-15:00 | 21-APR-16:00 | 13-APR-16:00 | 27-APR-14:00 | 06-APR-12:00 | 06-APR-15:00 | 14-APR-14:30 | 04-APR-16:00 | 10-APR-06:10
| May | 24-MAY-14:00 | 26-MAY-14:00 | 19-MAY-15:00 | 31-MAY-16:00 | 30-MAY-08:00 | 11-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 12-MAY-13:00 | 05-MAY-15:00 | 30-MAY-15:00 | 18-MAY-12:00 | 31-MAY-12:09 | 15-MAY-12:09 | 30-MAY-10:30 | 25-MAY-12:00
| Jun | 28-JUN-14:00 | 13-JUN-14:00 | 08-JUN-15:00 | 19-JUN-14:00 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-16:00 | 26-JUN-16:00 | 28-JUN-12:00 | 08-JUN-12:00 | 15-JUN-16:00 | 29-JUN-14:00 | 30-JUN-15:00 | 14-JUN-15:09 | 12-JUN-14:00
| Jul | 13-JUL-15:09 | 18-JUL-12:00 | 19-JUL-16:00 | 03-JUL-15:00 | 20-JUL-14:00 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-16:40 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-13:00 | 13-JUL-16:00 | 21-JUL-16:00 | 06-JUL-16:00 | 21-JUL-16:00
| Aug | 21-AUG-14:00 | 31-AUG-13:00 | 01-AUG-16:00 | 17-AUG-13:00 | 08-AUG-14:00 | 04-AUG-15:30 | 15-AUG-12:09 | 17-AUG-15:50 | 01-AUG-14:00 | 18-AUG-16:00 | 04-AUG-15:00 | 29-AUG-15:00 | 25-AUG-16:00 | 18-AUG-16:00 | 11-AUG-14:00 | 11-AUG-14:00
| Sep | 07-SEP-13:00 | 15-SEP-14:00 | 12-SEP-16:00 | 11-SEP-13:00 | 25-SEP-14:00 | 21-SEP-14:00 | 28-SEP-14:00 | 08-SEP-14:00 | 20-SEP-16:00 | 01-SEP-15:00 | 06-SEP-10:00 | 06-SEP-12:00 | 14-SEP-14:00 | 14-SEP-13:00 | 07-SEP-14:00 | 07-SEP-15:00
| Oct | 06-OCT-14:39 | 06-OCT-15:00 | 24-OCT-13:00 | 12-OCT-15:00 | 19-OCT-10:00 | 03-OCT-15:00 | 31-OCT-12:00 | 03-OCT-09:00 | 13-OCT-14:00 | 05-OCT-15:00 | 26-OCT-15:30 | 05-OCT-14:00 | 25-OCT-12:00 | 19-OCT-13:09 | 20-OCT-14:00 | 30-OCT-08:09
| Nov | 07-NOV-14:00 | 03-NOV-14:30 | 13-NOV-13:00 | 03-NOV-13:00 | 29-NOV-09:00 | 13-NOV-11:09 | 20-NOV-09:09 | 03-NOV-13:00 | 08-NOV-17:30 | 20-NOV-09:09 | 02-NOV-14:39 | 10-NOV-10:39 | 01-NOV-14:00 | 21-NOV-10:00 | 24-NOV-07:10 | 06-NOV-09:09
| Dec | 15-DEC-15:39 | 19-DEC-14:00 | 06-DEC-15:00 | 18-DEC-07:10 | 18-DEC-08:20 | 04-DEC-11:39 | 29-DEC-09:09 | 11-DEC-09:09 | 08-DEC-14:00 | 11-DEC-07:10 | 26-DEC-09:09 | 11-DEC-07:10 | 20-DEC-07:10 | 11-DEC-07:10 | 21-DEC-08:09 | 29-DEC-09:09
Source Energy
| Total Source Energy (GJ) | 37965.14 | 36861.5 | 33151.8 | 33025.13 | 29153.37 | 35978.7 | 24176.61 | 33594.81 | 31659.16 | 17202.16 | 32132.3 | 30870.65 | 31598.27 | 31623.45 | 30694.81 | 34890.86
| Total Source Energy (MJ/m2) | 9980.3 | 9690.17 | 8714.97 | 8681.67 | 7663.86 | 9458.1 | 6355.56 | 8831.42 | 8322.58 | 4522.12 | 8446.96 | 8115.3 | 8306.57 | 8313.19 | 8069.07 | 9172.13
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 3.39 | 51.39 | 330.71 | 159.01 | 110.23 | 620.54 | 71.44 | 228.13 | 674.69 | 195.41 | 398.41 | 698 | 439.1 | 691.09 | 538.55 | 694.76
| Water Systems | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48 | 240.48
| Total Building | 243.87 | 291.87 | 571.19 | 399.49 | 350.71 | 861.02 | 311.92 | 468.61 | 915.17 | 435.89 | 638.89 | 938.48 | 679.57 | 931.57 | 779.03 | 935.24
Emissions
| Carbon Equivalent (kg) | 828646.6902 | 881541.1959 | 811423.8471 | 779321.5231 | 348269.9661 | 879537.7308 | 293617.1326 | 673760.9528 | 972747.8181 | 233680.5916 | 1163830 | 943699.6582 | 792205.9013 | 837364.1156 | 765751.7724 | 714479.0519
| CO2 (kg) | 1982320 | 2253060 | 1968120 | 1838350 | 955367.9869 | 2138990 | 807979.3622 | 1584030 | 2324000 | 613789.4457 | 2753070 | 2257400 | 1897180 | 2010750 | 1837460 | 1847690
| NOX (kg) | 3222.1629 | 2834.6169 | 3074.5791 | 3217.7825 | 835.1077 | 3281.144 | 707.9644 | 2810.6296 | 3826.3933 | 755.5335 | 4705.6933 | 3704.7887 | 3140.5644 | 3288.3953 | 3025.8474 | 2164.5766
| SO2 (kg) | 11206.0549 | 11063.7776 | 9326.0349 | 7601.7784 | 5773.7548 | 12598.7287 | 4580.2347 | 7586.6955 | 9302.5456 | 1269.2256 | 13240.1474 | 8971.2701 | 4627.5542 | 5300.9142 | 4430.2645 | 10200.3925
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0517 | 0.0317 | 0.026 | 0.0284 | 0.0033 | 0.0242 | 0.0027 | 0.0312 | 0.0368 | 0.0056 | 0.0406 | 0.0356 | 0.0345 | 0.0374 | 0.033 | 0.0354
| Water for Electricity (m3) | 1386.7 | 3773.47 | 68878.7 | 13519.1 | 34827.5 | 62825.4 | 27626.6 | 471.7521 | 9671.63 | 16754.7 | 3047.63 | 9327.12 | 3040.72 | 125716 | 2911.01 | 2046.84

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15566.03 | 4092.01 | 4092.01
Net Site Energy | 15566.03 | 4092.01 | 4092.01
Total Source Energy | 37965.14 | 9980.3 | 9980.3
Net Source Energy | 37965.14 | 9980.3 | 9980.3
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 187.87 | 5918.12 | 0 | 0 | 0 | 0
Cooling | 5130 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 879.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 31.86 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1166.83 | 0 | 0 | 0 | 0 | 0
Pumps | 32.19 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 9.12 | 0 | 0 | 0 | 0 | 3.39
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 36.14 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 9423.39 | 6142.64 | 0 | 0 | 0 | 243.87
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 22.6 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 14 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 19.4 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 7.53 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 7.53 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 10.8 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 22.6 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 22.6 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 10.8 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 75.3 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 24.7 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 17.2 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 10.8 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 24.7 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 19.4 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 24.7 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 8.61 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 10.8 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 8.61 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 8.61 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 10.8 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 8.61 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 19.4 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 17.2 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 19.4 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 10.8 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 10.8 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 19.4 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 22.6 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 8.61 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 8.61 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 7.53 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 19.4 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 17.2 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 19.4 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 19.4 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 19.4 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 8.61 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 8.61 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 8.61 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 8.61 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 3.125 | 5.873 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 5.835 | 0.251 | 0.11 | No | 5F762C | 180 | S
4A8120 | WINDOW-NONRES-FIXED | 2.32 | 2.32 | 5.835 | 0.251 | 0.11 | No | 84FB73 | 0 | N
AAE778 | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 5.835 | 0.251 | 0.11 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | F629C1 | 0 | N
8128A9 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | F629C1 | 0 | N
9B1541 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 879583 | 180 | S
CF850A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 879583 | 180 | S
A6BA23 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | E326E4 | 90 | E
D10D28 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | E326E4 | 90 | E
38B811 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
591336 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
18748E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 6D2616 | 0 | N
1D94BE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 6D2616 | 0 | N
137A56 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
44E54A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
8D508E | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
B2D381 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
757D10 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 5.835 | 0.251 | 0.11 | No | EA6DC8 | 180 | S
24167A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 997723 | 180 | S
2C0938 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 997723 | 180 | S
E33BAE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | B40F89 | 270 | W
8600DD | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | CEC7BD | 180 | S
88E1FC | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
E8D997 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
F83F33 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | 61E610 | 90 | E
B1F5EE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | D95F04 | 90 | E
F52F3D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 208CCF | 90 | E
80885D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | AEF992 | 180 | S
2BE8DE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
513E2A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 54D065 | 180 | S
1AD478 | WINDOW-NONRES-FIXED | 3.72 | 3.72 | 5.835 | 0.251 | 0.11 | No | 97F00A | 180 | S
27F0AC | WINDOW-NONRES-FIXED | 5.95 | 5.95 | 5.835 | 0.251 | 0.11 | No | A497E9 | 180 | S
724114 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 88A75F | 180 | S
5635BC | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | B4E619 | 90 | E
D538C4 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | B4E619 | 90 | E
831C1D | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 5.835 | 0.251 | 0.11 | No | 9EC269 | 0 | N
9BB95F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | B316F7 | 0 | N
C0778D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | B316F7 | 0 | N
2EF63B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9621FD | 0 | N
7D2D69 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9621FD | 0 | N
C417C0 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
D23C8B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
EB042B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
E55A57 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | 4ABC66 | 180 | S
93D018 | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B55FA | 90 | E
15B02B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9C3A6A | 0 | N
820282 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 68A2D7 | 0 | N
A2790A | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 5.835 | 0.251 | 0.11 | No | CE3FEF | 0 | N
79FCEE | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | CE618F | 90 | E
EDE617 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | CE618F | 90 | E
29FA28 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
944FCE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
C41399 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
3DB407 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
5031C8 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
95BA33 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | D22917 | 90 | E
F27282 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | D22917 | 90 | E
9DF7DE | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
D0BE44 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
B0FB49 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
44F571 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | BE5F2F | 270 | W
3833A2 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
6BD844 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
86D536 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
BAF71D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
142781 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 88E360 | 0 | N
9BC521 | WINDOW-NONRES-FIXED | 5.71 | 5.71 | 5.835 | 0.251 | 0.11 | No | 88E360 | 0 | N
2111A1 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 5.835 | 0.251 | 0.11 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 2E2D0C | 0 | N
E74902 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-NONRES-FIXED | 1.11 | 1.11 | 5.835 | 0.251 | 0.11 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 97.22 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 211.08 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 183888.03 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 467230.33 | 320306.48 | 146923.85 | 0.69 | 2.75
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 447122.3 | 324830.99 | 122291.31 | 0.73 | 2.86
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2715.36 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 238.5 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 13779.44 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1822.34 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2358.15 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1273.12 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1488.29 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 3945.07 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 144765.5 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 593.87 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 676.3 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1141.15 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 18202.8 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1046.17 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 2785.51 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 12738.56 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2180.77 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 5424.89 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 3001.09 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 681.67 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 70245.63 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1239.8 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 3238.9 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2963.35 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2180.77 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 231.85 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 4179.43 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1239.8 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 4563.76 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 50016.48 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 49878.8 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 36126.47 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 2190.23 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2318.76 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 3528.62 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4656.14 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 2585.12 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9815.12 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 8228.33 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 591.81 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 16430.84 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 2194.59 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 406.68 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2892.87 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1285.71 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 4132.67 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 13110.9 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3337.25 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 1460.12 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 21562.53 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 5531.92 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 6432.59 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 184.77 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 7199.86 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 3355.44 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4461.2 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 300.92 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 8862.78 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3374.46 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4477.9 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 778.06 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4533.93 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2659.9 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4860.83 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3157 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2392.73 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 532.2 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 532.2 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 532.2 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 579.02 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 579.02 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 573.13 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1511.48 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 487.99 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 934.26 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1116.89 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 9543.98 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 864.49 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 8563.6 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 4718.25 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1247.14 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1314.29 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 90.34 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 187.51 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 223.78 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 1330.42 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 7535.31 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1815.64 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1000.64 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 4602.13 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 214.09 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1209.8 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 558.99 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1639.46 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 855.46 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 6571.74 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1335.02 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 5377.72 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 922.05 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 26884.63 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3276.59 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1105.41 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 12424.21 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3801.96 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 584.08 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 341.06 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 268.13 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2836.25 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 17816.75 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 14202.03 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 608.43 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 10148.45 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 4452.74 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 8001.74 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 6796.38 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 4104.01 | 1
AHU-1_HEATC | Coil:Heating:Water | 16260.95 | -
AHU-2_HEATC | Coil:Heating:Water | 19990.12 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 19.54 | 32895.58 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 21.71 | 36544.18 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 1012.57 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 159254.0513 | 254.4257 | 865.3638 | 0 | 0.004 | 107080.9303 | 66126.9437
February | 143191.794 | 229.0324 | 780.1924 | 0 | 0.0036 | 96541.9849 | 59484.2683
March | 161997.2316 | 260.2684 | 891.7627 | 0 | 0.0041 | 110348.9078 | 67412.3062
April | 158863.9484 | 256.3459 | 883.2627 | 0 | 0.0041 | 109298.0989 | 66219.8147
May | 173864.1171 | 284.3758 | 996.7694 | 0 | 0.0046 | 123347.2853 | 72855.684
June | 172400.3446 | 283.7367 | 1002.1912 | 0 | 0.0046 | 124019.7445 | 72418.1658
July | 175995.6458 | 291.6886 | 1039.1062 | 0 | 0.0048 | 128589.6801 | 74132.2844
August | 179940.646 | 297.9888 | 1060.5247 | 0 | 0.0049 | 131240.0206 | 75770.1336
September | 171618.6591 | 282.4296 | 997.4855 | 0 | 0.0046 | 123437.4102 | 72087.7555
October | 172210.4268 | 280.2569 | 976.1594 | 0 | 0.0045 | 120795.6155 | 72021.0388
November | 157999.5158 | 254.4303 | 874.3581 | 0 | 0.004 | 108195.7411 | 65807.3133
December | 154980.7381 | 247.1839 | 838.8789 | 0 | 0.0039 | 103803.2856 | 64310.9819
Annual Sum or Average | 1982320 | 3222.1629 | 11206.0549 | 0 | 0.0517 | 1386700 | 828646.6902
Minimum of Months | 143191.794 | 229.0324 | 780.1924 | 0 | 0.0036 | 96541.9849 | 59484.2683
Maximum of Months | 179940.646 | 297.9888 | 1060.5247 | 0 | 0.0049 | 131240.0206 | 75770.1336
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 727674000000 | 434761.464 | 06-JAN-13:00 | 58033.2 | 120867.849 | 39962.554 | 347.527 | 214529.698 | 0 | 1020.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 656056000000 | 442238.326 | 23-FEB-11:00 | 58033.2 | 120867.849 | 40670.275 | 1103.981 | 220542.386 | 0 | 1020.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 749882000000 | 446010.144 | 13-MAR-15:50 | 58033.2 | 120867.849 | 40913.811 | 85.064 | 225089.585 | 0 | 1020.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 742741000000 | 453678.288 | 03-APR-14:30 | 58033.2 | 120867.849 | 42209.257 | 68.375 | 231478.971 | 0 | 1020.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 838213000000 | 477769.29 | 24-MAY-14:00 | 58033.2 | 120867.849 | 43273.612 | 27.687 | 254546.307 | 0 | 1020.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 842783000000 | 491688.841 | 28-JUN-14:00 | 58033.2 | 120867.849 | 45410.699 | 20.499 | 266335.959 | 0 | 1020.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 873838000000 | 478942.957 | 13-JUL-15:09 | 58033.2 | 120867.849 | 43820.636 | 31.553 | 255169.084 | 0 | 1020.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 891849000000 | 487822.132 | 21-AUG-14:00 | 58033.2 | 120867.849 | 43733.533 | 62.666 | 264104.249 | 0 | 1020.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 838826000000 | 478016.737 | 07-SEP-13:00 | 58033.2 | 120867.849 | 44126.005 | 44.957 | 253924.09 | 0 | 1020.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 820873000000 | 473005.176 | 06-OCT-14:39 | 58033.2 | 120867.849 | 44883.225 | 50.613 | 248149.654 | 0 | 1020.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 735250000000 | 452384.882 | 07-NOV-14:00 | 58033.2 | 120867.849 | 43212.57 | 104.407 | 229146.22 | 0 | 1020.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 705401000000 | 432347.117 | 15-DEC-15:39 | 58033.2 | 120867.849 | 40008.4 | 230.184 | 212186.848 | 0 | 1020.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 9423390000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 656056000000 | 432347.117 |  | 58033.2 | 120867.849 | 39962.554 | 20.499 | 212186.848 | 0 | 1020.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 891849000000 | 491688.841 |  | 58033.2 | 120867.849 | 45410.699 | 1103.981 | 266335.959 | 0 | 1020.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 205497.6 | 70305.86 | 0 | 275803.46
Cost per Total Building Area ($/m2) | 54.02 | 18.48 | 0 | 72.5
Cost per Net Conditioned Building Area ($/m2) | 54.02 | 18.48 | 0 | 72.5

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 14336.56 | 3768.8 | 3768.8
Net Site Energy | 14336.56 | 3768.8 | 3768.8
Total Source Energy | 36861.5 | 9690.17 | 9690.17
Net Source Energy | 36861.5 | 9690.17 | 9690.17
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 274.76 | 5757.67 | 0 | 0 | 0 | 0
Cooling | 3947.04 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 879.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 31.85 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1060.49 | 0 | 0 | 0 | 0 | 0
Pumps | 30.99 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 138.15 | 0 | 0 | 0 | 0 | 51.39
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 41.7 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8348.81 | 5987.75 | 0 | 0 | 0 | 291.87
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 22.6 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 14 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 19.4 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 7.53 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 7.53 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 10.8 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 22.6 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 22.6 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 10.8 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 75.3 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 24.7 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 17.2 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 10.8 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 24.7 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 19.4 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 24.7 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 8.61 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 10.8 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 8.61 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 8.61 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 10.8 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 8.61 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 19.4 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 17.2 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 19.4 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 10.8 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 10.8 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 19.4 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 22.6 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 8.61 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 8.61 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 7.53 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 19.4 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 17.2 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 19.4 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 19.4 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 19.4 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 8.61 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 8.61 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 8.61 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 8.61 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.852 | 0.976 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 5.835 | 0.251 | 0.11 | No | 5F762C | 180 | S
4A8120 | WINDOW-NONRES-FIXED | 2.32 | 2.32 | 5.835 | 0.251 | 0.11 | No | 84FB73 | 0 | N
AAE778 | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 5.835 | 0.251 | 0.11 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | F629C1 | 0 | N
8128A9 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | F629C1 | 0 | N
9B1541 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 879583 | 180 | S
CF850A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 879583 | 180 | S
A6BA23 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | E326E4 | 90 | E
D10D28 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | E326E4 | 90 | E
38B811 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
591336 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
18748E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 6D2616 | 0 | N
1D94BE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 6D2616 | 0 | N
137A56 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
44E54A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
8D508E | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
B2D381 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
757D10 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 5.835 | 0.251 | 0.11 | No | EA6DC8 | 180 | S
24167A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 997723 | 180 | S
2C0938 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 997723 | 180 | S
E33BAE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | B40F89 | 270 | W
8600DD | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | CEC7BD | 180 | S
88E1FC | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
E8D997 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
F83F33 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | 61E610 | 90 | E
B1F5EE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | D95F04 | 90 | E
F52F3D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 208CCF | 90 | E
80885D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | AEF992 | 180 | S
2BE8DE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
513E2A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 54D065 | 180 | S
1AD478 | WINDOW-NONRES-FIXED | 3.72 | 3.72 | 5.835 | 0.251 | 0.11 | No | 97F00A | 180 | S
27F0AC | WINDOW-NONRES-FIXED | 5.95 | 5.95 | 5.835 | 0.251 | 0.11 | No | A497E9 | 180 | S
724114 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 88A75F | 180 | S
5635BC | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | B4E619 | 90 | E
D538C4 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | B4E619 | 90 | E
831C1D | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 5.835 | 0.251 | 0.11 | No | 9EC269 | 0 | N
9BB95F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | B316F7 | 0 | N
C0778D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | B316F7 | 0 | N
2EF63B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9621FD | 0 | N
7D2D69 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9621FD | 0 | N
C417C0 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
D23C8B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
EB042B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
E55A57 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | 4ABC66 | 180 | S
93D018 | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B55FA | 90 | E
15B02B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9C3A6A | 0 | N
820282 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 68A2D7 | 0 | N
A2790A | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 5.835 | 0.251 | 0.11 | No | CE3FEF | 0 | N
79FCEE | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | CE618F | 90 | E
EDE617 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | CE618F | 90 | E
29FA28 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
944FCE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
C41399 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
3DB407 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
5031C8 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
95BA33 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | D22917 | 90 | E
F27282 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | D22917 | 90 | E
9DF7DE | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
D0BE44 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
B0FB49 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
44F571 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | BE5F2F | 270 | W
3833A2 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
6BD844 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
86D536 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
BAF71D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
142781 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 88E360 | 0 | N
9BC521 | WINDOW-NONRES-FIXED | 5.71 | 5.71 | 5.835 | 0.251 | 0.11 | No | 88E360 | 0 | N
2111A1 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 5.835 | 0.251 | 0.11 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 2E2D0C | 0 | N
E74902 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-NONRES-FIXED | 1.11 | 1.11 | 5.835 | 0.251 | 0.11 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 97.22 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 211.08 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 177013.45 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 439177.77 | 299438.93 | 139738.84 | 0.68 | 2.75
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 391727.32 | 277815.38 | 113911.94 | 0.71 | 2.81
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2375.48 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 226.72 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 13402.19 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1811.68 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2344.77 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1263.78 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1415.29 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2510.44 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148687.53 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 589.95 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 648.4 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1132.79 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 14805.51 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1008.89 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1235.25 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 11500.19 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2102.13 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 5399.39 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2528.59 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 655.05 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 70203.26 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1235.25 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1820.38 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2949.32 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2102.13 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 220.31 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 4160.39 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1235.25 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 4529.91 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 43691.73 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 44226.03 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 36054 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 2181.28 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2234.64 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2804.86 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4639.09 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1235.25 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9779.17 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7713.68 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 568.8 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 14751.99 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1799.14 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 389.8 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2882.28 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1281 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 4117.53 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 10344.99 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2920.6 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 1402.36 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 13435.34 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 3201.11 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 4210 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 175.33 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 4472.02 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 2319.74 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3821.11 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 303.85 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 6413.97 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3136.67 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4203.63 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 705.02 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3216.78 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2205.67 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4362.97 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2667.14 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2208.74 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 367.5 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 367.5 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 367.5 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 415.27 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 415.27 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 414.16 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 620.1 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 489.69 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 937.53 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1120.9 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 6560.35 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 868.08 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 7561.06 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2391.13 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1258.03 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1325.88 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 91.99 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 192.47 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 230.03 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 822.15 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6940.31 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1674.07 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 395.46 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 4625.7 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 213.78 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 925.79 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 543.32 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 720.19 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 838.5 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5952.99 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1330.12 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3991.61 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 922.62 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 24246.18 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2611.92 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 472.07 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 11507.37 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3720.17 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 581.93 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 343.67 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 268.55 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2772.74 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 15784.14 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 12000.34 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 612.24 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6886.55 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2263.89 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2763.93 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 3312.94 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1721.83 | 1
AHU-1_HEATC | Coil:Heating:Water | 13868.88 | -
AHU-2_HEATC | Coil:Heating:Water | 41554.72 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.1 | 30467.93 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.91 | 30143.65 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 974.71 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 181160.8667 | 225.7938 | 859.7961 | 0 | 0.0025 | 293235.8894 | 70607.4133
February | 155906.0457 | 193.6901 | 731.1567 | 0 | 0.0021 | 249359.8248 | 60683.5544
March | 179583.1908 | 224.2619 | 858.3935 | 0 | 0.0025 | 292759.7928 | 70048.5186
April | 178261.2906 | 223.4421 | 863.7129 | 0 | 0.0025 | 294578.2935 | 69640.0056
May | 198252.7147 | 250.1939 | 984.294 | 0 | 0.0028 | 335712.308 | 77668.1965
June | 204666.237 | 259.8029 | 1037.3566 | 0 | 0.003 | 353817.8467 | 80376.0823
July | 211685.4481 | 269.8732 | 1089.1818 | 0 | 0.0031 | 371499.8307 | 83282.1902
August | 213046.2531 | 271.4746 | 1094.3139 | 0 | 0.0031 | 373249.6381 | 83800.3564
September | 194391.9067 | 245.9669 | 974.1633 | 0 | 0.0028 | 332260.248 | 76238.8498
October | 187774.1142 | 235.8875 | 917.1084 | 0 | 0.0026 | 312792.0199 | 73423.5298
November | 172191.0951 | 215.0812 | 823.7664 | 0 | 0.0024 | 280950.3005 | 67171.6482
December | 176140.9225 | 219.1489 | 830.5341 | 0 | 0.0024 | 283253.9944 | 68600.8507
Annual Sum or Average | 2253060 | 2834.6169 | 11063.7776 | 0 | 0.0317 | 3773470 | 881541.1959
Minimum of Months | 155906.0457 | 193.6901 | 731.1567 | 0 | 0.0021 | 249359.8248 | 60683.5544
Maximum of Months | 213046.2531 | 271.4746 | 1094.3139 | 0 | 0.0031 | 373249.6381 | 83800.3564
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 648785000000 | 405733.643 | 03-JAN-11:00 | 58033.2 | 120867.849 | 35065.92 | 1135.618 | 189648.276 | 0 | 982.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 551709000000 | 380451.043 | 23-FEB-13:00 | 58033.2 | 120867.849 | 35975.84 | 328.753 | 164262.62 | 0 | 982.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 647732000000 | 394459.072 | 24-MAR-15:00 | 58033.2 | 120867.849 | 35344.63 | 168.452 | 179062.159 | 0 | 982.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 651755000000 | 414229.363 | 20-APR-14:00 | 58033.2 | 120867.849 | 36242.372 | 90.161 | 198013 | 0 | 982.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 742764000000 | 454456.105 | 26-MAY-14:00 | 58033.2 | 120867.849 | 38608.536 | 47.166 | 235916.572 | 0 | 982.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 782823000000 | 458356.908 | 13-JUN-14:00 | 58033.2 | 120867.849 | 38849.027 | 42.097 | 239581.955 | 0 | 982.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 821944000000 | 463856.752 | 18-JUL-12:00 | 58033.2 | 120867.849 | 37786.16 | 79.835 | 246106.927 | 0 | 982.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 825816000000 | 467716.436 | 31-AUG-13:00 | 58033.2 | 120867.849 | 39499.638 | 69.034 | 248263.934 | 0 | 982.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 735126000000 | 456728.783 | 15-SEP-14:00 | 58033.2 | 120867.849 | 37859.789 | 78.59 | 238906.573 | 0 | 982.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 692053000000 | 433829.638 | 06-OCT-15:00 | 58033.2 | 120867.849 | 37889.944 | 61.291 | 215994.574 | 0 | 982.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 621603000000 | 407845.312 | 03-NOV-14:30 | 58033.2 | 120867.849 | 35960.919 | 182.425 | 191818.137 | 0 | 982.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 626700000000 | 395912.596 | 19-DEC-14:00 | 58033.2 | 120867.849 | 35281.509 | 444.881 | 180302.376 | 0 | 982.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 8348810000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 551709000000 | 380451.043 |  | 58033.2 | 120867.849 | 35065.92 | 42.097 | 164262.62 | 0 | 982.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 825816000000 | 467716.436 |  | 58033.2 | 120867.849 | 39499.638 | 1135.618 | 248263.934 | 0 | 982.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 244764.52 | 49056.94 | 0 | 293821.46
Cost per Total Building Area ($/m2) | 64.34 | 12.9 | 0 | 77.24
Cost per Net Conditioned Building Area ($/m2) | 64.34 | 12.9 | 0 | 77.24

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 14527.22 | 3818.92 | 3818.92
Net Site Energy | 14527.22 | 3818.92 | 3818.92
Total Source Energy | 33151.8 | 8714.97 | 8714.97
Net Source Energy | 33151.8 | 8714.97 | 8714.97
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 282.75 | 5952.68 | 0 | 0 | 0 | 0
Cooling | 3115.56 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 879.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 31.85 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1133.01 | 0 | 0 | 0 | 0 | 0
Pumps | 29.99 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 889.02 | 0 | 0 | 0 | 0 | 330.71
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 38.47 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8347.7 | 6179.52 | 0 | 0 | 0 | 571.19
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 22.6 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 14 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 19.4 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 7.53 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 7.53 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 10.8 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 22.6 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 22.6 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 10.8 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 75.3 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 24.7 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 17.2 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 10.8 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 24.7 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 19.4 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 24.7 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 8.61 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 10.8 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 8.61 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 8.61 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 10.8 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 8.61 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 19.4 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 17.2 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 19.4 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 10.8 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 10.8 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 19.4 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 22.6 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 8.61 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 8.61 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 7.53 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 19.4 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 17.2 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 19.4 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 19.4 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 19.4 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 8.61 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 8.61 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 8.61 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 8.61 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.363 | 1.712 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 5.835 | 0.251 | 0.11 | No | 5F762C | 180 | S
4A8120 | WINDOW-NONRES-FIXED | 2.32 | 2.32 | 5.835 | 0.251 | 0.11 | No | 84FB73 | 0 | N
AAE778 | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 5.835 | 0.251 | 0.11 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | F629C1 | 0 | N
8128A9 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | F629C1 | 0 | N
9B1541 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 879583 | 180 | S
CF850A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 879583 | 180 | S
A6BA23 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | E326E4 | 90 | E
D10D28 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | E326E4 | 90 | E
38B811 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
591336 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
18748E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 6D2616 | 0 | N
1D94BE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 6D2616 | 0 | N
137A56 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
44E54A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
8D508E | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
B2D381 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
757D10 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 5.835 | 0.251 | 0.11 | No | EA6DC8 | 180 | S
24167A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 997723 | 180 | S
2C0938 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 997723 | 180 | S
E33BAE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | B40F89 | 270 | W
8600DD | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | CEC7BD | 180 | S
88E1FC | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
E8D997 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
F83F33 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | 61E610 | 90 | E
B1F5EE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | D95F04 | 90 | E
F52F3D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 208CCF | 90 | E
80885D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | AEF992 | 180 | S
2BE8DE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
513E2A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 54D065 | 180 | S
1AD478 | WINDOW-NONRES-FIXED | 3.72 | 3.72 | 5.835 | 0.251 | 0.11 | No | 97F00A | 180 | S
27F0AC | WINDOW-NONRES-FIXED | 5.95 | 5.95 | 5.835 | 0.251 | 0.11 | No | A497E9 | 180 | S
724114 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 88A75F | 180 | S
5635BC | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | B4E619 | 90 | E
D538C4 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | B4E619 | 90 | E
831C1D | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 5.835 | 0.251 | 0.11 | No | 9EC269 | 0 | N
9BB95F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | B316F7 | 0 | N
C0778D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | B316F7 | 0 | N
2EF63B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9621FD | 0 | N
7D2D69 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9621FD | 0 | N
C417C0 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
D23C8B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
EB042B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
E55A57 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | 4ABC66 | 180 | S
93D018 | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B55FA | 90 | E
15B02B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9C3A6A | 0 | N
820282 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 68A2D7 | 0 | N
A2790A | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 5.835 | 0.251 | 0.11 | No | CE3FEF | 0 | N
79FCEE | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | CE618F | 90 | E
EDE617 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | CE618F | 90 | E
29FA28 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
944FCE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
C41399 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
3DB407 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
5031C8 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
95BA33 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | D22917 | 90 | E
F27282 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | D22917 | 90 | E
9DF7DE | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
D0BE44 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
B0FB49 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
44F571 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | BE5F2F | 270 | W
3833A2 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
6BD844 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
86D536 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
BAF71D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
142781 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 88E360 | 0 | N
9BC521 | WINDOW-NONRES-FIXED | 5.71 | 5.71 | 5.835 | 0.251 | 0.11 | No | 88E360 | 0 | N
2111A1 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 5.835 | 0.251 | 0.11 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 2E2D0C | 0 | N
E74902 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-NONRES-FIXED | 1.11 | 1.11 | 5.835 | 0.251 | 0.11 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 97.22 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 211.08 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 171243.17 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 423921.71 | 298465.39 | 125456.32 | 0.7 | 2.8
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 388548.43 | 289771.89 | 98776.54 | 0.75 | 2.91
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2872.93 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 118.69 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 14371.34 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1658.27 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2142.37 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1073.45 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1538.18 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2863.64 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148123.04 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 474.02 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 354.19 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 959.41 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 15943.31 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 577.9 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1604.83 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 11712.25 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1200.03 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 4939.44 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2581.2 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 364.91 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 69679.91 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1191.15 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 2118.71 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2717.55 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1200.03 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 114.93 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3832.1 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1191.15 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3901.42 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 46724.68 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 45753.98 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35208.98 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 2052.44 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1275.84 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2921.95 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4473.45 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1485.77 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9430.01 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 8000.3 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 317.3 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 17037.56 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 2109.92 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 212.62 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2779.37 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1235.26 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 3970.52 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 12171.2 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2565.68 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 786.16 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 14404.29 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 3937.23 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 4871.46 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 90.46 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 5307.84 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 2841.09 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4687.75 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 302.8 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 7880.44 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3570.7 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4790.37 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 890.97 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3826.25 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2571.73 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4753.84 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3092.82 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2406.78 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.82 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.82 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.82 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.98 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 483.98 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 481.75 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 976.84 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 489.71 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 937.54 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1120.91 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 7896.01 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 893.48 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 8622.93 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 4064.8 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1258.08 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1325.94 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 91.75 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 191.95 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 229.4 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 1067.2 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 7466.49 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1779.88 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 602.87 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 4625.82 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 233.76 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1081 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 536.69 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1037.38 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 756.84 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5833.75 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1282.53 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 4638.44 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1079.71 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 23256.88 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3016.75 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 649.1 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 12675.1 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3336.09 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 561.11 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 400.4 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 313.19 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2462.38 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 15880.7 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 12624.35 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 700.22 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 8365.28 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 3206.54 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 4248.16 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 4405.29 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2569.29 | 1
AHU-1_HEATC | Coil:Heating:Water | 0 | -
AHU-2_HEATC | Coil:Heating:Water | 31059.94 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 19.02 | 32017.37 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 20.1 | 33829.73 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 942.94 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 152702.7823 | 234.0145 | 690.7728 | 0 | 0.0019 | 5101530 | 62498.1611
February | 143790.3945 | 221.5104 | 658.8043 | 0 | 0.0018 | 4865510 | 58967.1941
March | 157837.6015 | 244.3639 | 731.9438 | 0 | 0.002 | 5405740 | 64850.5558
April | 159732.3153 | 249.3251 | 755.4 | 0 | 0.0021 | 5579100 | 65834.0988
May | 168566.3156 | 264.2142 | 805.1357 | 0 | 0.0022 | 5946490 | 69586.3017
June | 177150.5365 | 280.6469 | 867.6772 | 0 | 0.0024 | 6408580 | 73431.0763
July | 186388.4576 | 296.9973 | 925.3343 | 0 | 0.0026 | 6834520 | 77433.7841
August | 185881.9138 | 295.6192 | 918.6887 | 0 | 0.0025 | 6785410 | 77165.6007
September | 168972.0998 | 266.1115 | 816.1982 | 0 | 0.0023 | 6028270 | 69881.3598
October | 160705.1065 | 250.1688 | 755.1192 | 0 | 0.0021 | 5576990 | 66166.8035
November | 147973.083 | 227.9952 | 678.2672 | 0 | 0.0019 | 5009250 | 60686.6595
December | 158418.4471 | 243.6121 | 722.6937 | 0 | 0.002 | 5337330 | 64922.2516
Annual Sum or Average | 1968120 | 3074.5791 | 9326.0349 | 0 | 0.026 | 68878700 | 811423.8471
Minimum of Months | 143790.3945 | 221.5104 | 658.8043 | 0 | 0.0018 | 4865510 | 58967.1941
Maximum of Months | 186388.4576 | 296.9973 | 925.3343 | 0 | 0.0026 | 6834520 | 77433.7841
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 618276000000 | 399978.793 | 27-JAN-09:09 | 58033.2 | 120867.849 | 35836.644 | 14541.586 | 69748.508 | 0 | 951.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 589671000000 | 405201.232 | 28-FEB-16:00 | 58033.2 | 120867.849 | 38209.311 | 450.224 | 132540.301 | 0 | 951.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 655145000000 | 442017.145 | 30-MAR-15:00 | 58033.2 | 120867.849 | 39316.235 | 124.192 | 154800.565 | 0 | 951.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 676154000000 | 435491.594 | 26-APR-15:00 | 58033.2 | 120867.849 | 39938.164 | 105.106 | 173033.664 | 0 | 951.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 720680000000 | 475614.923 | 19-MAY-15:00 | 58033.2 | 120867.849 | 41784.645 | 81.157 | 209330.834 | 0 | 951.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 776682000000 | 552188.666 | 08-JUN-15:00 | 58033.2 | 120867.849 | 46530.457 | 59.191 | 286962.145 | 0 | 951.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 828304000000 | 521594.037 | 19-JUL-16:00 | 58033.2 | 120867.849 | 46339.937 | 50.091 | 295351.952 | 0 | 951.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 822352000000 | 518348.884 | 01-AUG-16:00 | 58033.2 | 120867.849 | 46498.39 | 48.729 | 291949.709 | 0 | 951.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 730591000000 | 478452.82 | 12-SEP-16:00 | 58033.2 | 120867.849 | 44548.362 | 62.514 | 253989.888 | 0 | 951.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 675898000000 | 430513.154 | 24-OCT-13:00 | 58033.2 | 120867.849 | 40072.366 | 543.691 | 176193.449 | 0 | 951.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 607092000000 | 408568.694 | 13-NOV-13:00 | 58033.2 | 120867.849 | 38152.829 | 1812.948 | 150860.494 | 0 | 951.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 646853000000 | 403638.379 | 06-DEC-15:00 | 58033.2 | 120867.849 | 37471.879 | 4698.902 | 108289.769 | 0 | 951.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 8347700000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 589671000000 | 399978.793 |  | 58033.2 | 120867.849 | 35836.644 | 48.729 | 69748.508 | 0 | 951.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 828304000000 | 552188.666 |  | 58033.2 | 120867.849 | 46530.457 | 14541.586 | 295351.952 | 0 | 951.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 172886.95 | 53265.19 | 0 | 226152.13
Cost per Total Building Area ($/m2) | 45.45 | 14 | 0 | 59.45
Cost per Net Conditioned Building Area ($/m2) | 45.45 | 14 | 0 | 59.45

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 14024.66 | 3686.81 | 3686.81
Net Site Energy | 14024.66 | 3686.81 | 3686.81
Total Source Energy | 33025.13 | 8681.67 | 8681.67
Net Source Energy | 33025.13 | 8681.67 | 8681.67
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 389.67 | 5994.23 | 0 | 0 | 0 | 0
Cooling | 2982 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 879.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 31.84 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1067.53 | 0 | 0 | 0 | 0 | 0
Pumps | 30.99 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 427.44 | 0 | 0 | 0 | 0 | 159.01
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 47.07 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7794.98 | 6229.68 | 0 | 0 | 0 | 399.49
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 22.6 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 14 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 19.4 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 7.53 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 7.53 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 10.8 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 22.6 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 22.6 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 10.8 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 75.3 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 24.7 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 17.2 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 10.8 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 24.7 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 19.4 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 24.7 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 8.61 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 10.8 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 8.61 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 8.61 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 10.8 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 8.61 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 19.4 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 17.2 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 19.4 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 10.8 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 10.8 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 19.4 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 22.6 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 8.61 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 8.61 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 7.53 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 19.4 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 17.2 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 19.4 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 19.4 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 19.4 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 8.61 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 8.61 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 8.61 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 8.61 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 4.092 | 0.255 | 0.129 | No | 5F762C | 180 | S
4A8120 | WINDOW-NONRES-FIXED | 2.32 | 2.32 | 4.092 | 0.255 | 0.129 | No | 84FB73 | 0 | N
AAE778 | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 4.092 | 0.255 | 0.129 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | F629C1 | 0 | N
8128A9 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | F629C1 | 0 | N
9B1541 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 879583 | 180 | S
CF850A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 879583 | 180 | S
A6BA23 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | E326E4 | 90 | E
D10D28 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | E326E4 | 90 | E
38B811 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 1D96D7 | 90 | E
591336 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 1D96D7 | 90 | E
18748E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 6D2616 | 0 | N
1D94BE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 6D2616 | 0 | N
137A56 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.255 | 0.129 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 28B002 | 180 | S
44E54A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 28B002 | 180 | S
8D508E | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 28B002 | 180 | S
B2D381 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 28B002 | 180 | S
757D10 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 4.092 | 0.255 | 0.129 | No | EA6DC8 | 180 | S
24167A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 997723 | 180 | S
2C0938 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 997723 | 180 | S
E33BAE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | B40F89 | 270 | W
8600DD | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | CEC7BD | 180 | S
88E1FC | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 859BC1 | 0 | N
E8D997 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 859BC1 | 0 | N
F83F33 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.255 | 0.129 | No | 61E610 | 90 | E
B1F5EE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | D95F04 | 90 | E
F52F3D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 208CCF | 90 | E
80885D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 4.092 | 0.255 | 0.129 | No | AEF992 | 180 | S
2BE8DE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 1775A6 | 270 | W
513E2A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 54D065 | 180 | S
1AD478 | WINDOW-NONRES-FIXED | 3.72 | 3.72 | 4.092 | 0.255 | 0.129 | No | 97F00A | 180 | S
27F0AC | WINDOW-NONRES-FIXED | 5.95 | 5.95 | 4.092 | 0.255 | 0.129 | No | A497E9 | 180 | S
724114 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 88A75F | 180 | S
5635BC | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.255 | 0.129 | No | B4E619 | 90 | E
D538C4 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.255 | 0.129 | No | B4E619 | 90 | E
831C1D | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 4.092 | 0.255 | 0.129 | No | 9EC269 | 0 | N
9BB95F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | B316F7 | 0 | N
C0778D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | B316F7 | 0 | N
2EF63B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 9621FD | 0 | N
7D2D69 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 9621FD | 0 | N
C417C0 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 4B1439 | 90 | E
D23C8B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 4B1439 | 90 | E
EB042B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 4B1439 | 90 | E
E55A57 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.255 | 0.129 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 4.092 | 0.255 | 0.129 | No | 4ABC66 | 180 | S
93D018 | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 4.092 | 0.255 | 0.129 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | 4B55FA | 90 | E
15B02B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 9C3A6A | 0 | N
820282 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 68A2D7 | 0 | N
A2790A | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 4.092 | 0.255 | 0.129 | No | CE3FEF | 0 | N
79FCEE | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.255 | 0.129 | No | CE618F | 90 | E
EDE617 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.255 | 0.129 | No | CE618F | 90 | E
29FA28 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 5ADC59 | 0 | N
944FCE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 5ADC59 | 0 | N
C41399 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.255 | 0.129 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.255 | 0.129 | No | C1BC97 | 180 | S
3DB407 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.255 | 0.129 | No | C1BC97 | 180 | S
5031C8 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.255 | 0.129 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.255 | 0.129 | No | C1BC97 | 180 | S
95BA33 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.255 | 0.129 | No | D22917 | 90 | E
F27282 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.255 | 0.129 | No | D22917 | 90 | E
9DF7DE | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.255 | 0.129 | No | 38B339 | 270 | W
D0BE44 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.255 | 0.129 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.255 | 0.129 | No | 38B339 | 270 | W
B0FB49 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 4.092 | 0.255 | 0.129 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.255 | 0.129 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.255 | 0.129 | No | 8DA7DB | 180 | S
44F571 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 4.092 | 0.255 | 0.129 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 4.092 | 0.255 | 0.129 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 4.092 | 0.255 | 0.129 | No | BE5F2F | 270 | W
3833A2 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | C86329 | 90 | E
6BD844 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | C86329 | 90 | E
86D536 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | C86329 | 90 | E
BAF71D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.255 | 0.129 | No | C86329 | 90 | E
142781 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.255 | 0.129 | No | 88E360 | 0 | N
9BC521 | WINDOW-NONRES-FIXED | 5.71 | 5.71 | 4.092 | 0.255 | 0.129 | No | 88E360 | 0 | N
2111A1 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 4.092 | 0.255 | 0.129 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.255 | 0.129 | No | 2E2D0C | 0 | N
E74902 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.255 | 0.129 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-NONRES-FIXED | 1.11 | 1.11 | 4.092 | 0.255 | 0.129 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 4.09 | 0.255 | 0.129
North Total or Average |  |  | 97.22 | 4.09 | 0.255 | 0.129
Non-North Total or Average |  |  | 211.08 | 4.09 | 0.255 | 0.129
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 176994.27 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 415704.99 | 290531.01 | 125173.98 | 0.7 | 2.79
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 366570.09 | 267582.6 | 98987.49 | 0.73 | 2.87
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2246.73 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 205.23 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 13020.07 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1788.97 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2314.61 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1239.8 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1552.92 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2404.66 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148704.5 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 574.87 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 594.34 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1109.86 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 13600.06 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 926.16 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1194.56 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 11096.86 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1929.69 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 5333.77 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2454.15 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 600.7 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 70133.24 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1194.56 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 2057.18 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2916.93 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1929.69 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 199.41 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 4114.66 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1194.56 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 4443.96 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 42468.11 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 42998.88 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35936.64 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 2162.97 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2051.23 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2705.49 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4486.27 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1194.56 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9457.02 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7457.4 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 521.62 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 14203.6 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1707.94 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 357.27 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2787.33 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1238.8 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 3981.89 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 9680.33 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2718.78 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 1269.64 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 12710.65 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2808 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3987.03 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 158.65 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 4067.9 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 2202.18 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3668.37 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 302.88 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5824.48 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3067.95 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4104.48 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 670.37 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2995.82 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2087.26 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4244.39 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2521.22 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2148.03 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 373.9 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 373.9 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 373.9 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 414.19 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 414.19 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 412.64 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 656.1 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 489.71 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 937.53 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1120.91 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 6078.31 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 867.46 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 7130.33 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2339.32 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1258.08 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1325.94 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 91.77 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 191.99 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 229.44 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 736.84 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6791.61 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1672.29 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 361.75 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 4625.82 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 218.67 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 926.9 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 557.45 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 696.34 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 853.88 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5888.11 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1286.21 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3797.33 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 892.14 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 24039.15 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2709.14 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 423.14 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 11276 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3793.32 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 562.72 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 338.79 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 266.86 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2831.16 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 15394.92 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 11661.95 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 598.2 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6457.32 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2058.88 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2385.49 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2770.22 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1570.68 | 1
AHU-1_HEATC | Coil:Heating:Water | 14053.91 | -
AHU-2_HEATC | Coil:Heating:Water | 50790.79 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.3 | 30802.3 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.01 | 30312.37 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 974.61 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 155383.5151 | 268.7174 | 626.5458 | 0 | 0.0023 | 1114220 | 65569.72
February | 139530.3799 | 241.4078 | 563.1444 | 0 | 0.0021 | 1001470 | 58889.7562
March | 150413.5243 | 260.7498 | 609.5814 | 0 | 0.0023 | 1084060 | 63530.399
April | 142963.459 | 248.1219 | 580.7964 | 0 | 0.0022 | 1032870 | 60410.2278
May | 152767.5458 | 267.7959 | 633.6575 | 0 | 0.0024 | 1126910 | 64798.5219
June | 158176.9341 | 280.5613 | 672.188 | 0 | 0.0025 | 1195470 | 67396.1783
July | 167749.5048 | 299.6532 | 723.2247 | 0 | 0.0027 | 1286260 | 71669.9925
August | 170049.005 | 303.8132 | 733.3954 | 0 | 0.0027 | 1304350 | 72657.2787
September | 158132.9428 | 279.8041 | 668.6715 | 0 | 0.0025 | 1189210 | 67314.7073
October | 146822.4199 | 254.9316 | 597.0234 | 0 | 0.0022 | 1061730 | 62051.2163
November | 143354.9533 | 247.7803 | 577.3814 | 0 | 0.0022 | 1026790 | 60481.3556
December | 153007.8041 | 264.4461 | 616.1684 | 0 | 0.0023 | 1095760 | 64552.1695
Annual Sum or Average | 1838350 | 3217.7825 | 7601.7784 | 0 | 0.0284 | 13519100 | 779321.5231
Minimum of Months | 139530.3799 | 241.4078 | 563.1444 | 0 | 0.0021 | 1001470 | 58889.7562
Maximum of Months | 170049.005 | 303.8132 | 733.3954 | 0 | 0.0027 | 1304350 | 72657.2787
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 642450000000 | 365868.433 | 30-JAN-07:10 | 58033.2 | 96785.431 | 33972.815 | 83255.347 | 28066.769 | 2025 | 982.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 577439000000 | 374560.359 | 02-FEB-07:10 | 58033.2 | 96785.431 | 34073.329 | 76341.254 | 17220.152 | 2025 | 982.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 625059000000 | 378400.266 | 22-MAR-16:00 | 58033.2 | 120867.849 | 36681.58 | 205.983 | 110765.346 | 0 | 982.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 595545000000 | 384576.253 | 14-APR-16:00 | 58033.2 | 120867.849 | 37155.047 | 62.444 | 167475.037 | 0 | 982.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 649765000000 | 416967.004 | 31-MAY-16:00 | 58033.2 | 120867.849 | 37657.004 | 36.703 | 199389.573 | 0 | 982.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 689295000000 | 430062.501 | 19-JUN-14:00 | 58033.2 | 120867.849 | 38142.933 | 32.058 | 212003.787 | 0 | 982.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 741644000000 | 456284.807 | 03-JUL-15:00 | 58033.2 | 120867.849 | 40432.079 | 6.613 | 235962.391 | 0 | 982.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 752074000000 | 436937.445 | 17-AUG-13:00 | 58033.2 | 120867.849 | 38617.73 | 48.03 | 218387.96 | 0 | 982.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 685685000000 | 415810.539 | 11-SEP-13:00 | 58033.2 | 120867.849 | 37048.648 | 71.342 | 198806.825 | 0 | 982.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 612184000000 | 401356.778 | 12-OCT-15:00 | 58033.2 | 120867.849 | 37248.185 | 93.343 | 184131.526 | 0 | 982.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 592036000000 | 355944.544 | 03-NOV-13:00 | 58033.2 | 120867.849 | 34768.751 | 5781.396 | 75715.611 | 0 | 982.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 631808000000 | 382774.901 | 18-DEC-07:10 | 58033.2 | 96785.431 | 33972.807 | 89408.956 | 22551.163 | 2025 | 982.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 7794980000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 577439000000 | 355944.544 |  | 58033.2 | 96785.431 | 33972.807 | 6.613 | 17220.152 | 0 | 982.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 752074000000 | 456284.807 |  | 58033.2 | 120867.849 | 40432.079 | 89408.956 | 235962.391 | 2025 | 982.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 213815.38 | 67942.2 | 0 | 281757.59
Cost per Total Building Area ($/m2) | 56.21 | 17.86 | 0 | 74.07
Cost per Net Conditioned Building Area ($/m2) | 56.21 | 17.86 | 0 | 74.07

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 13598.96 | 3574.9 | 3574.9
Net Site Energy | 13598.96 | 3574.9 | 3574.9
Total Source Energy | 29153.37 | 7663.86 | 7663.86
Net Source Energy | 29153.37 | 7663.86 | 7663.86
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 344.86 | 6223.6 | 0 | 0 | 0 | 0
Cooling | 2504.1 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 879.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 31.82 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1069.23 | 0 | 0 | 0 | 0 | 0
Pumps | 29.08 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 296.32 | 0 | 0 | 0 | 0 | 110.23
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 46.03 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7140.94 | 6458.01 | 0 | 0 | 0 | 350.71
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 22.6 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 14 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 19.4 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 7.53 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 7.53 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 10.8 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 22.6 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 22.6 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 10.8 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 75.3 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 24.7 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 17.2 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 10.8 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 24.7 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 19.4 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 24.7 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 8.61 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 10.8 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 8.61 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 8.61 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 10.8 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 8.61 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 19.4 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 17.2 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 19.4 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 10.8 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 10.8 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 19.4 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 22.6 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 8.61 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 8.61 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 7.53 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 19.4 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 17.2 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 19.4 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 19.4 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 19.4 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 8.61 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 8.61 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 8.61 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 8.61 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.249 | 1.536 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 5.835 | 0.44 | 0.272 | No | 5F762C | 180 | S
4A8120 | WINDOW-NONRES-FIXED | 2.32 | 2.32 | 5.835 | 0.44 | 0.272 | No | 84FB73 | 0 | N
AAE778 | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 5.835 | 0.44 | 0.272 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | F629C1 | 0 | N
8128A9 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | F629C1 | 0 | N
9B1541 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 879583 | 180 | S
CF850A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 879583 | 180 | S
A6BA23 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | E326E4 | 90 | E
D10D28 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | E326E4 | 90 | E
38B811 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 1D96D7 | 90 | E
591336 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 1D96D7 | 90 | E
18748E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 6D2616 | 0 | N
1D94BE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 6D2616 | 0 | N
137A56 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.44 | 0.272 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 28B002 | 180 | S
44E54A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 28B002 | 180 | S
8D508E | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 28B002 | 180 | S
B2D381 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 28B002 | 180 | S
757D10 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 5.835 | 0.44 | 0.272 | No | EA6DC8 | 180 | S
24167A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 997723 | 180 | S
2C0938 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 997723 | 180 | S
E33BAE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | B40F89 | 270 | W
8600DD | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | CEC7BD | 180 | S
88E1FC | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 859BC1 | 0 | N
E8D997 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 859BC1 | 0 | N
F83F33 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.44 | 0.272 | No | 61E610 | 90 | E
B1F5EE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | D95F04 | 90 | E
F52F3D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 208CCF | 90 | E
80885D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.44 | 0.272 | No | AEF992 | 180 | S
2BE8DE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 1775A6 | 270 | W
513E2A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 54D065 | 180 | S
1AD478 | WINDOW-NONRES-FIXED | 3.72 | 3.72 | 5.835 | 0.44 | 0.272 | No | 97F00A | 180 | S
27F0AC | WINDOW-NONRES-FIXED | 5.95 | 5.95 | 5.835 | 0.44 | 0.272 | No | A497E9 | 180 | S
724114 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 88A75F | 180 | S
5635BC | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.44 | 0.272 | No | B4E619 | 90 | E
D538C4 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.44 | 0.272 | No | B4E619 | 90 | E
831C1D | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 5.835 | 0.44 | 0.272 | No | 9EC269 | 0 | N
9BB95F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | B316F7 | 0 | N
C0778D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | B316F7 | 0 | N
2EF63B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 9621FD | 0 | N
7D2D69 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 9621FD | 0 | N
C417C0 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 4B1439 | 90 | E
D23C8B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 4B1439 | 90 | E
EB042B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 4B1439 | 90 | E
E55A57 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.44 | 0.272 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.44 | 0.272 | No | 4ABC66 | 180 | S
93D018 | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.44 | 0.272 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | 4B55FA | 90 | E
15B02B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 9C3A6A | 0 | N
820282 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 68A2D7 | 0 | N
A2790A | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 5.835 | 0.44 | 0.272 | No | CE3FEF | 0 | N
79FCEE | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.44 | 0.272 | No | CE618F | 90 | E
EDE617 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.44 | 0.272 | No | CE618F | 90 | E
29FA28 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 5ADC59 | 0 | N
944FCE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 5ADC59 | 0 | N
C41399 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.44 | 0.272 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.44 | 0.272 | No | C1BC97 | 180 | S
3DB407 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.44 | 0.272 | No | C1BC97 | 180 | S
5031C8 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.44 | 0.272 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.44 | 0.272 | No | C1BC97 | 180 | S
95BA33 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.44 | 0.272 | No | D22917 | 90 | E
F27282 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.44 | 0.272 | No | D22917 | 90 | E
9DF7DE | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.44 | 0.272 | No | 38B339 | 270 | W
D0BE44 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.44 | 0.272 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.44 | 0.272 | No | 38B339 | 270 | W
B0FB49 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.44 | 0.272 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.44 | 0.272 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.44 | 0.272 | No | 8DA7DB | 180 | S
44F571 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.44 | 0.272 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.44 | 0.272 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.44 | 0.272 | No | BE5F2F | 270 | W
3833A2 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | C86329 | 90 | E
6BD844 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | C86329 | 90 | E
86D536 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | C86329 | 90 | E
BAF71D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.44 | 0.272 | No | C86329 | 90 | E
142781 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.44 | 0.272 | No | 88E360 | 0 | N
9BC521 | WINDOW-NONRES-FIXED | 5.71 | 5.71 | 5.835 | 0.44 | 0.272 | No | 88E360 | 0 | N
2111A1 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 5.835 | 0.44 | 0.272 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.44 | 0.272 | No | 2E2D0C | 0 | N
E74902 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.44 | 0.272 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-NONRES-FIXED | 1.11 | 1.11 | 5.835 | 0.44 | 0.272 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 5.83 | 0.44 | 0.272
North Total or Average |  |  | 97.22 | 5.83 | 0.44 | 0.272
Non-North Total or Average |  |  | 211.08 | 5.83 | 0.44 | 0.272
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 166014.68 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 373660.7 | 271671.4 | 101989.3 | 0.73 | 2.86
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 327063.9 | 255232.85 | 71831.05 | 0.78 | 3.01
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2841.22 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 208.14 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 14988.47 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1791.22 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2317.58 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1242.31 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1034.3 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2479.92 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 146879.22 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 578.56 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 602.31 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1112.19 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 16851.71 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 938.82 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1235.4 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 10538.16 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1956.01 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 5340.31 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2411.08 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 608.89 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 70136.27 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1235.4 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1380.64 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2920.13 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1956.01 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 202.23 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 4119.23 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1235.4 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 4452.26 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 45172.71 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 45938.57 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35946.55 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 2164.76 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2079.24 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2861.52 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4639.64 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1235.4 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9780.33 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 8232.78 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 528.74 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 16572.73 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1887.77 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 362.06 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2882.62 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1281.15 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 4118.02 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 11030.2 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3459.11 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 1293.6 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 10923.62 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 3548.8 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2957.67 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 160.88 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 4252.87 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 2195.62 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4222.02 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 303.84 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 7405.12 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3440.99 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4671.52 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 887.59 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3504.99 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1862.24 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4016.88 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2257.8 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2036.96 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 433.01 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 433.01 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 433.01 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 330.72 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 330.44 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 328.86 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 515.1 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 489.69 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 937.53 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1120.91 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 7252.48 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 801.66 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 8287.29 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3421.16 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1258.04 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1325.88 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 92.09 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 192.55 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 230.12 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 930.37 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6553.89 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1619.2 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 425.6 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 4625.71 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 234.96 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 740.62 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 597.32 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 644.41 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 896.67 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5960.9 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1330.28 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 4440.78 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1002.05 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 24512.78 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2998.13 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 523.6 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 13833.97 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3983.25 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 582 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 340.53 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 264.97 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2982.8 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 17884.57 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 13632.47 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 669.71 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 7749.96 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2286.17 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 3562.66 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2784.59 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2359.94 | 1
AHU-1_HEATC | Coil:Heating:Water | 0 | -
AHU-2_HEATC | Coil:Heating:Water | 18694.69 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.18 | 30598.02 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.78 | 31606.12 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 914.15 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 78954.7266 | 69.1207 | 458.4411 | 0 | 0.0003 | 2765240 | 28725.0496
February | 67796.5237 | 59.4245 | 380.7194 | 0 | 0.0002 | 2296360 | 24626.0508
March | 77683.7111 | 68.0127 | 450.207 | 0 | 0.0003 | 2715570 | 28260.0271
April | 74757.9725 | 65.4566 | 432.2833 | 0 | 0.0003 | 2607450 | 27192.7394
May | 80608.9235 | 70.4853 | 482.9878 | 0 | 0.0003 | 2913380 | 29372.4608
June | 81126.487 | 70.856 | 500.7369 | 0 | 0.0003 | 3020520 | 29605.7421
July | 84178.4497 | 73.4642 | 529.8467 | 0 | 0.0003 | 3196160 | 30750.8445
August | 86091.7373 | 75.0545 | 556.1126 | 0 | 0.0003 | 3354670 | 31493.1728
September | 81547.6542 | 71.1491 | 516.7161 | 0 | 0.0003 | 3116970 | 29800.2608
October | 83724.4223 | 73.0976 | 521.6767 | 0 | 0.0003 | 3146850 | 30568.7784
November | 78189.8821 | 68.3784 | 467.0078 | 0 | 0.0003 | 2816980 | 28486.4722
December | 80707.4969 | 70.6082 | 477.0193 | 0 | 0.0003 | 2877340 | 29388.3676
Annual Sum or Average | 955367.9869 | 835.1077 | 5773.7548 | 0 | 0.0033 | 34827500 | 348269.9661
Minimum of Months | 67796.5237 | 59.4245 | 380.7194 | 0 | 0.0002 | 2296360 | 24626.0508
Maximum of Months | 86091.7373 | 75.0545 | 556.1126 | 0 | 0.0003 | 3354670 | 31493.1728
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 566977000000 | 398372.132 | 25-JAN-09:09 | 58033.2 | 120867.849 | 34154.205 | 16241.41 | 68153.251 | 0 | 922.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 470841000000 | 386844.537 | 10-FEB-08:50 | 58033.2 | 108826.64 | 34189.242 | 17986.013 | 66887.225 | 0 | 922.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 556793000000 | 396677.887 | 30-MAR-08:09 | 58033.2 | 120867.849 | 34164.283 | 14638.91 | 68051.428 | 0 | 922.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 534625000000 | 425058.42 | 11-APR-15:00 | 58033.2 | 120867.849 | 38153.592 | 15.035 | 141728.037 | 0 | 922.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 597352000000 | 372722.994 | 30-MAY-08:00 | 58033.2 | 120867.849 | 34700.43 | 3693.617 | 154505.68 | 0 | 922.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 619319000000 | 372088.841 | 28-JUN-12:00 | 58033.2 | 120867.849 | 36889.679 | 39.163 | 155336.734 | 0 | 922.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 655333000000 | 374015.39 | 20-JUL-14:00 | 58033.2 | 120867.849 | 37794.666 | 0 | 156397.458 | 0 | 922.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 687834000000 | 394031.791 | 08-AUG-14:00 | 58033.2 | 120867.849 | 39426.876 | 0 | 174781.65 | 0 | 922.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 639096000000 | 393901.626 | 25-SEP-14:00 | 58033.2 | 120867.849 | 40251.684 | 13.797 | 173812.879 | 0 | 922.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 645223000000 | 394671.729 | 19-OCT-10:00 | 58033.2 | 120867.849 | 37241.309 | 268.106 | 145019.15 | 0 | 922.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 577586000000 | 393388.006 | 29-NOV-09:00 | 58033.2 | 120867.849 | 34383.63 | 10156.513 | 69024.596 | 0 | 922.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 589963000000 | 393164.19 | 18-DEC-08:20 | 58033.2 | 108826.64 | 33978.727 | 29415.417 | 61987.989 | 0 | 922.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 7140940000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 470841000000 | 372088.841 |  | 58033.2 | 108826.64 | 33978.727 | 0 | 61987.989 | 0 | 922.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 687834000000 | 425058.42 |  | 58033.2 | 120867.849 | 40251.684 | 29415.417 | 174781.65 | 0 | 922.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 242196.03 | 54193.78 | 0 | 296389.81
Cost per Total Building Area ($/m2) | 63.67 | 14.25 | 0 | 77.92
Cost per Net Conditioned Building Area ($/m2) | 63.67 | 14.25 | 0 | 77.92

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 14186.69 | 3729.41 | 3729.41
Net Site Energy | 14186.69 | 3729.41 | 3729.41
Total Source Energy | 35978.7 | 9458.1 | 9458.1
Net Source Energy | 35978.7 | 9458.1 | 9458.1
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 303.28 | 5711.77 | 0 | 0 | 0 | 0
Cooling | 2230.28 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 879.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 31.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1116.15 | 0 | 0 | 0 | 0 | 0
Pumps | 29.05 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 1668.11 | 0 | 0 | 0 | 0 | 620.54
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 42.35 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8244.2 | 5942.49 | 0 | 0 | 0 | 861.02
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 22.6 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 14 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 19.4 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 7.53 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 7.53 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 10.8 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 22.6 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 22.6 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 10.8 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 75.3 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 24.7 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 17.2 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 10.8 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 24.7 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 19.4 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 24.7 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 8.61 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 10.8 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 8.61 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 8.61 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 10.8 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 8.61 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 19.4 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 17.2 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 19.4 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 10.8 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 10.8 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 19.4 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 22.6 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 8.61 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 8.61 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 7.53 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 19.4 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 17.2 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 19.4 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 19.4 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 19.4 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 8.61 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 8.61 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 8.61 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 8.61 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.908 | 1.051 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 5.835 | 0.251 | 0.11 | No | 5F762C | 180 | S
4A8120 | WINDOW-NONRES-FIXED | 2.32 | 2.32 | 5.835 | 0.251 | 0.11 | No | 84FB73 | 0 | N
AAE778 | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 5.835 | 0.251 | 0.11 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | F629C1 | 0 | N
8128A9 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | F629C1 | 0 | N
9B1541 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 879583 | 180 | S
CF850A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 879583 | 180 | S
A6BA23 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | E326E4 | 90 | E
D10D28 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | E326E4 | 90 | E
38B811 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
591336 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1D96D7 | 90 | E
18748E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 6D2616 | 0 | N
1D94BE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 6D2616 | 0 | N
137A56 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
44E54A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
8D508E | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
B2D381 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 28B002 | 180 | S
757D10 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 5.835 | 0.251 | 0.11 | No | EA6DC8 | 180 | S
24167A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 997723 | 180 | S
2C0938 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 997723 | 180 | S
E33BAE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | B40F89 | 270 | W
8600DD | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | CEC7BD | 180 | S
88E1FC | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
E8D997 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 859BC1 | 0 | N
F83F33 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | 61E610 | 90 | E
B1F5EE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | D95F04 | 90 | E
F52F3D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 208CCF | 90 | E
80885D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | AEF992 | 180 | S
2BE8DE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
513E2A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 54D065 | 180 | S
1AD478 | WINDOW-NONRES-FIXED | 3.72 | 3.72 | 5.835 | 0.251 | 0.11 | No | 97F00A | 180 | S
27F0AC | WINDOW-NONRES-FIXED | 5.95 | 5.95 | 5.835 | 0.251 | 0.11 | No | A497E9 | 180 | S
724114 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 88A75F | 180 | S
5635BC | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | B4E619 | 90 | E
D538C4 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | B4E619 | 90 | E
831C1D | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 5.835 | 0.251 | 0.11 | No | 9EC269 | 0 | N
9BB95F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | B316F7 | 0 | N
C0778D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | B316F7 | 0 | N
2EF63B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9621FD | 0 | N
7D2D69 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9621FD | 0 | N
C417C0 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
D23C8B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
EB042B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B1439 | 90 | E
E55A57 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | 4ABC66 | 180 | S
93D018 | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 5.835 | 0.251 | 0.11 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | 4B55FA | 90 | E
15B02B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9C3A6A | 0 | N
820282 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 68A2D7 | 0 | N
A2790A | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 5.835 | 0.251 | 0.11 | No | CE3FEF | 0 | N
79FCEE | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | CE618F | 90 | E
EDE617 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | CE618F | 90 | E
29FA28 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
944FCE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
C41399 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 5.835 | 0.251 | 0.11 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
3DB407 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
5031C8 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | C1BC97 | 180 | S
95BA33 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | D22917 | 90 | E
F27282 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | D22917 | 90 | E
9DF7DE | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
D0BE44 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 5.835 | 0.251 | 0.11 | No | 38B339 | 270 | W
B0FB49 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 8DA7DB | 180 | S
44F571 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 5.835 | 0.251 | 0.11 | No | BE5F2F | 270 | W
3833A2 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
6BD844 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
86D536 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
BAF71D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 5.835 | 0.251 | 0.11 | No | C86329 | 90 | E
142781 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 88E360 | 0 | N
9BC521 | WINDOW-NONRES-FIXED | 5.71 | 5.71 | 5.835 | 0.251 | 0.11 | No | 88E360 | 0 | N
2111A1 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 5.835 | 0.251 | 0.11 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 2E2D0C | 0 | N
E74902 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 5.835 | 0.251 | 0.11 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-NONRES-FIXED | 1.11 | 1.11 | 5.835 | 0.251 | 0.11 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 97.22 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 211.08 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 165834.71 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 379511.34 | 278403.88 | 101107.46 | 0.73 | 2.88
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 331552.31 | 259178.75 | 72373.56 | 0.78 | 3.01
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2557.04 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 107.44 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 13756.06 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1633.27 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2110.66 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1040.35 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1379 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2395.42 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148578.06 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 459.5 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 326.2 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 929.72 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 14523.91 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 530.27 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1145.72 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 10967.52 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1101.43 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 4867.94 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2355.76 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 335.54 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 69597.1 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1145.72 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1737.53 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2680.49 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1101.43 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 104.12 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3778.23 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1145.72 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3788.73 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 43493.75 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 42923.72 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35069.71 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 2030.86 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1170.82 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2650.09 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4302.82 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1145.72 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9070.31 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7456.02 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 291.73 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 15504.1 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1817.96 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 195.81 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2673.35 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1188.15 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 3819.07 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 10881.02 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2217.29 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 756.18 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 11627.63 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2869.92 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3614.76 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 82.11 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 3886.99 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 2418.3 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4225.16 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 301.68 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 6906.29 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3360.03 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4520.89 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 814.84 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3195.76 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2332.32 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4499.42 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2824.43 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2278.56 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 402.92 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 402.92 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 402.92 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 414.51 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 414.51 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 413.09 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 700.74 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 489.73 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 937.54 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1120.92 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 6528.2 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 858.04 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 8064.7 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2933.71 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1258.06 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1325.92 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 91.53 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 191.42 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 228.76 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 821.26 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 7099.52 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1661.76 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 433.56 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 4625.88 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 224.51 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 919.21 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 514.52 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 755.35 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 757.05 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5615.8 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1233.51 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3955.48 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 984.28 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 22181.42 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2763.88 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 473.73 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 11734.63 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3334.41 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 539.66 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 363.82 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 283.38 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2461.32 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 14914.24 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 11599.75 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 648.97 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6830.39 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2317.25 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2850.93 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 3363.35 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1838.44 | 1
AHU-1_HEATC | Coil:Heating:Water | 0 | -
AHU-2_HEATC | Coil:Heating:Water | 36739.86 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.87 | 31762.73 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 19.11 | 32162.47 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 913.16 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 176589.8381 | 268.0655 | 1013.6365 | 0 | 0.002 | 5054530 | 72319.5974
February | 154272.4374 | 234.0791 | 884.5147 | 0 | 0.0017 | 4410650 | 63168.5934
March | 176803.7312 | 269.3965 | 1024.3225 | 0 | 0.002 | 5107860 | 72511.7837
April | 175541.072 | 269.2672 | 1033.8754 | 0 | 0.002 | 5155570 | 72180.4631
May | 185286.2955 | 285.2737 | 1101.2166 | 0 | 0.0021 | 5491420 | 76297.5623
June | 191286.0998 | 297.0383 | 1160.6281 | 0 | 0.0022 | 5787790 | 79030.832
July | 192311.473 | 298.3083 | 1163.8207 | 0 | 0.0022 | 5803690 | 79420.9763
August | 191219.4475 | 296.9383 | 1160.2562 | 0 | 0.0022 | 5785930 | 79003.6533
September | 177574.0429 | 273.6595 | 1057.8226 | 0 | 0.002 | 5275040 | 73148.8029
October | 172961.685 | 264.3483 | 1009.6392 | 0 | 0.0019 | 5034670 | 71019.8348
November | 166944.9278 | 253.8531 | 962.3034 | 0 | 0.0019 | 4798570 | 68414.2319
December | 178200.6149 | 270.9161 | 1026.6927 | 0 | 0.002 | 5119650 | 73021.3996
Annual Sum or Average | 2138990 | 3281.144 | 12598.7287 | 0 | 0.0242 | 62825400 | 879537.7308
Minimum of Months | 154272.4374 | 234.0791 | 884.5147 | 0 | 0.0017 | 4410650 | 63168.5934
Maximum of Months | 192311.473 | 298.3083 | 1163.8207 | 0 | 0.0022 | 5803690 | 79420.9763
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 663276000000 | 393094.421 | 17-JAN-13:00 | 58033.2 | 120867.849 | 35951.698 | 9735.477 | 67584.971 | 0 | 921.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 578784000000 | 390753.534 | 07-FEB-11:00 | 58033.2 | 120867.849 | 35916.129 | 7506.683 | 67508.446 | 0 | 921.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 670274000000 | 388180.648 | 30-MAR-09:39 | 58033.2 | 120867.849 | 35758.533 | 5440.049 | 67159.791 | 0 | 921.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 676534000000 | 390957.95 | 21-APR-15:30 | 58033.2 | 120867.849 | 40173.499 | 76.803 | 161555.012 | 0 | 921.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 720606000000 | 472660.446 | 11-MAY-15:00 | 58033.2 | 120867.849 | 40293.318 | 67.133 | 171819.434 | 0 | 921.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 759497000000 | 505192.34 | 27-JUN-15:00 | 58033.2 | 120867.849 | 46113.58 | 39.935 | 246279.368 | 0 | 921.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 761584000000 | 482369.702 | 24-JUL-15:00 | 58033.2 | 120867.849 | 44389.983 | 59.999 | 235493.805 | 0 | 921.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 759253000000 | 459945.118 | 04-AUG-15:30 | 58033.2 | 120867.849 | 44708.467 | 49.851 | 235364.525 | 0 | 921.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 692212000000 | 458567.841 | 21-SEP-14:00 | 58033.2 | 120867.849 | 42420.078 | 80.334 | 190144.982 | 0 | 921.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 660670000000 | 415495.714 | 03-OCT-15:00 | 58033.2 | 120867.849 | 40021.04 | 85.747 | 159792.32 | 0 | 921.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 629688000000 | 392360.467 | 13-NOV-11:09 | 58033.2 | 120867.849 | 35287.234 | 10661.771 | 66589.188 | 0 | 921.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 671821000000 | 391383.752 | 04-DEC-11:39 | 58033.2 | 120867.849 | 35389.61 | 14303.022 | 61868.845 | 0 | 921.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 8244200000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 578784000000 | 388180.648 |  | 58033.2 | 120867.849 | 35287.234 | 39.935 | 61868.845 | 0 | 921.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 761584000000 | 505192.34 |  | 58033.2 | 120867.849 | 46113.58 | 14303.022 | 246279.368 | 0 | 921.226 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 204363.71 | 48737.47 | 0 | 253101.17
Cost per Total Building Area ($/m2) | 53.72 | 12.81 | 0 | 66.54
Cost per Net Conditioned Building Area ($/m2) | 53.72 | 12.81 | 0 | 66.54

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 11749.68 | 3088.76 | 3088.76
Net Site Energy | 11749.68 | 3088.76 | 3088.76
Total Source Energy | 24176.61 | 6355.56 | 6355.56
Net Source Energy | 24176.61 | 6355.56 | 6355.56
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 391.93 | 5846.19 | 0 | 0 | 0 | 0
Cooling | 1175.51 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 879.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 31.83 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 979.26 | 0 | 0 | 0 | 0 | 0
Pumps | 28.38 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 192.05 | 0 | 0 | 0 | 0 | 71.44
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 50.63 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5664.49 | 6085.19 | 0 | 0 | 0 | 311.92
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 22.6 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 14 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 19.4 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 7.53 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 7.53 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 10.8 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 22.6 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 22.6 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 10.8 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 75.3 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 24.7 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 17.2 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 10.8 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 24.7 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 19.4 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 24.7 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 8.61 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 10.8 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 8.61 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 8.61 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 10.8 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 8.61 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 19.4 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 17.2 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 19.4 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 10.8 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 10.8 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 19.4 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 22.6 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 8.61 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 8.61 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 7.53 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 19.4 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 17.2 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 19.4 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 19.4 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 19.4 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 8.61 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 8.61 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 8.61 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 8.61 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.738 | 0.83 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 4.092 | 0.392 | 0.253 | No | 5F762C | 180 | S
4A8120 | WINDOW-NONRES-FIXED | 2.32 | 2.32 | 4.092 | 0.392 | 0.253 | No | 84FB73 | 0 | N
AAE778 | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 4.092 | 0.392 | 0.253 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | F629C1 | 0 | N
8128A9 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | F629C1 | 0 | N
9B1541 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 879583 | 180 | S
CF850A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 879583 | 180 | S
A6BA23 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | E326E4 | 90 | E
D10D28 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | E326E4 | 90 | E
38B811 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 1D96D7 | 90 | E
591336 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 1D96D7 | 90 | E
18748E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 6D2616 | 0 | N
1D94BE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 6D2616 | 0 | N
137A56 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.392 | 0.253 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 28B002 | 180 | S
44E54A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 28B002 | 180 | S
8D508E | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 28B002 | 180 | S
B2D381 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 28B002 | 180 | S
757D10 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 4.092 | 0.392 | 0.253 | No | EA6DC8 | 180 | S
24167A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 997723 | 180 | S
2C0938 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 997723 | 180 | S
E33BAE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | B40F89 | 270 | W
8600DD | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | CEC7BD | 180 | S
88E1FC | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 859BC1 | 0 | N
E8D997 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 859BC1 | 0 | N
F83F33 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.392 | 0.253 | No | 61E610 | 90 | E
B1F5EE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | D95F04 | 90 | E
F52F3D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 208CCF | 90 | E
80885D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 4.092 | 0.392 | 0.253 | No | AEF992 | 180 | S
2BE8DE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 1775A6 | 270 | W
513E2A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 54D065 | 180 | S
1AD478 | WINDOW-NONRES-FIXED | 3.72 | 3.72 | 4.092 | 0.392 | 0.253 | No | 97F00A | 180 | S
27F0AC | WINDOW-NONRES-FIXED | 5.95 | 5.95 | 4.092 | 0.392 | 0.253 | No | A497E9 | 180 | S
724114 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 88A75F | 180 | S
5635BC | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.392 | 0.253 | No | B4E619 | 90 | E
D538C4 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.392 | 0.253 | No | B4E619 | 90 | E
831C1D | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 4.092 | 0.392 | 0.253 | No | 9EC269 | 0 | N
9BB95F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | B316F7 | 0 | N
C0778D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | B316F7 | 0 | N
2EF63B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 9621FD | 0 | N
7D2D69 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 9621FD | 0 | N
C417C0 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 4B1439 | 90 | E
D23C8B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 4B1439 | 90 | E
EB042B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 4B1439 | 90 | E
E55A57 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.392 | 0.253 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 4.092 | 0.392 | 0.253 | No | 4ABC66 | 180 | S
93D018 | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 4.092 | 0.392 | 0.253 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 4B55FA | 90 | E
15B02B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 9C3A6A | 0 | N
820282 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 68A2D7 | 0 | N
A2790A | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 4.092 | 0.392 | 0.253 | No | CE3FEF | 0 | N
79FCEE | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.392 | 0.253 | No | CE618F | 90 | E
EDE617 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.392 | 0.253 | No | CE618F | 90 | E
29FA28 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 5ADC59 | 0 | N
944FCE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 5ADC59 | 0 | N
C41399 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.392 | 0.253 | No | C1BC97 | 180 | S
3DB407 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.392 | 0.253 | No | C1BC97 | 180 | S
5031C8 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.392 | 0.253 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.392 | 0.253 | No | C1BC97 | 180 | S
95BA33 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.392 | 0.253 | No | D22917 | 90 | E
F27282 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.392 | 0.253 | No | D22917 | 90 | E
9DF7DE | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.392 | 0.253 | No | 38B339 | 270 | W
D0BE44 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.392 | 0.253 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.392 | 0.253 | No | 38B339 | 270 | W
B0FB49 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 4.092 | 0.392 | 0.253 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.392 | 0.253 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.392 | 0.253 | No | 8DA7DB | 180 | S
44F571 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 4.092 | 0.392 | 0.253 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 4.092 | 0.392 | 0.253 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 4.092 | 0.392 | 0.253 | No | BE5F2F | 270 | W
3833A2 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | C86329 | 90 | E
6BD844 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | C86329 | 90 | E
86D536 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | C86329 | 90 | E
BAF71D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | C86329 | 90 | E
142781 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.392 | 0.253 | No | 88E360 | 0 | N
9BC521 | WINDOW-NONRES-FIXED | 5.71 | 5.71 | 4.092 | 0.392 | 0.253 | No | 88E360 | 0 | N
2111A1 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 4.092 | 0.392 | 0.253 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.392 | 0.253 | No | 2E2D0C | 0 | N
E74902 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.392 | 0.253 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-NONRES-FIXED | 1.11 | 1.11 | 4.092 | 0.392 | 0.253 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 97.22 | 4.09 | 0.392 | 0.253
Non-North Total or Average |  |  | 211.08 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 161980.17 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 323450.86 | 241425.76 | 82025.1 | 0.75 | 2.91
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 278342.13 | 222299.4 | 56042.72 | 0.8 | 3.07
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2792.11 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 115.67 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 15044.94 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1604.19 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2076.47 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1007.49 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1098.71 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1965.08 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 147703.97 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 445.22 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 299.69 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 900.44 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 13142.55 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 495.75 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1239.36 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9198.1 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1024.54 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 4797.15 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2313.47 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 307.79 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 69497.37 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1239.36 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1451.1 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2643.7 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1024.54 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 111.54 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3725.06 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1239.36 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3673.44 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 42140.75 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 41167.24 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 34922.53 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 2008.92 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1090.64 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2602.66 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4654.49 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1239.36 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9811.64 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7489.46 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 267.57 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 16165.73 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1623.89 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 179.9 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2891.85 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1285.25 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 4131.2 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 10048 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2528.89 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 817.98 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 9475.46 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 1893.08 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2774.52 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 86.76 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2950.08 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 1623.37 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4308.59 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 303.94 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 6098.2 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3539.32 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4858.1 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 967.34 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2571.52 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1655.07 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3845.85 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2023.25 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1946.27 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 396.7 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 396.7 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 396.7 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 310.2 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 310.2 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 310.2 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 457.67 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 489.67 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 937.53 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1120.9 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5262.51 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 770.45 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 8013.32 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2895.34 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1258.02 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1325.87 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 92.11 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 192.6 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 230.18 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 577.67 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6261.35 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1576.51 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 375.34 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 4625.69 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 204.11 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 756.09 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 519.35 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 496.02 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 811.26 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5275.45 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1334.55 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3372.4 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 767.81 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 20780.97 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2256.44 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 375.34 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 13684.41 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3575.6 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 583.87 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 259.86 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 202.2 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2653.31 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 16018.29 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 12269.7 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 511.01 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5337.98 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1446.34 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2142.79 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1563.4 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1741.66 | 1
AHU-1_HEATC | Coil:Heating:Water | 7689.24 | -
AHU-2_HEATC | Coil:Heating:Water | 28099.94 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.76 | 28217.86 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.81 | 28305.13 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 891.93 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 67624.466 | 59.3276 | 370.1193 | 0 | 0.0002 | 2232370 | 24534.1609
February | 59096.3074 | 51.8649 | 320.0046 | 0 | 0.0002 | 1930090 | 21429.653
March | 66695.6256 | 58.4927 | 368.6161 | 0 | 0.0002 | 2223330 | 24208.1016
April | 63340.0121 | 55.5719 | 346.105 | 0 | 0.0002 | 2087530 | 22978.0374
May | 67729.9299 | 59.3571 | 381.9677 | 0 | 0.0002 | 2303900 | 24606.8112
June | 67042.4904 | 58.7026 | 387.3974 | 0 | 0.0002 | 2336700 | 24385.453
July | 70201.9941 | 61.4472 | 409.5728 | 0 | 0.0002 | 2470480 | 25546.6188
August | 72442.1988 | 63.3546 | 432.2008 | 0 | 0.0002 | 2607020 | 26390.9947
September | 70018.9293 | 61.2343 | 417.9295 | 0 | 0.0002 | 2520940 | 25508.7558
October | 70102.9016 | 61.3805 | 405.3992 | 0 | 0.0002 | 2445290 | 25499.5891
November | 66020.3429 | 57.8708 | 370.1879 | 0 | 0.0002 | 2232840 | 23979.1806
December | 67664.164 | 59.3602 | 370.7343 | 0 | 0.0002 | 2236090 | 24549.7766
Annual Sum or Average | 807979.3622 | 707.9644 | 4580.2347 | 0 | 0.0027 | 27626600 | 293617.1326
Minimum of Months | 59096.3074 | 51.8649 | 320.0046 | 0 | 0.0002 | 1930090 | 21429.653
Maximum of Months | 72442.1988 | 63.3546 | 432.2008 | 0 | 0.0002 | 2607020 | 26390.9947
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 457721000000 | 357889.003 | 17-JAN-14:00 | 58033.2 | 120867.849 | 32185.731 | 3820.783 | 42081.438 | 0 | 900.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 395741000000 | 325592.687 | 15-FEB-15:00 | 58033.2 | 120867.849 | 33837.538 | 405.826 | 111548.272 | 0 | 900.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 455866000000 | 360703.746 | 13-MAR-12:00 | 58033.2 | 120867.849 | 31782.653 | 3378.316 | 45741.727 | 0 | 900.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 428022000000 | 371266.332 | 05-APR-09:00 | 58033.2 | 120867.849 | 31550.842 | 6289.798 | 53624.642 | 0 | 900.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 472386000000 | 335273.419 | 17-MAY-13:00 | 58033.2 | 120867.849 | 33933.705 | 99.853 | 121438.812 | 0 | 900.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 479112000000 | 340732.569 | 15-JUN-12:00 | 58033.2 | 120867.849 | 34066.96 | 111.749 | 126752.81 | 0 | 900.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 506542000000 | 361195.868 | 03-JUL-12:00 | 58033.2 | 120867.849 | 34276.784 | 60.968 | 147057.065 | 0 | 900.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 534537000000 | 356514.995 | 15-AUG-12:09 | 58033.2 | 120867.849 | 33830.992 | 137.577 | 142745.376 | 0 | 900.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 516887000000 | 384619.167 | 28-SEP-14:00 | 58033.2 | 120867.849 | 38850.863 | 17.732 | 165949.522 | 0 | 900.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 501376000000 | 336477.815 | 31-OCT-12:00 | 58033.2 | 120867.849 | 33667.582 | 618.966 | 122390.217 | 0 | 900.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 457816000000 | 348957.498 | 20-NOV-09:09 | 58033.2 | 120867.849 | 31236.614 | 25530.865 | 12388.969 | 0 | 900.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 458481000000 | 343583.246 | 29-DEC-09:09 | 58033.2 | 120867.849 | 31366.1 | 32416.096 | 0 | 0 | 900.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 5664490000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 395741000000 | 325592.687 |  | 58033.2 | 120867.849 | 31236.614 | 17.732 | 0 | 0 | 900.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 534537000000 | 384619.167 |  | 58033.2 | 120867.849 | 38850.863 | 32416.096 | 165949.522 | 0 | 900.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 229321.43 | 51063.8 | 0 | 280385.24
Cost per Total Building Area ($/m2) | 60.28 | 13.42 | 0 | 73.71
Cost per Net Conditioned Building Area ($/m2) | 60.28 | 13.42 | 0 | 73.71

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 13748.87 | 3614.31 | 3614.31
Net Site Energy | 13748.87 | 3614.31 | 3614.31
Total Source Energy | 33594.81 | 8831.42 | 8831.42
Net Source Energy | 33594.81 | 8831.42 | 8831.42
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 443.87 | 6028.92 | 0 | 0 | 0 | 0
Cooling | 2477.82 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 879.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 31.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1015.96 | 0 | 0 | 0 | 0 | 0
Pumps | 32.05 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 613.26 | 0 | 0 | 0 | 0 | 228.13
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 51.28 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7480.29 | 6268.58 | 0 | 0 | 0 | 468.61
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 22.6 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 14 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 19.4 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 7.53 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 7.53 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 10.8 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 22.6 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 22.6 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 10.8 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 75.3 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 24.7 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 17.2 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 10.8 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 24.7 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 19.4 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 24.7 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 8.61 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 10.8 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 8.61 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 8.61 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 10.8 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 8.61 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 19.4 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 17.2 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 19.4 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 10.8 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 10.8 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 19.4 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 22.6 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 8.61 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 8.61 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 7.53 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 19.4 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 17.2 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 19.4 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 19.4 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 19.4 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 8.61 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 8.61 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 8.61 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 8.61 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.505 | 0.547 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 3.354 | 0.355 | 0.274 | No | 5F762C | 180 | S
4A8120 | WINDOW-NONRES-FIXED | 2.32 | 2.32 | 3.354 | 0.355 | 0.274 | No | 84FB73 | 0 | N
AAE778 | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 3.354 | 0.355 | 0.274 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | F629C1 | 0 | N
8128A9 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | F629C1 | 0 | N
9B1541 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 879583 | 180 | S
CF850A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 879583 | 180 | S
A6BA23 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | E326E4 | 90 | E
D10D28 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | E326E4 | 90 | E
38B811 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 1D96D7 | 90 | E
591336 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 1D96D7 | 90 | E
18748E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 6D2616 | 0 | N
1D94BE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 6D2616 | 0 | N
137A56 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.355 | 0.274 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 28B002 | 180 | S
44E54A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 28B002 | 180 | S
8D508E | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 28B002 | 180 | S
B2D381 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 28B002 | 180 | S
757D10 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 3.354 | 0.355 | 0.274 | No | EA6DC8 | 180 | S
24167A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 997723 | 180 | S
2C0938 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 997723 | 180 | S
E33BAE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | B40F89 | 270 | W
8600DD | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | CEC7BD | 180 | S
88E1FC | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 859BC1 | 0 | N
E8D997 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 859BC1 | 0 | N
F83F33 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.355 | 0.274 | No | 61E610 | 90 | E
B1F5EE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | D95F04 | 90 | E
F52F3D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 208CCF | 90 | E
80885D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 3.354 | 0.355 | 0.274 | No | AEF992 | 180 | S
2BE8DE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 1775A6 | 270 | W
513E2A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 54D065 | 180 | S
1AD478 | WINDOW-NONRES-FIXED | 3.72 | 3.72 | 3.354 | 0.355 | 0.274 | No | 97F00A | 180 | S
27F0AC | WINDOW-NONRES-FIXED | 5.95 | 5.95 | 3.354 | 0.355 | 0.274 | No | A497E9 | 180 | S
724114 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 88A75F | 180 | S
5635BC | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.355 | 0.274 | No | B4E619 | 90 | E
D538C4 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.355 | 0.274 | No | B4E619 | 90 | E
831C1D | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 3.354 | 0.355 | 0.274 | No | 9EC269 | 0 | N
9BB95F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | B316F7 | 0 | N
C0778D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | B316F7 | 0 | N
2EF63B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 9621FD | 0 | N
7D2D69 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 9621FD | 0 | N
C417C0 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 4B1439 | 90 | E
D23C8B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 4B1439 | 90 | E
EB042B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 4B1439 | 90 | E
E55A57 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.355 | 0.274 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 3.354 | 0.355 | 0.274 | No | 4ABC66 | 180 | S
93D018 | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 3.354 | 0.355 | 0.274 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | 4B55FA | 90 | E
15B02B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 9C3A6A | 0 | N
820282 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 68A2D7 | 0 | N
A2790A | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 3.354 | 0.355 | 0.274 | No | CE3FEF | 0 | N
79FCEE | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.355 | 0.274 | No | CE618F | 90 | E
EDE617 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.355 | 0.274 | No | CE618F | 90 | E
29FA28 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 5ADC59 | 0 | N
944FCE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 5ADC59 | 0 | N
C41399 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.355 | 0.274 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.355 | 0.274 | No | C1BC97 | 180 | S
3DB407 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.355 | 0.274 | No | C1BC97 | 180 | S
5031C8 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.355 | 0.274 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.355 | 0.274 | No | C1BC97 | 180 | S
95BA33 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.355 | 0.274 | No | D22917 | 90 | E
F27282 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.355 | 0.274 | No | D22917 | 90 | E
9DF7DE | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.355 | 0.274 | No | 38B339 | 270 | W
D0BE44 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.355 | 0.274 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.355 | 0.274 | No | 38B339 | 270 | W
B0FB49 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 3.354 | 0.355 | 0.274 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.355 | 0.274 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.355 | 0.274 | No | 8DA7DB | 180 | S
44F571 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 3.354 | 0.355 | 0.274 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 3.354 | 0.355 | 0.274 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 3.354 | 0.355 | 0.274 | No | BE5F2F | 270 | W
3833A2 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | C86329 | 90 | E
6BD844 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | C86329 | 90 | E
86D536 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | C86329 | 90 | E
BAF71D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.355 | 0.274 | No | C86329 | 90 | E
142781 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.355 | 0.274 | No | 88E360 | 0 | N
9BC521 | WINDOW-NONRES-FIXED | 5.71 | 5.71 | 3.354 | 0.355 | 0.274 | No | 88E360 | 0 | N
2111A1 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 3.354 | 0.355 | 0.274 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.355 | 0.274 | No | 2E2D0C | 0 | N
E74902 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.355 | 0.274 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-NONRES-FIXED | 1.11 | 1.11 | 3.354 | 0.355 | 0.274 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 3.35 | 0.355 | 0.274
North Total or Average |  |  | 97.22 | 3.35 | 0.355 | 0.274
Non-North Total or Average |  |  | 211.08 | 3.35 | 0.355 | 0.274
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 183076.95 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 413369.68 | 284457.42 | 128912.26 | 0.69 | 2.76
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 353276.02 | 252350.09 | 100925.93 | 0.71 | 2.83
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2169.21 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 189.12 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 12856.7 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1770.69 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2290.51 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1218.42 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1633.01 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2224.67 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 149040.01 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 565.4 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 554.74 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1090.86 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 13738.92 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 866.36 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1233.21 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 10897.94 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1804.87 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 5279.57 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2361.29 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 561.19 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 70068.34 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1233.21 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 2159.84 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2890.34 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1804.87 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 183.72 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 4077.26 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1233.21 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 4374.61 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 41599.54 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 42187.84 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35837.44 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 2148.1 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1918.5 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2589.75 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4631.4 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1233.21 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9762.97 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7274.54 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 487.34 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 13852.27 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1624.84 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 333.43 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2877.5 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1278.88 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 4110.71 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 9501.2 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2562.91 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 1181.95 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 13207.43 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2732.47 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 4045.4 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 146.11 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 4226.41 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 2038.31 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3602.47 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 303.79 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5801.27 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3036.26 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4070.06 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 663.06 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2862.9 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2049.62 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4204.96 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2487.2 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2127.81 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 376.07 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 376.07 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 376.07 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 404.19 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 404.19 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 402.68 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 686.14 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 489.69 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 937.53 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1120.9 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5777.08 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 870.36 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 7242.53 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1992.55 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1258.03 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1325.88 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 92.04 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 192.47 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 230.03 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 693.68 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6707.58 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1650.79 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 373.47 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 4625.7 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 217.59 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 931.33 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 497.89 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 726.24 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 793.88 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5475.07 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1327.91 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3612.91 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 947.31 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 21821.08 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2649.05 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 373.47 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 10719.84 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3507.88 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 580.97 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 348.67 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 272.39 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2601.79 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 14585.18 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 10907.12 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 619.33 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6003.79 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1847.66 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1657.48 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2224.54 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1254.43 | 1
AHU-1_HEATC | Coil:Heating:Water | 24301.74 | -
AHU-2_HEATC | Coil:Heating:Water | 61243.2 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.47 | 29400.77 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.45 | 27683.94 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 1008.1 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 138016.2275 | 241.5411 | 642.5383 | 0 | 0.0027 | 39952.753 | 58398.4881
February | 122509.6518 | 214.8976 | 573.0769 | 0 | 0.0024 | 35633.8651 | 51882.4345
March | 131977.9638 | 232.0336 | 620.2801 | 0 | 0.0026 | 38569.1525 | 55940.4594
April | 121232.9555 | 211.9831 | 563.3776 | 0 | 0.0023 | 35030.5067 | 51280.0356
May | 128704.9823 | 227.2984 | 610.5242 | 0 | 0.0025 | 37962.9107 | 54646.3445
June | 135759.006 | 245.0411 | 673.1673 | 0 | 0.0028 | 41860.0836 | 58124.6337
July | 142929.4614 | 259.8467 | 719.0099 | 0 | 0.0029 | 44711.4099 | 61364.9942
August | 145449.9626 | 265.745 | 738.9555 | 0 | 0.003 | 45952.1841 | 62567.468
September | 128092.5954 | 228.2319 | 618.7453 | 0 | 0.0025 | 38474.8582 | 54570.5807
October | 128541.1928 | 226.523 | 607.063 | 0 | 0.0025 | 37747.5088 | 54532.3505
November | 126106.1065 | 221.4613 | 591.3089 | 0 | 0.0024 | 36767.6255 | 53428.8454
December | 134709.7229 | 236.0268 | 628.6486 | 0 | 0.0026 | 39089.203 | 57024.3183
Annual Sum or Average | 1584030 | 2810.6296 | 7586.6955 | 0 | 0.0312 | 471752.0612 | 673760.9528
Minimum of Months | 121232.9555 | 211.9831 | 563.3776 | 0 | 0.0023 | 35030.5067 | 51280.0356
Maximum of Months | 145449.9626 | 265.745 | 738.9555 | 0 | 0.003 | 45952.1841 | 62567.468
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 633507000000 | 370969.175 | 17-JAN-07:10 | 58033.2 | 96785.431 | 32362.317 | 98815.98 | 0 | 2025 | 1016.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 565025000000 | 364365.716 | 21-FEB-09:09 | 58033.2 | 120867.849 | 32363.561 | 67119.982 | 17466.642 | 0 | 1016.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 611568000000 | 359400.876 | 09-MAR-15:00 | 58033.2 | 120867.849 | 33425.286 | 1827.389 | 144230.983 | 0 | 1016.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 555458000000 | 352707.131 | 04-APR-15:00 | 58033.2 | 120867.849 | 33864.042 | 573.299 | 138352.572 | 0 | 1016.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 601955000000 | 402658.702 | 31-MAY-15:00 | 58033.2 | 120867.849 | 34367.752 | 238.828 | 188134.903 | 0 | 1016.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 663750000000 | 447808.177 | 30-JUN-16:00 | 58033.2 | 120867.849 | 37609.163 | 48.503 | 230233.292 | 0 | 1016.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 708962000000 | 451024.625 | 25-JUL-12:00 | 58033.2 | 120867.849 | 36363.118 | 92.382 | 234651.906 | 0 | 1016.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 728636000000 | 451266.486 | 17-AUG-15:50 | 58033.2 | 120867.849 | 37496.795 | 63.294 | 233789.178 | 0 | 1016.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 610073000000 | 409823.323 | 08-SEP-14:00 | 58033.2 | 120867.849 | 36338.783 | 92.187 | 193475.135 | 0 | 1016.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 598540000000 | 384478.526 | 03-OCT-09:00 | 58033.2 | 120867.849 | 32945.647 | 2739.889 | 168875.772 | 0 | 1016.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 583002000000 | 364531.937 | 03-NOV-13:00 | 58033.2 | 120867.849 | 34031.082 | 1659.781 | 148923.856 | 0 | 1016.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 619814000000 | 351596.735 | 11-DEC-09:09 | 58033.2 | 120867.849 | 32372.456 | 56331.043 | 27894.305 | 0 | 1016.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 7480290000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 555458000000 | 351596.735 |  | 58033.2 | 96785.431 | 32362.317 | 48.503 | 0 | 0 | 1016.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 728636000000 | 451266.486 |  | 58033.2 | 120867.849 | 37609.163 | 98815.98 | 234651.906 | 2025 | 1016.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 140249.28 | 63609.19 | 0 | 203858.47
Cost per Total Building Area ($/m2) | 36.87 | 16.72 | 0 | 53.59
Cost per Net Conditioned Building Area ($/m2) | 36.87 | 16.72 | 0 | 53.59

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 13361.42 | 3512.46 | 3512.46
Net Site Energy | 13361.42 | 3512.46 | 3512.46
Total Source Energy | 31659.16 | 8322.58 | 8322.58
Net Source Energy | 31659.16 | 8322.58 | 8322.58
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 329.81 | 5454.8 | 0 | 0 | 0 | 0
Cooling | 1426.83 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 879.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 31.82 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1171.3 | 0 | 0 | 0 | 0 | 0
Pumps | 28.83 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 1813.67 | 0 | 0 | 0 | 0 | 674.69
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 50.47 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7667.78 | 5693.64 | 0 | 0 | 0 | 915.17
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 22.6 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 14 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 19.4 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 7.53 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 7.53 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 10.8 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 22.6 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 22.6 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 10.8 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 75.3 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 24.7 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 17.2 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 10.8 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 24.7 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 19.4 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 24.7 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 8.61 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 10.8 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 8.61 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 8.61 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 10.8 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 8.61 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 19.4 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 17.2 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 19.4 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 10.8 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 10.8 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 19.4 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 22.6 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 8.61 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 8.61 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 7.53 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 19.4 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 17.2 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 19.4 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 19.4 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 19.4 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 8.61 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 8.61 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 8.61 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 8.61 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.568 | 0.621 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 4.092 | 0.362 | 0.225 | No | 5F762C | 180 | S
4A8120 | WINDOW-NONRES-FIXED | 2.32 | 2.32 | 4.092 | 0.362 | 0.225 | No | 84FB73 | 0 | N
AAE778 | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 4.092 | 0.362 | 0.225 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | F629C1 | 0 | N
8128A9 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | F629C1 | 0 | N
9B1541 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 879583 | 180 | S
CF850A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 879583 | 180 | S
A6BA23 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | E326E4 | 90 | E
D10D28 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | E326E4 | 90 | E
38B811 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 1D96D7 | 90 | E
591336 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 1D96D7 | 90 | E
18748E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 6D2616 | 0 | N
1D94BE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 6D2616 | 0 | N
137A56 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.362 | 0.225 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 28B002 | 180 | S
44E54A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 28B002 | 180 | S
8D508E | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 28B002 | 180 | S
B2D381 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 28B002 | 180 | S
757D10 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 4.092 | 0.362 | 0.225 | No | EA6DC8 | 180 | S
24167A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 997723 | 180 | S
2C0938 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 997723 | 180 | S
E33BAE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | B40F89 | 270 | W
8600DD | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | CEC7BD | 180 | S
88E1FC | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 859BC1 | 0 | N
E8D997 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 859BC1 | 0 | N
F83F33 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.362 | 0.225 | No | 61E610 | 90 | E
B1F5EE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | D95F04 | 90 | E
F52F3D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 208CCF | 90 | E
80885D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 4.092 | 0.362 | 0.225 | No | AEF992 | 180 | S
2BE8DE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 1775A6 | 270 | W
513E2A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 54D065 | 180 | S
1AD478 | WINDOW-NONRES-FIXED | 3.72 | 3.72 | 4.092 | 0.362 | 0.225 | No | 97F00A | 180 | S
27F0AC | WINDOW-NONRES-FIXED | 5.95 | 5.95 | 4.092 | 0.362 | 0.225 | No | A497E9 | 180 | S
724114 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 88A75F | 180 | S
5635BC | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.362 | 0.225 | No | B4E619 | 90 | E
D538C4 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.362 | 0.225 | No | B4E619 | 90 | E
831C1D | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 4.092 | 0.362 | 0.225 | No | 9EC269 | 0 | N
9BB95F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | B316F7 | 0 | N
C0778D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | B316F7 | 0 | N
2EF63B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 9621FD | 0 | N
7D2D69 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 9621FD | 0 | N
C417C0 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 4B1439 | 90 | E
D23C8B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 4B1439 | 90 | E
EB042B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 4B1439 | 90 | E
E55A57 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.362 | 0.225 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 4.092 | 0.362 | 0.225 | No | 4ABC66 | 180 | S
93D018 | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 4.092 | 0.362 | 0.225 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | 4B55FA | 90 | E
15B02B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 9C3A6A | 0 | N
820282 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 68A2D7 | 0 | N
A2790A | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 4.092 | 0.362 | 0.225 | No | CE3FEF | 0 | N
79FCEE | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.362 | 0.225 | No | CE618F | 90 | E
EDE617 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.362 | 0.225 | No | CE618F | 90 | E
29FA28 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 5ADC59 | 0 | N
944FCE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 5ADC59 | 0 | N
C41399 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.362 | 0.225 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.362 | 0.225 | No | C1BC97 | 180 | S
3DB407 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.362 | 0.225 | No | C1BC97 | 180 | S
5031C8 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.362 | 0.225 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.362 | 0.225 | No | C1BC97 | 180 | S
95BA33 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.362 | 0.225 | No | D22917 | 90 | E
F27282 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.362 | 0.225 | No | D22917 | 90 | E
9DF7DE | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.362 | 0.225 | No | 38B339 | 270 | W
D0BE44 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.362 | 0.225 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.362 | 0.225 | No | 38B339 | 270 | W
B0FB49 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 4.092 | 0.362 | 0.225 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.362 | 0.225 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.362 | 0.225 | No | 8DA7DB | 180 | S
44F571 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 4.092 | 0.362 | 0.225 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 4.092 | 0.362 | 0.225 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 4.092 | 0.362 | 0.225 | No | BE5F2F | 270 | W
3833A2 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | C86329 | 90 | E
6BD844 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | C86329 | 90 | E
86D536 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | C86329 | 90 | E
BAF71D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.362 | 0.225 | No | C86329 | 90 | E
142781 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.362 | 0.225 | No | 88E360 | 0 | N
9BC521 | WINDOW-NONRES-FIXED | 5.71 | 5.71 | 4.092 | 0.362 | 0.225 | No | 88E360 | 0 | N
2111A1 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 4.092 | 0.362 | 0.225 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.362 | 0.225 | No | 2E2D0C | 0 | N
E74902 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.362 | 0.225 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-NONRES-FIXED | 1.11 | 1.11 | 4.092 | 0.362 | 0.225 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 4.09 | 0.362 | 0.225
North Total or Average |  |  | 97.22 | 4.09 | 0.362 | 0.225
Non-North Total or Average |  |  | 211.08 | 4.09 | 0.362 | 0.225
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 164539.4 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 331988.78 | 265144.58 | 66844.19 | 0.8 | 3.07
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 306402.89 | 244710.28 | 61692.61 | 0.8 | 3.07
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 1838.22 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 137.09 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 12032.69 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1698.85 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2195.8 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1130.16 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1473.34 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2033.32 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148464.32 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 485.49 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 402.75 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1010.37 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 13231.41 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 656.21 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1020.28 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 10010.21 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1362.11 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 5061.93 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2212.54 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 414.52 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 69846.98 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1020.28 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1881.18 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2780.68 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1362.11 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 132.67 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3924.19 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1020.28 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 4089.4 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 39643.05 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 41183.24 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35449.73 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 2087.99 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1448.37 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2412.43 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 3877.13 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1020.28 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 8077.26 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 6592.16 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 360.43 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 12362.66 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1355.09 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 241.79 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2380.66 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1058.06 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 3400.94 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 8537.15 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2066.91 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 894.26 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 12039.3 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2517.45 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3660.74 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 104.25 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 3894.01 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 1685.56 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3171.39 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 299.46 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5425.6 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2861.26 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3829.66 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 574.31 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2567.58 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1801.76 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3990.64 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2198.73 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2017.42 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 316.61 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 316.61 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 316.61 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 343.25 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 343.25 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 341.9 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 594.42 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 490.02 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 938.02 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1121.51 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5191.81 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 795.57 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 6810.5 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1773.09 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1260.06 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1328.04 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 91.32 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 191.42 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 228.87 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 561.6 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6428.4 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1579.83 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 308.86 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 4630.41 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 201.04 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 839.91 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 493.29 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 632.8 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 783.54 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5191.58 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1098.16 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3347.77 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 765.14 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 20428.6 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2096.58 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 325.7 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9625.4 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3454.11 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 480.45 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 280.23 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 218.11 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2558.39 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 13844.07 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 10125.77 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 504.62 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5298.07 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1870.11 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1693.4 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2085.61 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1190.62 | 1
AHU-1_HEATC | Coil:Heating:Water | 2640.53 | -
AHU-2_HEATC | Coil:Heating:Water | 46626.29 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 20.06 | 33760.56 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.51 | 31158.68 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 906.02 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 201143.4419 | 329.7411 | 797.3717 | 0 | 0.0032 | 828997.25 | 84051.0467
February | 179947.1026 | 295.1835 | 714.3752 | 0 | 0.0028 | 742710.2759 | 75212.4769
March | 203033.5568 | 334.1189 | 811.7887 | 0 | 0.0032 | 843995.3808 | 84966.347
April | 195652.0424 | 322.4763 | 785.007 | 0 | 0.0031 | 816154.863 | 81926.808
May | 206913.3727 | 342.6747 | 839.0524 | 0 | 0.0033 | 872356.4625 | 86802.9497
June | 192096.5824 | 317.9125 | 777.7576 | 0 | 0.0031 | 808627.2057 | 80565.1544
July | 191818.9307 | 316.9541 | 773.9333 | 0 | 0.0031 | 804647.538 | 80399.7733
August | 193458.8254 | 320.016 | 782.4561 | 0 | 0.0031 | 813511.0482 | 81121.6719
September | 178671.0441 | 293.8599 | 713.4752 | 0 | 0.0028 | 741780.2476 | 74754.6203
October | 189963.6674 | 311.7923 | 755.1023 | 0 | 0.003 | 785054.1221 | 79416.5375
November | 191984.6201 | 315.2276 | 763.7756 | 0 | 0.003 | 794072.3194 | 80273.0199
December | 199317.1059 | 326.4365 | 788.4504 | 0 | 0.0031 | 819719.8755 | 83257.4126
Annual Sum or Average | 2324000 | 3826.3933 | 9302.5456 | 0 | 0.0368 | 9671630 | 972747.8181
Minimum of Months | 178671.0441 | 293.8599 | 713.4752 | 0 | 0.0028 | 741780.2476 | 74754.6203
Maximum of Months | 206913.3727 | 342.6747 | 839.0524 | 0 | 0.0033 | 872356.4625 | 86802.9497
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 657239000000 | 375600.164 | 26-JAN-15:00 | 58033.2 | 120867.849 | 39374.698 | 3252.508 | 53157.816 | 0 | 914.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 588830000000 | 383036.041 | 13-FEB-15:00 | 58033.2 | 120867.849 | 38988.725 | 2377.528 | 85619.849 | 0 | 914.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 669130000000 | 394844.763 | 02-MAR-14:00 | 58033.2 | 120867.849 | 40202.993 | 1157.476 | 91564.196 | 0 | 914.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 647057000000 | 427618.392 | 21-APR-16:00 | 58033.2 | 120867.849 | 42770.155 | 18.663 | 117722.285 | 0 | 914.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 691615000000 | 418102.289 | 12-MAY-13:00 | 58033.2 | 120867.849 | 41751.239 | 107.146 | 120741.875 | 0 | 914.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 641089000000 | 462090.59 | 26-JUN-16:00 | 58033.2 | 120867.849 | 43201.142 | 12.086 | 144263.216 | 0 | 914.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 637934000000 | 448606.046 | 31-JUL-16:40 | 58033.2 | 120867.849 | 45622.19 | 13.103 | 164201.596 | 0 | 914.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 644961000000 | 396352.794 | 01-AUG-14:00 | 58033.2 | 120867.849 | 45853.179 | 13.376 | 170671.096 | 0 | 914.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 588092000000 | 402475.547 | 20-SEP-16:00 | 58033.2 | 120867.849 | 43483.394 | 23.221 | 130598.207 | 0 | 914.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 622400000000 | 388731.178 | 13-OCT-14:00 | 58033.2 | 120867.849 | 42461.42 | 140.165 | 112502.081 | 0 | 914.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 629550000000 | 386010.235 | 08-NOV-17:30 | 58033.2 | 120867.849 | 38917.672 | 1614.17 | 63638.25 | 2025 | 914.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 649884000000 | 366733.909 | 08-DEC-14:00 | 58033.2 | 120867.849 | 38743.003 | 4231.481 | 43944.281 | 0 | 914.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 7667780000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 588092000000 | 366733.909 |  | 58033.2 | 120867.849 | 38743.003 | 12.086 | 43944.281 | 0 | 914.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 691615000000 | 462090.59 |  | 58033.2 | 120867.849 | 45853.179 | 4231.481 | 170671.096 | 2025 | 914.093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 78846.48 | 41268.27 | 0 | 120114.75
Cost per Total Building Area ($/m2) | 20.73 | 10.85 | 0 | 31.58
Cost per Net Conditioned Building Area ($/m2) | 20.73 | 10.85 | 0 | 31.58

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 12238.78 | 3217.34 | 3217.34
Net Site Energy | 12238.78 | 3217.34 | 3217.34
Total Source Energy | 17202.16 | 4522.12 | 4522.12
Net Source Energy | 17202.16 | 4522.12 | 4522.12
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 519.59 | 6093.21 | 0 | 0 | 0 | 0
Cooling | 925.55 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 879.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 31.76 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1005.69 | 0 | 0 | 0 | 0 | 0
Pumps | 30.31 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 525.3 | 0 | 0 | 0 | 0 | 195.41
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 53.48 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 5903.72 | 6335.06 | 0 | 0 | 0 | 435.89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 22.6 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 14 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 19.4 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 7.53 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 7.53 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 10.8 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 22.6 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 22.6 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 10.8 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 75.3 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 24.7 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 17.2 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 10.8 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 24.7 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 19.4 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 24.7 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 8.61 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 10.8 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 8.61 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 8.61 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 10.8 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 8.61 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 19.4 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 17.2 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 19.4 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 10.8 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 10.8 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 19.4 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 22.6 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 8.61 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 8.61 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 7.53 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 19.4 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 17.2 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 19.4 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 19.4 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 19.4 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 8.61 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 8.61 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 8.61 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 8.61 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.522 | 0.567 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 4.092 | 0.392 | 0.253 | No | 5F762C | 180 | S
4A8120 | WINDOW-NONRES-FIXED | 2.32 | 2.32 | 4.092 | 0.392 | 0.253 | No | 84FB73 | 0 | N
AAE778 | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 4.092 | 0.392 | 0.253 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | F629C1 | 0 | N
8128A9 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | F629C1 | 0 | N
9B1541 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 879583 | 180 | S
CF850A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 879583 | 180 | S
A6BA23 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | E326E4 | 90 | E
D10D28 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | E326E4 | 90 | E
38B811 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 1D96D7 | 90 | E
591336 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 1D96D7 | 90 | E
18748E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 6D2616 | 0 | N
1D94BE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 6D2616 | 0 | N
137A56 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.392 | 0.253 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 28B002 | 180 | S
44E54A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 28B002 | 180 | S
8D508E | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 28B002 | 180 | S
B2D381 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 28B002 | 180 | S
757D10 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 4.092 | 0.392 | 0.253 | No | EA6DC8 | 180 | S
24167A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 997723 | 180 | S
2C0938 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 997723 | 180 | S
E33BAE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | B40F89 | 270 | W
8600DD | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | CEC7BD | 180 | S
88E1FC | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 859BC1 | 0 | N
E8D997 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 859BC1 | 0 | N
F83F33 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.392 | 0.253 | No | 61E610 | 90 | E
B1F5EE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | D95F04 | 90 | E
F52F3D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 208CCF | 90 | E
80885D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 4.092 | 0.392 | 0.253 | No | AEF992 | 180 | S
2BE8DE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 1775A6 | 270 | W
513E2A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 54D065 | 180 | S
1AD478 | WINDOW-NONRES-FIXED | 3.72 | 3.72 | 4.092 | 0.392 | 0.253 | No | 97F00A | 180 | S
27F0AC | WINDOW-NONRES-FIXED | 5.95 | 5.95 | 4.092 | 0.392 | 0.253 | No | A497E9 | 180 | S
724114 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 88A75F | 180 | S
5635BC | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.392 | 0.253 | No | B4E619 | 90 | E
D538C4 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.392 | 0.253 | No | B4E619 | 90 | E
831C1D | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 4.092 | 0.392 | 0.253 | No | 9EC269 | 0 | N
9BB95F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | B316F7 | 0 | N
C0778D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | B316F7 | 0 | N
2EF63B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 9621FD | 0 | N
7D2D69 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 9621FD | 0 | N
C417C0 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 4B1439 | 90 | E
D23C8B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 4B1439 | 90 | E
EB042B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 4B1439 | 90 | E
E55A57 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.392 | 0.253 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 4.092 | 0.392 | 0.253 | No | 4ABC66 | 180 | S
93D018 | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 4.092 | 0.392 | 0.253 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | 4B55FA | 90 | E
15B02B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 9C3A6A | 0 | N
820282 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 68A2D7 | 0 | N
A2790A | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 4.092 | 0.392 | 0.253 | No | CE3FEF | 0 | N
79FCEE | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.392 | 0.253 | No | CE618F | 90 | E
EDE617 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.392 | 0.253 | No | CE618F | 90 | E
29FA28 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 5ADC59 | 0 | N
944FCE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 5ADC59 | 0 | N
C41399 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 4.092 | 0.392 | 0.253 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.392 | 0.253 | No | C1BC97 | 180 | S
3DB407 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.392 | 0.253 | No | C1BC97 | 180 | S
5031C8 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.392 | 0.253 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.392 | 0.253 | No | C1BC97 | 180 | S
95BA33 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.392 | 0.253 | No | D22917 | 90 | E
F27282 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.392 | 0.253 | No | D22917 | 90 | E
9DF7DE | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.392 | 0.253 | No | 38B339 | 270 | W
D0BE44 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.392 | 0.253 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 4.092 | 0.392 | 0.253 | No | 38B339 | 270 | W
B0FB49 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 4.092 | 0.392 | 0.253 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.392 | 0.253 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.392 | 0.253 | No | 8DA7DB | 180 | S
44F571 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 4.092 | 0.392 | 0.253 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 4.092 | 0.392 | 0.253 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 4.092 | 0.392 | 0.253 | No | BE5F2F | 270 | W
3833A2 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | C86329 | 90 | E
6BD844 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | C86329 | 90 | E
86D536 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | C86329 | 90 | E
BAF71D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 4.092 | 0.392 | 0.253 | No | C86329 | 90 | E
142781 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.392 | 0.253 | No | 88E360 | 0 | N
9BC521 | WINDOW-NONRES-FIXED | 5.71 | 5.71 | 4.092 | 0.392 | 0.253 | No | 88E360 | 0 | N
2111A1 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 4.092 | 0.392 | 0.253 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.392 | 0.253 | No | 2E2D0C | 0 | N
E74902 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 4.092 | 0.392 | 0.253 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-NONRES-FIXED | 1.11 | 1.11 | 4.092 | 0.392 | 0.253 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 97.22 | 4.09 | 0.392 | 0.253
Non-North Total or Average |  |  | 211.08 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 173058.86 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 337425.47 | 250696.85 | 86728.61 | 0.74 | 2.9
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 275683.56 | 220176.13 | 55507.43 | 0.8 | 3.07
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2751 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 119.33 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 15083.19 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1659.55 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2144.06 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1075.43 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1388.32 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2024.94 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148477.66 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 474.88 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 355.81 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 961.18 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 13576.5 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 580.65 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1222.29 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9855.92 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1205.72 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 4943.24 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2281.62 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 366.6 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 69680.98 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1222.29 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 1777.15 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2719.52 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1205.72 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 115.55 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3834.97 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1222.29 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3907.62 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 42687.98 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 41844.73 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35215.04 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 2053.57 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1281.9 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2566.83 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4590.41 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1222.29 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9676.55 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7624.83 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 318.78 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 15949.95 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1604.67 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 213.59 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2852.03 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1267.56 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 4074.33 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 9900.6 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2681.36 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 806.72 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 11302.57 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2344.83 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 3407.7 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 90.94 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 3619.05 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 1745.18 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4320.06 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 303.54 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 6070.92 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3465.61 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4759.93 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 940.49 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2780.88 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1834.94 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4006.65 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2236.77 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2029.26 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 362.9 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 362.9 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 362.9 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 357.34 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 356.73 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 354.74 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 563.64 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 489.7 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 937.53 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1120.9 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5648.65 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 819.43 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 7914.29 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2342.08 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1258.06 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1325.9 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 91.95 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 192.37 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 229.9 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 657.31 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6445.08 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1620.87 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 370.16 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 4625.76 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 201.88 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 809.09 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 491.71 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 600.5 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 781.52 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5212.9 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1316.13 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3536.74 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 768.67 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 20467.74 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2084.08 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 370.16 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 13177.12 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3443.65 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 575.81 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 264.26 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 206.04 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2549.77 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 15167.32 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 11533.64 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 495.1 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5761.62 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1652.5 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1643.26 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1763.02 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1367.78 | 1
AHU-1_HEATC | Coil:Heating:Water | 15357.33 | -
AHU-2_HEATC | Coil:Heating:Water | 46060.6 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.3 | 29116.25 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.65 | 28034.78 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 952.94 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 54385.4236 | 66.8278 | 111.7142 | 0 | 0.0005 | 1474690 | 20692.9737
February | 48378.6148 | 59.4924 | 99.6667 | 0 | 0.0004 | 1315660 | 18412.3428
March | 52938.58 | 65.172 | 109.5213 | 0 | 0.0005 | 1445770 | 20155.5362
April | 49572.0761 | 60.5342 | 99.4065 | 0 | 0.0004 | 1312140 | 18820.9533
May | 49760.6525 | 60.6242 | 98.8892 | 0 | 0.0004 | 1305280 | 18877.5291
June | 49414.766 | 61.173 | 104.3966 | 0 | 0.0005 | 1378190 | 18850.2249
July | 52388.0406 | 65.6346 | 115.6633 | 0 | 0.0005 | 1527080 | 20068.06
August | 53680.4139 | 68.0631 | 123.6844 | 0 | 0.0005 | 1633150 | 20649.8109
September | 49555.5612 | 61.2816 | 104.2746 | 0 | 0.0005 | 1376560 | 18896.898
October | 49843.6599 | 60.2641 | 96.1092 | 0 | 0.0004 | 1268490 | 18859.6195
November | 51158.9648 | 62.5828 | 103.296 | 0 | 0.0005 | 1363500 | 19435.3101
December | 52712.6925 | 63.8836 | 102.6036 | 0 | 0.0005 | 1354230 | 19961.333
Annual Sum or Average | 613789.4457 | 755.5335 | 1269.2256 | 0 | 0.0056 | 16754700 | 233680.5916
Minimum of Months | 48378.6148 | 59.4924 | 96.1092 | 0 | 0.0004 | 1268490 | 18412.3428
Maximum of Months | 54385.4236 | 68.0631 | 123.6844 | 0 | 0.0005 | 1633150 | 20692.9737
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 519622000000 | 355879.023 | 03-JAN-09:09 | 58033.2 | 120867.849 | 32318.579 | 43698.391 | 0 | 0 | 961.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 463588000000 | 372762.627 | 22-FEB-13:00 | 58033.2 | 120867.849 | 32415.22 | 5700.036 | 54785.316 | 0 | 961.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 509431000000 | 349891.318 | 23-MAR-15:30 | 58033.2 | 120867.849 | 33401.628 | 1835.296 | 34792.34 | 0 | 961.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 462347000000 | 338450.88 | 13-APR-16:00 | 58033.2 | 120867.849 | 32938.032 | 1981.409 | 34706.606 | 0 | 961.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 459930000000 | 341946.873 | 05-MAY-15:00 | 58033.2 | 120867.849 | 34165.555 | 243.252 | 127676.012 | 0 | 961.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 485619000000 | 346053.837 | 28-JUN-12:00 | 58033.2 | 120867.849 | 34893.694 | 243.782 | 131054.308 | 0 | 961.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 538085000000 | 368538.942 | 24-JUL-14:00 | 58033.2 | 120867.849 | 35315.054 | 89.732 | 153272.103 | 0 | 961.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 575457000000 | 362227.985 | 18-AUG-16:00 | 58033.2 | 120867.849 | 35965.707 | 58.279 | 146341.944 | 0 | 961.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 485047000000 | 368299.573 | 01-SEP-15:00 | 58033.2 | 120867.849 | 35799.403 | 91.406 | 152546.709 | 0 | 961.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 446965000000 | 315983.153 | 05-OCT-15:00 | 58033.2 | 120867.849 | 32814.573 | 2266.01 | 101040.516 | 0 | 961.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 480445000000 | 356342.474 | 20-NOV-09:09 | 58033.2 | 120867.849 | 32143.162 | 44337.258 | 0 | 0 | 961.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 477179000000 | 346444.381 | 11-DEC-07:10 | 58033.2 | 96785.431 | 32133.984 | 80481.227 | 0 | 2025 | 961.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 5903720000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 446965000000 | 315983.153 |  | 58033.2 | 96785.431 | 32133.984 | 58.279 | 0 | 0 | 961.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 575457000000 | 372762.627 |  | 58033.2 | 120867.849 | 35965.707 | 80481.227 | 153272.103 | 2025 | 961.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 118852.68 | 52381.02 | 0 | 171233.7
Cost per Total Building Area ($/m2) | 31.24 | 13.77 | 0 | 45.01
Cost per Net Conditioned Building Area ($/m2) | 31.24 | 13.77 | 0 | 45.01

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 13533.06 | 3557.58 | 3557.58
Net Site Energy | 13533.06 | 3557.58 | 3557.58
Total Source Energy | 32132.3 | 8446.96 | 8446.96
Net Source Energy | 32132.3 | 8446.96 | 8446.96
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 541.6 | 6217.88 | 0 | 0 | 0 | 0
Cooling | 1502.58 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 879.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 31.81 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1025.19 | 0 | 0 | 0 | 0 | 0
Pumps | 34.11 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 1070.99 | 0 | 0 | 0 | 0 | 398.41
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 55 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7071.8 | 6461.25 | 0 | 0 | 0 | 638.89
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 22.6 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 14 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 19.4 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 7.53 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 7.53 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 10.8 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 22.6 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 22.6 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 10.8 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 75.3 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 24.7 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 17.2 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 10.8 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 24.7 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 19.4 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 24.7 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 8.61 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 10.8 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 8.61 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 8.61 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 10.8 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 8.61 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 19.4 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 17.2 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 19.4 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 10.8 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 10.8 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 19.4 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 22.6 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 8.61 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 8.61 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 7.53 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 19.4 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 17.2 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 19.4 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 19.4 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 19.4 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 8.61 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 8.61 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 8.61 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 8.61 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 3.354 | 0.385 | 0.305 | No | 5F762C | 180 | S
4A8120 | WINDOW-NONRES-FIXED | 2.32 | 2.32 | 3.354 | 0.385 | 0.305 | No | 84FB73 | 0 | N
AAE778 | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 3.354 | 0.385 | 0.305 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | F629C1 | 0 | N
8128A9 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | F629C1 | 0 | N
9B1541 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 879583 | 180 | S
CF850A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 879583 | 180 | S
A6BA23 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | E326E4 | 90 | E
D10D28 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | E326E4 | 90 | E
38B811 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
591336 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
18748E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 6D2616 | 0 | N
1D94BE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 6D2616 | 0 | N
137A56 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.385 | 0.305 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 28B002 | 180 | S
44E54A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 28B002 | 180 | S
8D508E | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 28B002 | 180 | S
B2D381 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 28B002 | 180 | S
757D10 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 3.354 | 0.385 | 0.305 | No | EA6DC8 | 180 | S
24167A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 997723 | 180 | S
2C0938 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 997723 | 180 | S
E33BAE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | B40F89 | 270 | W
8600DD | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | CEC7BD | 180 | S
88E1FC | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 859BC1 | 0 | N
E8D997 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 859BC1 | 0 | N
F83F33 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.385 | 0.305 | No | 61E610 | 90 | E
B1F5EE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | D95F04 | 90 | E
F52F3D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 208CCF | 90 | E
80885D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 3.354 | 0.385 | 0.305 | No | AEF992 | 180 | S
2BE8DE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 1775A6 | 270 | W
513E2A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 54D065 | 180 | S
1AD478 | WINDOW-NONRES-FIXED | 3.72 | 3.72 | 3.354 | 0.385 | 0.305 | No | 97F00A | 180 | S
27F0AC | WINDOW-NONRES-FIXED | 5.95 | 5.95 | 3.354 | 0.385 | 0.305 | No | A497E9 | 180 | S
724114 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 88A75F | 180 | S
5635BC | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.385 | 0.305 | No | B4E619 | 90 | E
D538C4 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.385 | 0.305 | No | B4E619 | 90 | E
831C1D | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 3.354 | 0.385 | 0.305 | No | 9EC269 | 0 | N
9BB95F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | B316F7 | 0 | N
C0778D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | B316F7 | 0 | N
2EF63B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 9621FD | 0 | N
7D2D69 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 9621FD | 0 | N
C417C0 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 4B1439 | 90 | E
D23C8B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 4B1439 | 90 | E
EB042B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 4B1439 | 90 | E
E55A57 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 3.354 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
93D018 | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 3.354 | 0.385 | 0.305 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 4B55FA | 90 | E
15B02B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
820282 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
A2790A | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 3.354 | 0.385 | 0.305 | No | CE3FEF | 0 | N
79FCEE | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.385 | 0.305 | No | CE618F | 90 | E
EDE617 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.385 | 0.305 | No | CE618F | 90 | E
29FA28 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
944FCE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C41399 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.385 | 0.305 | No | C1BC97 | 180 | S
3DB407 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.385 | 0.305 | No | C1BC97 | 180 | S
5031C8 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.385 | 0.305 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.385 | 0.305 | No | C1BC97 | 180 | S
95BA33 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.385 | 0.305 | No | D22917 | 90 | E
F27282 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.385 | 0.305 | No | D22917 | 90 | E
9DF7DE | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.385 | 0.305 | No | 38B339 | 270 | W
D0BE44 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.385 | 0.305 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.385 | 0.305 | No | 38B339 | 270 | W
B0FB49 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 3.354 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
44F571 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 3.354 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 3.354 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 3.354 | 0.385 | 0.305 | No | BE5F2F | 270 | W
3833A2 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | C86329 | 90 | E
6BD844 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | C86329 | 90 | E
86D536 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | C86329 | 90 | E
BAF71D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | C86329 | 90 | E
142781 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.385 | 0.305 | No | 88E360 | 0 | N
9BC521 | WINDOW-NONRES-FIXED | 5.71 | 5.71 | 3.354 | 0.385 | 0.305 | No | 88E360 | 0 | N
2111A1 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 3.354 | 0.385 | 0.305 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
E74902 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-NONRES-FIXED | 1.11 | 1.11 | 3.354 | 0.385 | 0.305 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 97.22 | 3.35 | 0.385 | 0.305
Non-North Total or Average |  |  | 211.08 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 194952.98 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 410396.21 | 284204.63 | 126191.57 | 0.69 | 2.77
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 350831.04 | 250989.96 | 99841.09 | 0.72 | 2.83
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2173.28 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 170.66 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 12892.48 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1751.17 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2264.79 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1195.42 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2023.87 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2167.09 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 149054.18 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 547.52 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 508.57 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1069.65 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 13914.69 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 795.9 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1244.37 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 10782.73 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1657.92 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 5220.45 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2320.77 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 514.83 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 70004.72 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1212.46 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 2679.63 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2861.37 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1657.92 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 165.78 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 4036.66 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1212.46 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 4301.09 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 41532.65 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 42102.29 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35732.73 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 2132.09 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1762.26 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2546.19 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4553.49 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1212.46 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9598.74 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7216.1 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 447.11 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 13811.62 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1606.6 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 305.64 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2829.1 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1257.36 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 4041.56 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 9528.88 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2493.4 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 1070.67 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 16070.61 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 3356.84 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 4944.85 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 131.8 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 5144.34 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 2131.1 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3640.37 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 303.29 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5909.3 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3053.07 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4100.95 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 678.44 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2876.5 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2044.47 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4198.22 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2486.34 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2124.71 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 375.61 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 375.61 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 375.61 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 400.24 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 400.24 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 398.78 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 851.07 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 489.7 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 937.53 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1120.9 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5801.37 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 867.71 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 7380.7 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1934.6 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1258.09 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1325.92 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 91.92 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 192.23 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 229.73 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 737.16 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6687.58 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1641.18 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 389.72 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 4625.82 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 220.11 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 982.62 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 504.15 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 895.46 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 765.75 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5294.04 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1305.53 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3638.11 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 950.95 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 20832.7 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2654.11 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 429.97 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 10578.08 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3374.33 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 571.17 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 346.55 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 269.95 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2493.79 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 14282.45 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 10650.6 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 620.89 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6046.15 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2194.05 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1500.82 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2322.31 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1185.99 | 1
AHU-1_HEATC | Coil:Heating:Water | 36664.04 | -
AHU-2_HEATC | Coil:Heating:Water | 78050.64 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.63 | 29685.32 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.4 | 27599.21 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 1073.49 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 248207.4455 | 420.8957 | 1173.5811 | 0 | 0.0036 | 270131.3802 | 104606.1262
February | 217596.9169 | 370.0906 | 1035.4563 | 0 | 0.0032 | 238339.8726 | 91810.8326
March | 234336.093 | 399.7841 | 1122.4448 | 0 | 0.0034 | 258364.5886 | 98990.5684
April | 203279.5177 | 344.7878 | 961.6209 | 0 | 0.003 | 221343.1184 | 85678.897
May | 213443.7136 | 363.4438 | 1018.1924 | 0 | 0.0031 | 234366.7152 | 90098.3335
June | 237804.3184 | 410.3993 | 1167.2224 | 0 | 0.0036 | 268678.4787 | 100904.8601
July | 256964.6881 | 445.2733 | 1272.1026 | 0 | 0.0039 | 292823.0654 | 109207.7711
August | 259492.7809 | 449.8529 | 1285.81 | 0 | 0.0039 | 295978.6416 | 110301.202
September | 221639.1308 | 379.9453 | 1072.5537 | 0 | 0.0033 | 246883.3461 | 93801.2518
October | 213519.3427 | 363.0419 | 1015.3722 | 0 | 0.0031 | 233716.7656 | 90079.5237
November | 208847.0713 | 354.2797 | 988.2494 | 0 | 0.003 | 227472.4596 | 88030.168
December | 237935.5306 | 403.899 | 1127.5417 | 0 | 0.0035 | 259534.7956 | 100317.3925
Annual Sum or Average | 2753070 | 4705.6933 | 13240.1474 | 0 | 0.0406 | 3047630 | 1163830
Minimum of Months | 203279.5177 | 344.7878 | 961.6209 | 0 | 0.003 | 221343.1184 | 85678.897
Maximum of Months | 259492.7809 | 449.8529 | 1285.81 | 0 | 0.0039 | 295978.6416 | 110301.202
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 626820000000 | 377249.16 | 27-JAN-07:10 | 58033.2 | 96785.431 | 32788.028 | 93690.756 | 0 | 2025 | 1081.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 553050000000 | 351685.089 | 09-FEB-07:10 | 58033.2 | 96785.431 | 32785.184 | 79555.578 | 0 | 0 | 1081.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 599516000000 | 351684.233 | 20-MAR-08:09 | 58033.2 | 120867.849 | 32690.176 | 51229.562 | 0 | 0 | 1081.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 513610000000 | 385490.561 | 27-APR-14:00 | 58033.2 | 120867.849 | 33930.955 | 1737.24 | 69839.754 | 0 | 1081.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 543830000000 | 397547.866 | 30-MAY-15:00 | 58033.2 | 120867.849 | 33918.475 | 866.483 | 182780.296 | 0 | 1081.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 623448000000 | 434805.598 | 08-JUN-12:00 | 58033.2 | 120867.849 | 36141.443 | 259.179 | 218422.364 | 0 | 1081.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 679474000000 | 438378.175 | 13-JUL-14:00 | 58033.2 | 120867.849 | 37437.001 | 111.295 | 220847.267 | 0 | 1081.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 686796000000 | 433618.115 | 04-AUG-15:00 | 58033.2 | 120867.849 | 36997.125 | 122.899 | 216515.478 | 0 | 1081.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 572874000000 | 398604.486 | 06-SEP-10:00 | 58033.2 | 120867.849 | 34562.388 | 1299.769 | 182759.717 | 0 | 1081.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 542322000000 | 387354.357 | 26-OCT-15:30 | 58033.2 | 120867.849 | 33910.475 | 3647.517 | 69813.753 | 0 | 1081.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 527833000000 | 365657.854 | 02-NOV-14:39 | 58033.2 | 120867.849 | 34152.673 | 1962.729 | 149559.84 | 0 | 1081.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 602231000000 | 361238.677 | 26-DEC-09:09 | 58033.2 | 120867.849 | 32682.082 | 69520.995 | 0 | 0 | 1081.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 7071800000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 513610000000 | 351684.233 |  | 58033.2 | 96785.431 | 32682.082 | 111.295 | 0 | 0 | 1081.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 686796000000 | 438378.175 |  | 58033.2 | 120867.849 | 37437.001 | 93690.756 | 220847.267 | 2025 | 1081.563 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 190397.19 | 58263.4 | 0 | 248660.59
Cost per Total Building Area ($/m2) | 50.05 | 15.32 | 0 | 65.37
Cost per Net Conditioned Building Area ($/m2) | 50.05 | 15.32 | 0 | 65.37

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 13196.11 | 3469 | 3469
Net Site Energy | 13196.11 | 3469 | 3469
Total Source Energy | 30870.65 | 8115.3 | 8115.3
Net Source Energy | 30870.65 | 8115.3 | 8115.3
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 382.76 | 5558.27 | 0 | 0 | 0 | 0
Cooling | 1061.62 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 879.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 31.79 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1145.97 | 0 | 0 | 0 | 0 | 0
Pumps | 30.65 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 1876.34 | 0 | 0 | 0 | 0 | 698
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 54.81 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7394.65 | 5801.45 | 0 | 0 | 0 | 938.48
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 22.6 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 14 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 19.4 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 7.53 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 7.53 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 10.8 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 22.6 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 22.6 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 10.8 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 75.3 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 24.7 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 17.2 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 10.8 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 24.7 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 19.4 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 24.7 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 8.61 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 10.8 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 8.61 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 8.61 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 10.8 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 8.61 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 19.4 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 17.2 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 19.4 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 10.8 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 10.8 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 19.4 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 22.6 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 8.61 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 8.61 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 7.53 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 19.4 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 17.2 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 19.4 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 19.4 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 19.4 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 8.61 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 8.61 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 8.61 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 8.61 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.466 | 0.5 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 3.354 | 0.385 | 0.305 | No | 5F762C | 180 | S
4A8120 | WINDOW-NONRES-FIXED | 2.32 | 2.32 | 3.354 | 0.385 | 0.305 | No | 84FB73 | 0 | N
AAE778 | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 3.354 | 0.385 | 0.305 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | F629C1 | 0 | N
8128A9 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | F629C1 | 0 | N
9B1541 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 879583 | 180 | S
CF850A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 879583 | 180 | S
A6BA23 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | E326E4 | 90 | E
D10D28 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | E326E4 | 90 | E
38B811 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
591336 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
18748E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 6D2616 | 0 | N
1D94BE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 6D2616 | 0 | N
137A56 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.385 | 0.305 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 28B002 | 180 | S
44E54A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 28B002 | 180 | S
8D508E | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 28B002 | 180 | S
B2D381 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 28B002 | 180 | S
757D10 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 3.354 | 0.385 | 0.305 | No | EA6DC8 | 180 | S
24167A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 997723 | 180 | S
2C0938 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 997723 | 180 | S
E33BAE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | B40F89 | 270 | W
8600DD | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | CEC7BD | 180 | S
88E1FC | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 859BC1 | 0 | N
E8D997 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 859BC1 | 0 | N
F83F33 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.385 | 0.305 | No | 61E610 | 90 | E
B1F5EE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | D95F04 | 90 | E
F52F3D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 208CCF | 90 | E
80885D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 3.354 | 0.385 | 0.305 | No | AEF992 | 180 | S
2BE8DE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 1775A6 | 270 | W
513E2A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 54D065 | 180 | S
1AD478 | WINDOW-NONRES-FIXED | 3.72 | 3.72 | 3.354 | 0.385 | 0.305 | No | 97F00A | 180 | S
27F0AC | WINDOW-NONRES-FIXED | 5.95 | 5.95 | 3.354 | 0.385 | 0.305 | No | A497E9 | 180 | S
724114 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 88A75F | 180 | S
5635BC | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.385 | 0.305 | No | B4E619 | 90 | E
D538C4 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.385 | 0.305 | No | B4E619 | 90 | E
831C1D | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 3.354 | 0.385 | 0.305 | No | 9EC269 | 0 | N
9BB95F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | B316F7 | 0 | N
C0778D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | B316F7 | 0 | N
2EF63B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 9621FD | 0 | N
7D2D69 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 9621FD | 0 | N
C417C0 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 4B1439 | 90 | E
D23C8B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 4B1439 | 90 | E
EB042B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 4B1439 | 90 | E
E55A57 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 3.354 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
93D018 | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 3.354 | 0.385 | 0.305 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | 4B55FA | 90 | E
15B02B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
820282 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
A2790A | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 3.354 | 0.385 | 0.305 | No | CE3FEF | 0 | N
79FCEE | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.385 | 0.305 | No | CE618F | 90 | E
EDE617 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.385 | 0.305 | No | CE618F | 90 | E
29FA28 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
944FCE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C41399 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 3.354 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.385 | 0.305 | No | C1BC97 | 180 | S
3DB407 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.385 | 0.305 | No | C1BC97 | 180 | S
5031C8 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.385 | 0.305 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.385 | 0.305 | No | C1BC97 | 180 | S
95BA33 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.385 | 0.305 | No | D22917 | 90 | E
F27282 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.385 | 0.305 | No | D22917 | 90 | E
9DF7DE | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.385 | 0.305 | No | 38B339 | 270 | W
D0BE44 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.385 | 0.305 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 3.354 | 0.385 | 0.305 | No | 38B339 | 270 | W
B0FB49 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 3.354 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
44F571 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 3.354 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 3.354 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 3.354 | 0.385 | 0.305 | No | BE5F2F | 270 | W
3833A2 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | C86329 | 90 | E
6BD844 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | C86329 | 90 | E
86D536 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | C86329 | 90 | E
BAF71D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 3.354 | 0.385 | 0.305 | No | C86329 | 90 | E
142781 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.385 | 0.305 | No | 88E360 | 0 | N
9BC521 | WINDOW-NONRES-FIXED | 5.71 | 5.71 | 3.354 | 0.385 | 0.305 | No | 88E360 | 0 | N
2111A1 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 3.354 | 0.385 | 0.305 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
E74902 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 3.354 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-NONRES-FIXED | 1.11 | 1.11 | 3.354 | 0.385 | 0.305 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 97.22 | 3.35 | 0.385 | 0.305
Non-North Total or Average |  |  | 211.08 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 175013.52 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 326551.31 | 260801.92 | 65749.39 | 0.8 | 3.07
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 286484.87 | 228802.65 | 57682.22 | 0.8 | 3.07
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 1835.56 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 135.08 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 11780.11 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1694.56 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2190.15 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1124.36 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1770.18 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1940.05 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148498.8 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 496.5 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 396.88 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1005.12 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 12539.77 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 647.66 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1092.23 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9741.6 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1344.4 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 5048.93 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2154.84 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 408.48 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 69832.01 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1047.39 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 2298.6 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2774 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1344.4 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 130.73 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3914.56 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1018.4 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 4070.06 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 38922.7 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40091.43 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35425.15 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 2084.29 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1429.53 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2330.92 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 3865.69 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1043.38 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 8062.4 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 6426.8 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 355.17 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 11934.46 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1417.69 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 238.26 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2376.28 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1056.12 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 3394.68 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 8045.33 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2003.9 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 880.18 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 14248.1 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 2957.76 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 4408.52 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 102.74 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 4591.31 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 1894.41 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3041.47 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 299.46 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5034.72 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2808.2 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3759.34 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 552.35 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2320.51 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1699.08 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3895.47 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2078.73 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1967.56 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 314.07 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 314.07 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 314.07 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 340.38 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 340.38 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 338.98 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 726.91 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 490.02 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 938.02 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1121.51 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4649.23 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 790.44 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 6562.66 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1867.34 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1260.06 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1328.05 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 91.28 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 191.31 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 228.72 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 651.31 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6303.95 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1573.52 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 341.48 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 4630.42 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 205.89 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 912.16 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 469.22 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 769.57 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 739.07 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4840.65 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1096.14 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3123.17 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 791.76 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 18549.48 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2094.88 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 380.2 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9005.85 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3243.43 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 479.56 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 285.21 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 222.4 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2388.01 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 12718.67 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9207.24 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 532.56 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 4750.66 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2072.97 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1293.4 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2198.04 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1020.5 | 1
AHU-1_HEATC | Coil:Heating:Water | 16503.73 | -
AHU-2_HEATC | Coil:Heating:Water | 62728.67 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 19.73 | 33207.61 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.31 | 29133.18 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 963.7 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 203519.2381 | 332.8408 | 802.4869 | 0 | 0.0032 | 834309.5022 | 84965.8307
February | 179967.2397 | 294.7105 | 711.7162 | 0 | 0.0028 | 739942.1811 | 75171.2577
March | 199743.7613 | 328.3295 | 796.6025 | 0 | 0.0032 | 828203.9636 | 83552.7828
April | 186062.2033 | 305.5647 | 740.5463 | 0 | 0.0029 | 769921.9795 | 77802.7413
May | 180757.4488 | 295.8263 | 713.8767 | 0 | 0.0028 | 742187.0516 | 75483.8432
June | 172347.2622 | 282.5814 | 683.4715 | 0 | 0.0027 | 710579.8319 | 72022.6892
July | 186955.7523 | 308.5156 | 752.1322 | 0 | 0.003 | 781978.2801 | 78321.8993
August | 185267.0475 | 305.4112 | 743.6186 | 0 | 0.0029 | 773124.549 | 77583.2768
September | 178501.2103 | 293.3111 | 711.3383 | 0 | 0.0028 | 739556.6521 | 74657.1278
October | 190611.8907 | 313.0487 | 758.7204 | 0 | 0.003 | 788817.1825 | 79706.4091
November | 187701.6787 | 307.749 | 744.3211 | 0 | 0.003 | 773842.8212 | 78438.4492
December | 205967.4878 | 336.9 | 812.4394 | 0 | 0.0032 | 844657.097 | 85993.3512
Annual Sum or Average | 2257400 | 3704.7887 | 8971.2701 | 0 | 0.0356 | 9327120 | 943699.6582
Minimum of Months | 172347.2622 | 282.5814 | 683.4715 | 0 | 0.0027 | 710579.8319 | 72022.6892
Maximum of Months | 205967.4878 | 336.9 | 812.4394 | 0 | 0.0032 | 844657.097 | 85993.3512
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 661451000000 | 382183.309 | 23-JAN-13:00 | 58033.2 | 120867.849 | 36843.028 | 6014.937 | 59452.527 | 0 | 971.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 586635000000 | 367159.57 | 07-FEB-14:00 | 58033.2 | 120867.849 | 38035.673 | 4628.331 | 44622.748 | 0 | 971.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 656610000000 | 402421.499 | 30-MAR-13:00 | 58033.2 | 120867.849 | 39170.736 | 1237.239 | 89997.867 | 0 | 971.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 610403000000 | 383271.154 | 06-APR-12:00 | 58033.2 | 120867.849 | 37679.453 | 3191.148 | 62527.735 | 0 | 971.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 588415000000 | 393943.231 | 18-MAY-12:00 | 58033.2 | 120867.849 | 39250.645 | 728.789 | 106686.331 | 0 | 971.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 563356000000 | 414841.65 | 15-JUN-16:00 | 58033.2 | 120867.849 | 41649.935 | 166.37 | 109398.149 | 0 | 971.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 619962000000 | 408733.348 | 17-JUL-13:00 | 58033.2 | 120867.849 | 41288.573 | 117.023 | 149138.408 | 0 | 971.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 612942000000 | 406837.47 | 29-AUG-15:00 | 58033.2 | 120867.849 | 43528.058 | 55.434 | 150252.277 | 0 | 971.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 586329000000 | 421556.643 | 06-SEP-12:00 | 58033.2 | 120867.849 | 40253.647 | 490.301 | 124298.344 | 0 | 971.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 625384000000 | 398549.167 | 05-OCT-14:00 | 58033.2 | 120867.849 | 41792.975 | 423.333 | 119386.428 | 0 | 971.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 613512000000 | 383197.132 | 10-NOV-10:39 | 58033.2 | 120867.849 | 37098.369 | 7858.637 | 58367.309 | 0 | 971.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 669654000000 | 382176.104 | 11-DEC-07:10 | 58033.2 | 96785.431 | 36356.09 | 90897.415 | 0 | 2025 | 971.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 7394650000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 563356000000 | 367159.57 |  | 58033.2 | 96785.431 | 36356.09 | 55.434 | 0 | 0 | 971.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 669654000000 | 421556.643 |  | 58033.2 | 120867.849 | 43528.058 | 90897.415 | 150252.277 | 2025 | 971.768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 76044.81 | 42031.18 | 0 | 118075.99
Cost per Total Building Area ($/m2) | 19.99 | 11.05 | 0 | 31.04
Cost per Net Conditioned Building Area ($/m2) | 19.99 | 11.05 | 0 | 31.04

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 13784.37 | 3623.64 | 3623.64
Net Site Energy | 13784.37 | 3623.64 | 3623.64
Total Source Energy | 31598.27 | 8306.57 | 8306.57
Net Source Energy | 31598.27 | 8306.57 | 8306.57
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 561.42 | 6482.06 | 0 | 0 | 0 | 0
Cooling | 1359.58 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 879.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 31.79 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1022.01 | 0 | 0 | 0 | 0 | 0
Pumps | 35.07 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 1180.36 | 0 | 0 | 0 | 0 | 439.1
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 58.18 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7055.75 | 6728.62 | 0 | 0 | 0 | 679.57
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 22.6 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 14 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 19.4 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 7.53 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 7.53 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 10.8 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 22.6 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 22.6 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 10.8 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 75.3 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 24.7 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 17.2 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 10.8 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 24.7 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 19.4 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 24.7 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 8.61 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 10.8 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 8.61 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 8.61 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 10.8 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 8.61 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 19.4 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 17.2 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 19.4 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 10.8 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 10.8 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 19.4 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 22.6 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 8.61 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 8.61 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 7.53 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 19.4 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 17.2 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 19.4 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 19.4 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 19.4 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 8.61 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 8.61 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 8.61 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 8.61 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.369 | 0.391 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 2.956 | 0.385 | 0.305 | No | 5F762C | 180 | S
4A8120 | WINDOW-NONRES-FIXED | 2.32 | 2.32 | 2.956 | 0.385 | 0.305 | No | 84FB73 | 0 | N
AAE778 | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 2.956 | 0.385 | 0.305 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | F629C1 | 0 | N
8128A9 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | F629C1 | 0 | N
9B1541 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 879583 | 180 | S
CF850A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 879583 | 180 | S
A6BA23 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | E326E4 | 90 | E
D10D28 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | E326E4 | 90 | E
38B811 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
591336 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
18748E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 6D2616 | 0 | N
1D94BE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 6D2616 | 0 | N
137A56 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.385 | 0.305 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 28B002 | 180 | S
44E54A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 28B002 | 180 | S
8D508E | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 28B002 | 180 | S
B2D381 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 28B002 | 180 | S
757D10 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 2.956 | 0.385 | 0.305 | No | EA6DC8 | 180 | S
24167A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 997723 | 180 | S
2C0938 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 997723 | 180 | S
E33BAE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | B40F89 | 270 | W
8600DD | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | CEC7BD | 180 | S
88E1FC | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 859BC1 | 0 | N
E8D997 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 859BC1 | 0 | N
F83F33 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.385 | 0.305 | No | 61E610 | 90 | E
B1F5EE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | D95F04 | 90 | E
F52F3D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 208CCF | 90 | E
80885D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 2.956 | 0.385 | 0.305 | No | AEF992 | 180 | S
2BE8DE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 1775A6 | 270 | W
513E2A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 54D065 | 180 | S
1AD478 | WINDOW-NONRES-FIXED | 3.72 | 3.72 | 2.956 | 0.385 | 0.305 | No | 97F00A | 180 | S
27F0AC | WINDOW-NONRES-FIXED | 5.95 | 5.95 | 2.956 | 0.385 | 0.305 | No | A497E9 | 180 | S
724114 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 88A75F | 180 | S
5635BC | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.385 | 0.305 | No | B4E619 | 90 | E
D538C4 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.385 | 0.305 | No | B4E619 | 90 | E
831C1D | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 2.956 | 0.385 | 0.305 | No | 9EC269 | 0 | N
9BB95F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | B316F7 | 0 | N
C0778D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | B316F7 | 0 | N
2EF63B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 9621FD | 0 | N
7D2D69 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 9621FD | 0 | N
C417C0 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 4B1439 | 90 | E
D23C8B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 4B1439 | 90 | E
EB042B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 4B1439 | 90 | E
E55A57 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 2.956 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
93D018 | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 2.956 | 0.385 | 0.305 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 4B55FA | 90 | E
15B02B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
820282 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
A2790A | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 2.956 | 0.385 | 0.305 | No | CE3FEF | 0 | N
79FCEE | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.385 | 0.305 | No | CE618F | 90 | E
EDE617 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.385 | 0.305 | No | CE618F | 90 | E
29FA28 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
944FCE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C41399 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.385 | 0.305 | No | C1BC97 | 180 | S
3DB407 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.385 | 0.305 | No | C1BC97 | 180 | S
5031C8 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.385 | 0.305 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.385 | 0.305 | No | C1BC97 | 180 | S
95BA33 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.385 | 0.305 | No | D22917 | 90 | E
F27282 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.385 | 0.305 | No | D22917 | 90 | E
9DF7DE | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.385 | 0.305 | No | 38B339 | 270 | W
D0BE44 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.385 | 0.305 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.385 | 0.305 | No | 38B339 | 270 | W
B0FB49 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 2.956 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
44F571 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 2.956 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 2.956 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 2.956 | 0.385 | 0.305 | No | BE5F2F | 270 | W
3833A2 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | C86329 | 90 | E
6BD844 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | C86329 | 90 | E
86D536 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | C86329 | 90 | E
BAF71D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | C86329 | 90 | E
142781 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.385 | 0.305 | No | 88E360 | 0 | N
9BC521 | WINDOW-NONRES-FIXED | 5.71 | 5.71 | 2.956 | 0.385 | 0.305 | No | 88E360 | 0 | N
2111A1 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 2.956 | 0.385 | 0.305 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
E74902 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-NONRES-FIXED | 1.11 | 1.11 | 2.956 | 0.385 | 0.305 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 97.22 | 2.96 | 0.385 | 0.305
Non-North Total or Average |  |  | 211.08 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 200484.34 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 399411.61 | 279197.6 | 120214.01 | 0.7 | 2.79
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 329046.71 | 237174.25 | 91872.45 | 0.72 | 2.85
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2238.12 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 162.84 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 13009.78 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1742.92 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2253.9 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1185.37 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2167.18 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2094.17 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 149048.74 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 538.63 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 488.99 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1060.37 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 13394.68 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 766.02 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1323.19 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 10597.38 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1595.41 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 5195.25 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2262.45 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 495.18 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 69977.57 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1277.87 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 2884.57 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2848.9 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1595.41 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 158.17 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 4019.26 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1203.13 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 4269.97 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 41187.38 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 41848.96 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35688.03 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 2125.24 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1695.73 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2526.58 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4518.43 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1274.6 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9524.83 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7139.21 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 430.05 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 13512.63 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1709.09 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 293.86 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2807.32 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1247.68 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 4010.44 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 9111.18 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2452.94 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 1023.45 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 17074.03 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 3573.32 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 5341.29 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 125.73 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 5504.1 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 2328.87 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3610.18 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 303.06 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5605.7 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3030.61 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4090.16 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 684.75 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2820.27 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1988.31 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4140.53 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2423.22 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2094.87 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 384.4 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 384.4 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 384.4 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 400.91 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 400.91 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 399.67 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 915.17 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 489.7 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 937.53 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1120.9 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5664.39 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 869.95 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 7243.45 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1833.96 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1258.07 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1325.94 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 91.86 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 192.12 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 229.59 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 776.2 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6601.53 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1637.55 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 411.97 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 4625.81 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 224.92 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 985.5 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 516.22 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 959.63 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 726.8 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5003.77 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1295.46 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3598.41 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 975.24 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 19300.84 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2721.16 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 452.06 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 10279.5 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3189.86 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 566.77 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 341.12 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 267.64 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2344.71 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 13367.24 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9855.17 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 634.57 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5941.66 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2158.69 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1194.94 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2274.72 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 957.19 | 1
AHU-1_HEATC | Coil:Heating:Water | 41392.26 | -
AHU-2_HEATC | Coil:Heating:Water | 86813.94 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.59 | 29609.9 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.67 | 26546.08 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 1103.95 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 185927.0998 | 301.1594 | 431.9483 | 0 | 0.0032 | 283798.6017 | 77004.6383
February | 159398.8201 | 261.1935 | 380.0983 | 0 | 0.0028 | 249746.399 | 66304.6569
March | 159214.3569 | 263.1012 | 386.8546 | 0 | 0.0029 | 254195.8921 | 66439.174
April | 143808.457 | 237.4235 | 348.707 | 0 | 0.0026 | 229128.7196 | 59989.4036
May | 147968.7899 | 245.3575 | 362.2642 | 0 | 0.0027 | 238041.7701 | 61826.7202
June | 157217.5324 | 264.4951 | 397.286 | 0 | 0.0029 | 261071.5313 | 66054.5615
July | 167359.0155 | 282.857 | 427.1476 | 0 | 0.0032 | 280700.356 | 70439.7785
August | 172161.9701 | 291.6926 | 441.744 | 0 | 0.0033 | 290295.4975 | 72529.926
September | 140415.0663 | 232.2271 | 341.8006 | 0 | 0.0025 | 224592.5251 | 58612.6638
October | 142372.4054 | 234.0077 | 341.8224 | 0 | 0.0026 | 224600.2561 | 59290.4776
November | 146657.5257 | 241.1416 | 352.406 | 0 | 0.0026 | 231554.7558 | 61083.671
December | 174680.8423 | 285.908 | 415.4751 | 0 | 0.0031 | 272989.4508 | 72630.2299
Annual Sum or Average | 1897180 | 3140.5644 | 4627.5542 | 0 | 0.0345 | 3040720 | 792205.9013
Minimum of Months | 140415.0663 | 232.2271 | 341.8006 | 0 | 0.0025 | 224592.5251 | 58612.6638
Maximum of Months | 185927.0998 | 301.1594 | 441.744 | 0 | 0.0033 | 290295.4975 | 77004.6383
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 658533000000 | 390080.3 | 09-JAN-07:10 | 58033.2 | 96785.431 | 32567.321 | 108174.973 | 0 | 2025 | 1112.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 579518000000 | 365686.399 | 07-FEB-08:09 | 58033.2 | 108826.64 | 32653.756 | 75280.059 | 0 | 0 | 1112.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 589842000000 | 356202.768 | 06-MAR-07:10 | 58033.2 | 96785.431 | 32567.442 | 85643.513 | 0 | 0 | 1112.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 531676000000 | 366063.466 | 06-APR-15:00 | 58033.2 | 120867.849 | 33719.817 | 3054.042 | 64424.877 | 0 | 1112.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 552358000000 | 389398.2 | 31-MAY-12:09 | 58033.2 | 120867.849 | 34815.377 | 979.799 | 173589.952 | 0 | 1112.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 605797000000 | 423104.23 | 29-JUN-14:00 | 58033.2 | 120867.849 | 36873.383 | 306.453 | 205911.324 | 0 | 1112.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 651344000000 | 422259.812 | 13-JUL-16:00 | 58033.2 | 120867.849 | 36251.94 | 344.523 | 205650.279 | 0 | 1112.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 673609000000 | 421995.642 | 25-AUG-16:00 | 58033.2 | 120867.849 | 36909.093 | 321.815 | 204751.664 | 0 | 1112.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 521150000000 | 391051.177 | 14-SEP-14:00 | 58033.2 | 120867.849 | 36259.605 | 664.754 | 174113.748 | 0 | 1112.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 521168000000 | 360264.501 | 25-OCT-12:00 | 58033.2 | 120867.849 | 33413.59 | 7990.223 | 45407.777 | 0 | 1112.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 537305000000 | 369298.333 | 01-NOV-14:00 | 58033.2 | 120867.849 | 33332.237 | 6705.828 | 49247.198 | 0 | 1112.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 633451000000 | 363312.356 | 20-DEC-07:10 | 58033.2 | 96785.431 | 32663.43 | 82364.594 | 0 | 2025 | 1112.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 7055750000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 521150000000 | 356202.768 |  | 58033.2 | 96785.431 | 32567.321 | 306.453 | 0 | 0 | 1112.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 673609000000 | 423104.23 |  | 58033.2 | 120867.849 | 36909.093 | 108174.973 | 205911.324 | 2025 | 1112.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 104967.16 | 53844.58 | 0 | 158811.74
Cost per Total Building Area ($/m2) | 27.59 | 14.15 | 0 | 41.75
Cost per Net Conditioned Building Area ($/m2) | 27.59 | 14.15 | 0 | 41.75

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 13361.18 | 3512.39 | 3512.39
Net Site Energy | 13361.18 | 3512.39 | 3512.39
Total Source Energy | 31623.45 | 8313.19 | 8313.19
Net Source Energy | 31623.45 | 8313.19 | 8313.19
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 511.93 | 5969.31 | 0 | 0 | 0 | 0
Cooling | 752.04 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 879.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 31.78 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1092.32 | 0 | 0 | 0 | 0 | 0
Pumps | 33.37 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 1857.76 | 0 | 0 | 0 | 0 | 691.09
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 58.76 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7144.73 | 6216.45 | 0 | 0 | 0 | 931.57
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 22.6 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 14 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 19.4 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 7.53 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 7.53 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 10.8 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 22.6 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 22.6 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 10.8 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 75.3 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 24.7 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 17.2 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 10.8 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 24.7 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 19.4 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 24.7 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 8.61 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 10.8 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 8.61 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 8.61 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 10.8 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 8.61 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 19.4 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 17.2 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 19.4 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 10.8 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 10.8 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 19.4 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 22.6 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 8.61 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 8.61 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 7.53 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 19.4 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 17.2 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 19.4 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 19.4 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 19.4 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 8.61 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 8.61 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 8.61 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 8.61 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.409 | 0.435 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 2.956 | 0.385 | 0.305 | No | 5F762C | 180 | S
4A8120 | WINDOW-NONRES-FIXED | 2.32 | 2.32 | 2.956 | 0.385 | 0.305 | No | 84FB73 | 0 | N
AAE778 | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 2.956 | 0.385 | 0.305 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | F629C1 | 0 | N
8128A9 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | F629C1 | 0 | N
9B1541 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 879583 | 180 | S
CF850A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 879583 | 180 | S
A6BA23 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | E326E4 | 90 | E
D10D28 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | E326E4 | 90 | E
38B811 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
591336 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 1D96D7 | 90 | E
18748E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 6D2616 | 0 | N
1D94BE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 6D2616 | 0 | N
137A56 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.385 | 0.305 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 28B002 | 180 | S
44E54A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 28B002 | 180 | S
8D508E | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 28B002 | 180 | S
B2D381 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 28B002 | 180 | S
757D10 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 2.956 | 0.385 | 0.305 | No | EA6DC8 | 180 | S
24167A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 997723 | 180 | S
2C0938 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 997723 | 180 | S
E33BAE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | B40F89 | 270 | W
8600DD | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | CEC7BD | 180 | S
88E1FC | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 859BC1 | 0 | N
E8D997 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 859BC1 | 0 | N
F83F33 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.385 | 0.305 | No | 61E610 | 90 | E
B1F5EE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | D95F04 | 90 | E
F52F3D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 208CCF | 90 | E
80885D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 2.956 | 0.385 | 0.305 | No | AEF992 | 180 | S
2BE8DE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 1775A6 | 270 | W
513E2A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 54D065 | 180 | S
1AD478 | WINDOW-NONRES-FIXED | 3.72 | 3.72 | 2.956 | 0.385 | 0.305 | No | 97F00A | 180 | S
27F0AC | WINDOW-NONRES-FIXED | 5.95 | 5.95 | 2.956 | 0.385 | 0.305 | No | A497E9 | 180 | S
724114 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 88A75F | 180 | S
5635BC | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.385 | 0.305 | No | B4E619 | 90 | E
D538C4 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.385 | 0.305 | No | B4E619 | 90 | E
831C1D | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 2.956 | 0.385 | 0.305 | No | 9EC269 | 0 | N
9BB95F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | B316F7 | 0 | N
C0778D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | B316F7 | 0 | N
2EF63B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 9621FD | 0 | N
7D2D69 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 9621FD | 0 | N
C417C0 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 4B1439 | 90 | E
D23C8B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 4B1439 | 90 | E
EB042B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 4B1439 | 90 | E
E55A57 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 2.956 | 0.385 | 0.305 | No | 4ABC66 | 180 | S
93D018 | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 2.956 | 0.385 | 0.305 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | 4B55FA | 90 | E
15B02B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
820282 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 68A2D7 | 0 | N
A2790A | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 2.956 | 0.385 | 0.305 | No | CE3FEF | 0 | N
79FCEE | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.385 | 0.305 | No | CE618F | 90 | E
EDE617 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.385 | 0.305 | No | CE618F | 90 | E
29FA28 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
944FCE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C41399 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.385 | 0.305 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.385 | 0.305 | No | C1BC97 | 180 | S
3DB407 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.385 | 0.305 | No | C1BC97 | 180 | S
5031C8 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.385 | 0.305 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.385 | 0.305 | No | C1BC97 | 180 | S
95BA33 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.385 | 0.305 | No | D22917 | 90 | E
F27282 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.385 | 0.305 | No | D22917 | 90 | E
9DF7DE | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.385 | 0.305 | No | 38B339 | 270 | W
D0BE44 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.385 | 0.305 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.385 | 0.305 | No | 38B339 | 270 | W
B0FB49 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 2.956 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.385 | 0.305 | No | 8DA7DB | 180 | S
44F571 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 2.956 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 2.956 | 0.385 | 0.305 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 2.956 | 0.385 | 0.305 | No | BE5F2F | 270 | W
3833A2 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | C86329 | 90 | E
6BD844 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | C86329 | 90 | E
86D536 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | C86329 | 90 | E
BAF71D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.385 | 0.305 | No | C86329 | 90 | E
142781 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.385 | 0.305 | No | 88E360 | 0 | N
9BC521 | WINDOW-NONRES-FIXED | 5.71 | 5.71 | 2.956 | 0.385 | 0.305 | No | 88E360 | 0 | N
2111A1 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 2.956 | 0.385 | 0.305 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
E74902 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.385 | 0.305 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-NONRES-FIXED | 1.11 | 1.11 | 2.956 | 0.385 | 0.305 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 97.22 | 2.96 | 0.385 | 0.305
Non-North Total or Average |  |  | 211.08 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 190681.84 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 316315.61 | 250858.61 | 65457 | 0.79 | 3.05
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 274499.81 | 219230.72 | 55269.09 | 0.8 | 3.07
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2177.97 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 127.98 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 12472.9 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1679.14 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2169.84 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1103.49 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2100.11 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1951.15 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148571.13 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 487.12 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 377.44 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 986.35 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 12381.47 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 617.66 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1296.33 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9785.86 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1282.29 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 5002.38 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2131.47 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 389.31 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 69768.35 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1249.2 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 2811.3 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2750.03 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1282.29 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 123.89 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3879.93 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1075.43 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 4000.34 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 39820.18 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 40387.25 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35333.51 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 2070.86 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1363.41 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2287.44 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4038.85 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1245.08 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 8513.88 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 6604.58 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 338.55 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 12603.17 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1675.51 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 226.57 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2509.35 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1115.26 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 3584.78 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 8226.96 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2156.02 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 830.68 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 16904.54 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 3482.09 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 5252.68 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 97.41 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 5385.7 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 2265.24 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3339.06 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 300.55 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5113.57 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2946.05 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3975.59 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 635.24 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2442.56 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1755.73 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3949.41 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2147.52 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1995.05 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 344.1 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 344.1 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 344.1 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 358.68 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 358.68 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 357.19 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 885.98 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 490 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 938.01 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1121.5 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4894.28 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 815.05 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 6818 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1951.14 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1260.03 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1328.02 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 91.65 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 192.22 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 229.78 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 754.2 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6357.38 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1603.84 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 403.01 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 4630.35 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 211.08 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1003.16 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 482.78 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 936.8 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 727.97 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4811.14 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1228.23 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3241.5 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 862.88 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 18380.17 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2267.96 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 448.3 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9724.44 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3191.58 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 506.48 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 305.14 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 237.94 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2346.14 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 12808.73 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9327.06 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 549.95 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 5040.23 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2244.29 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1285.12 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2377.48 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1023.29 | 1
AHU-1_HEATC | Coil:Heating:Water | 33785.14 | -
AHU-2_HEATC | Coil:Heating:Water | 79896.01 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 18.82 | 31677.56 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.58 | 27914.4 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 1049.98 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 190625.4933 | 308.8324 | 491.9903 | 0 | 0.0035 | 11667500 | 79102.7684
February | 163840.1914 | 265.4954 | 423.0687 | 0 | 0.003 | 10033000 | 67993.4173
March | 181985.6234 | 299.3456 | 486.0043 | 0 | 0.0034 | 11526300 | 75953.5486
April | 163085.4044 | 267.3076 | 432.0966 | 0 | 0.003 | 10247700 | 67973.5807
May | 157507.8889 | 257.1342 | 413.5886 | 0 | 0.0029 | 9808540 | 65549.18
June | 155724.4664 | 255.6279 | 413.9874 | 0 | 0.0029 | 9818240 | 64942.8106
July | 160860.9513 | 264.6526 | 429.7871 | 0 | 0.003 | 10193000 | 67142.2352
August | 156996.7558 | 257.6557 | 417.1503 | 0 | 0.0029 | 9893240 | 65467.5365
September | 152885.4444 | 250.0817 | 403.2365 | 0 | 0.0028 | 9563120 | 63673.2097
October | 169759.0659 | 278.6541 | 451.254 | 0 | 0.0032 | 10702100 | 70794.5811
November | 169606.2663 | 278.1683 | 449.9981 | 0 | 0.0032 | 10672200 | 70708.1474
December | 187870.6441 | 305.44 | 488.7524 | 0 | 0.0035 | 11590900 | 78063.1001
Annual Sum or Average | 2010750 | 3288.3953 | 5300.9142 | 0 | 0.0374 | 125716000 | 837364.1156
Minimum of Months | 152885.4444 | 250.0817 | 403.2365 | 0 | 0.0028 | 9563120 | 63673.2097
Maximum of Months | 190625.4933 | 308.8324 | 491.9903 | 0 | 0.0035 | 11667500 | 79102.7684
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 663092000000 | 393193.9 | 17-JAN-07:10 | 58033.2 | 96785.431 | 34774.783 | 103238.004 | 0 | 2025 | 1058.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 570201000000 | 393558.186 | 27-FEB-07:10 | 58033.2 | 96785.431 | 34774.783 | 100881.726 | 0 | 2025 | 1058.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 655068000000 | 380183.268 | 27-MAR-13:20 | 58033.2 | 120867.849 | 35478.174 | 6168.952 | 58577.048 | 0 | 1058.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 582399000000 | 380702.215 | 14-APR-14:30 | 58033.2 | 120867.849 | 36359.842 | 3686.728 | 60696.551 | 0 | 1058.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 557443000000 | 380002.38 | 15-MAY-12:09 | 58033.2 | 120867.849 | 35035.165 | 6102.817 | 58905.304 | 0 | 1058.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 557994000000 | 392811.931 | 30-JUN-15:00 | 58033.2 | 120867.849 | 39985.675 | 148.054 | 153919.521 | 0 | 1058.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 579295000000 | 389997.006 | 21-JUL-16:00 | 58033.2 | 120867.849 | 41936.163 | 137.735 | 153067.882 | 0 | 1058.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 562256000000 | 378178.52 | 18-AUG-16:00 | 58033.2 | 120867.849 | 40295.772 | 303.072 | 128896.811 | 0 | 1058.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 543495000000 | 373224.223 | 14-SEP-13:00 | 58033.2 | 120867.849 | 36982.26 | 3249.36 | 53033.509 | 0 | 1058.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 608224000000 | 381472.74 | 19-OCT-13:09 | 58033.2 | 120867.849 | 36008.092 | 5951.02 | 59554.534 | 0 | 1058.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 606529000000 | 360301.423 | 21-NOV-10:00 | 58033.2 | 120867.849 | 35022.345 | 9539.838 | 35780.145 | 0 | 1058.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 658738000000 | 407318.004 | 11-DEC-07:10 | 58033.2 | 96785.431 | 34774.783 | 114641.544 | 0 | 2025 | 1058.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 7144730000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 543495000000 | 360301.423 |  | 58033.2 | 96785.431 | 34774.783 | 137.735 | 0 | 0 | 1058.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 663092000000 | 407318.004 |  | 58033.2 | 120867.849 | 41936.163 | 114641.544 | 153919.521 | 2025 | 1058.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 139140.7 | 55147.21 | 0 | 194287.91
Cost per Total Building Area ($/m2) | 36.58 | 14.5 | 0 | 51.07
Cost per Net Conditioned Building Area ($/m2) | 36.58 | 14.5 | 0 | 51.07

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 13603.36 | 3576.06 | 3576.06
Net Site Energy | 13603.36 | 3576.06 | 3576.06
Total Source Energy | 30694.81 | 8069.07 | 8069.07
Net Source Energy | 30694.81 | 8069.07 | 8069.07
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 631.88 | 6596.75 | 0 | 0 | 0 | 0
Cooling | 729.43 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 879.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 31.77 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1013.27 | 0 | 0 | 0 | 0 | 0
Pumps | 35.19 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 1447.71 | 0 | 0 | 0 | 0 | 538.55
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 63.47 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6754.77 | 6848.59 | 0 | 0 | 0 | 779.03
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 22.6 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 14 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 19.4 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 7.53 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 7.53 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 10.8 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 22.6 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 22.6 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 10.8 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 75.3 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 24.7 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 17.2 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 10.8 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 24.7 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 19.4 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 24.7 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 8.61 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 10.8 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 8.61 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 8.61 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 10.8 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 8.61 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 19.4 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 17.2 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 19.4 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 10.8 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 10.8 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 19.4 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 22.6 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 8.61 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 8.61 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 7.53 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 19.4 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 17.2 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 19.4 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 19.4 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 19.4 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 8.61 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 8.61 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 8.61 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 8.61 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.329 | 0.346 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 2.956 | 0.487 | 0.409 | No | 5F762C | 180 | S
4A8120 | WINDOW-NONRES-FIXED | 2.32 | 2.32 | 2.956 | 0.487 | 0.409 | No | 84FB73 | 0 | N
AAE778 | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 2.956 | 0.487 | 0.409 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | F629C1 | 0 | N
8128A9 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | F629C1 | 0 | N
9B1541 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 879583 | 180 | S
CF850A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 879583 | 180 | S
A6BA23 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | E326E4 | 90 | E
D10D28 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | E326E4 | 90 | E
38B811 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 1D96D7 | 90 | E
591336 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 1D96D7 | 90 | E
18748E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 6D2616 | 0 | N
1D94BE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 6D2616 | 0 | N
137A56 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.487 | 0.409 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 28B002 | 180 | S
44E54A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 28B002 | 180 | S
8D508E | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 28B002 | 180 | S
B2D381 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 28B002 | 180 | S
757D10 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 2.956 | 0.487 | 0.409 | No | EA6DC8 | 180 | S
24167A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 997723 | 180 | S
2C0938 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 997723 | 180 | S
E33BAE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | B40F89 | 270 | W
8600DD | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | CEC7BD | 180 | S
88E1FC | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 859BC1 | 0 | N
E8D997 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 859BC1 | 0 | N
F83F33 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.487 | 0.409 | No | 61E610 | 90 | E
B1F5EE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | D95F04 | 90 | E
F52F3D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 208CCF | 90 | E
80885D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 2.956 | 0.487 | 0.409 | No | AEF992 | 180 | S
2BE8DE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 1775A6 | 270 | W
513E2A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 54D065 | 180 | S
1AD478 | WINDOW-NONRES-FIXED | 3.72 | 3.72 | 2.956 | 0.487 | 0.409 | No | 97F00A | 180 | S
27F0AC | WINDOW-NONRES-FIXED | 5.95 | 5.95 | 2.956 | 0.487 | 0.409 | No | A497E9 | 180 | S
724114 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 88A75F | 180 | S
5635BC | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.487 | 0.409 | No | B4E619 | 90 | E
D538C4 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.487 | 0.409 | No | B4E619 | 90 | E
831C1D | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 2.956 | 0.487 | 0.409 | No | 9EC269 | 0 | N
9BB95F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | B316F7 | 0 | N
C0778D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | B316F7 | 0 | N
2EF63B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 9621FD | 0 | N
7D2D69 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 9621FD | 0 | N
C417C0 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 4B1439 | 90 | E
D23C8B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 4B1439 | 90 | E
EB042B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 4B1439 | 90 | E
E55A57 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.487 | 0.409 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 2.956 | 0.487 | 0.409 | No | 4ABC66 | 180 | S
93D018 | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 2.956 | 0.487 | 0.409 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | 4B55FA | 90 | E
15B02B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 9C3A6A | 0 | N
820282 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 68A2D7 | 0 | N
A2790A | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 2.956 | 0.487 | 0.409 | No | CE3FEF | 0 | N
79FCEE | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.487 | 0.409 | No | CE618F | 90 | E
EDE617 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.487 | 0.409 | No | CE618F | 90 | E
29FA28 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 5ADC59 | 0 | N
944FCE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 5ADC59 | 0 | N
C41399 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.487 | 0.409 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.487 | 0.409 | No | C1BC97 | 180 | S
3DB407 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.487 | 0.409 | No | C1BC97 | 180 | S
5031C8 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.487 | 0.409 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.487 | 0.409 | No | C1BC97 | 180 | S
95BA33 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.487 | 0.409 | No | D22917 | 90 | E
F27282 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.487 | 0.409 | No | D22917 | 90 | E
9DF7DE | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.487 | 0.409 | No | 38B339 | 270 | W
D0BE44 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.487 | 0.409 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.487 | 0.409 | No | 38B339 | 270 | W
B0FB49 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 2.956 | 0.487 | 0.409 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.487 | 0.409 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.487 | 0.409 | No | 8DA7DB | 180 | S
44F571 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 2.956 | 0.487 | 0.409 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 2.956 | 0.487 | 0.409 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 2.956 | 0.487 | 0.409 | No | BE5F2F | 270 | W
3833A2 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | C86329 | 90 | E
6BD844 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | C86329 | 90 | E
86D536 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | C86329 | 90 | E
BAF71D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.487 | 0.409 | No | C86329 | 90 | E
142781 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.487 | 0.409 | No | 88E360 | 0 | N
9BC521 | WINDOW-NONRES-FIXED | 5.71 | 5.71 | 2.956 | 0.487 | 0.409 | No | 88E360 | 0 | N
2111A1 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 2.956 | 0.487 | 0.409 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.487 | 0.409 | No | 2E2D0C | 0 | N
E74902 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.487 | 0.409 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-NONRES-FIXED | 1.11 | 1.11 | 2.956 | 0.487 | 0.409 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 2.96 | 0.487 | 0.409
North Total or Average |  |  | 97.22 | 2.96 | 0.487 | 0.409
Non-North Total or Average |  |  | 211.08 | 2.96 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 201203.79 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 361002.46 | 261615.67 | 99386.79 | 0.72 | 2.85
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 289918.31 | 218116.19 | 71802.13 | 0.75 | 2.93
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 2328.47 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 113.98 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 13368.14 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1648.98 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 2130.19 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 1062.14 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2251.91 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1875.69 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148633.3 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 468.83 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 342.63 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 949.21 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 13506.93 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 558.48 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1356.86 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9724.23 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1159.8 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 4912.11 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2198.95 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 352.85 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 69646.23 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1312.64 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 2966.7 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2703.32 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1159.8 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 110.39 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3811.86 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1178 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3863.71 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 40380.77 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 41553.13 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 35153.08 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 2044.2 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1232.97 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2473.82 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4424.07 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1309.87 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9325.92 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 6813.6 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 306.81 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 13279.44 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 1767.78 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 205.68 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2748.69 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1221.63 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 3926.69 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 8526.32 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2150.16 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 777.49 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 17554.72 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 3706.98 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 5545.47 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 86.93 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 5714.66 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 2434.85 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 3662.3 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 302.94 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5682.18 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3085.57 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 4211.64 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 744.37 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2816.7 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1828.87 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3993.83 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2244.71 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2021.44 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 369.66 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 369.66 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 369.66 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 380.82 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 380.82 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 379.59 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 941.73 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 489.96 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 937.98 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1121.47 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 5673.54 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 848.17 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 7372.96 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1785.1 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1260.01 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1328.01 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 92.22 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 193.47 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 231.33 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 802.17 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6404.49 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1626.61 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 420.98 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 4630.2 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 221.48 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 979.96 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 508.44 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 984.52 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 721.06 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4720.89 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1275.91 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 3661.57 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 892.34 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 17812.97 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2371.92 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 459.63 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 10832.5 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3078.18 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 554.91 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 313.27 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 244.18 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2254.58 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 13228.79 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 9528.87 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 574.93 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6014.91 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2183.74 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1164.65 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2290.3 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 941.36 | 1
AHU-1_HEATC | Coil:Heating:Water | 45815.27 | -
AHU-2_HEATC | Coil:Heating:Water | 89615.73 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17.42 | 29325.68 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 15.31 | 25935.37 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 1107.91 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 186042.599 | 302.0778 | 434.5978 | 0 | 0.0033 | 285542.8309 | 77122.3741
February | 162893.0094 | 265.296 | 383.1454 | 0 | 0.0029 | 251740.994 | 67602.9777
March | 168251.5996 | 277.7604 | 407.9182 | 0 | 0.003 | 268035.2167 | 70184.0923
April | 144883.4312 | 239.7909 | 353.2432 | 0 | 0.0026 | 232112.0777 | 60494.4721
May | 141284.7001 | 233.3164 | 342.7813 | 0 | 0.0026 | 225235.3396 | 58942.3166
June | 136799.0912 | 226.7333 | 334.5827 | 0 | 0.0025 | 219851.9261 | 57149.7712
July | 152527.0574 | 255.5769 | 382.0887 | 0 | 0.0028 | 251080.2894 | 63985.6866
August | 146437.5389 | 244.0428 | 362.5019 | 0 | 0.0027 | 238203.4721 | 61303.9365
September | 125346.1903 | 204.932 | 297.3921 | 0 | 0.0022 | 195401.5419 | 52095.6995
October | 143623.3603 | 237.0511 | 348.0404 | 0 | 0.0026 | 228690.4277 | 59905.7989
November | 152259.7825 | 250.4001 | 366.0208 | 0 | 0.0027 | 240500.837 | 63421.5351
December | 177109.3158 | 288.8696 | 417.952 | 0 | 0.0031 | 274612.2319 | 73543.112
Annual Sum or Average | 1837460 | 3025.8474 | 4430.2645 | 0 | 0.033 | 2911010 | 765751.7724
Minimum of Months | 125346.1903 | 204.932 | 297.3921 | 0 | 0.0022 | 195401.5419 | 52095.6995
Maximum of Months | 186042.599 | 302.0778 | 434.5978 | 0 | 0.0033 | 285542.8309 | 77122.3741
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 662581000000 | 404779.735 | 09-JAN-07:10 | 58033.2 | 96785.431 | 32314.63 | 120173.834 | 0 | 2025 | 1115.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 584146000000 | 387062.947 | 02-FEB-07:10 | 58033.2 | 96785.431 | 32386.429 | 101940.169 | 0 | 2025 | 1115.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 621956000000 | 360907.346 | 27-MAR-06:10 | 58033.2 | 96785.431 | 32314.741 | 84110.684 | 0 | 0 | 1115.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 538599000000 | 355268.795 | 04-APR-16:00 | 58033.2 | 120867.849 | 33621.212 | 3614.15 | 53667.375 | 0 | 1115.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 522642000000 | 381538.741 | 30-MAY-10:30 | 58033.2 | 120867.849 | 32470.16 | 9029.956 | 60021.594 | 0 | 1115.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 510150000000 | 382021.142 | 14-JUN-15:09 | 58033.2 | 120867.849 | 35953.985 | 688.662 | 165361.463 | 0 | 1115.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 582613000000 | 394416.139 | 06-JUL-16:00 | 58033.2 | 120867.849 | 37306.781 | 389.035 | 176703.291 | 0 | 1115.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 552733000000 | 387749.993 | 11-AUG-14:00 | 58033.2 | 120867.849 | 36508.946 | 653.474 | 170570.54 | 0 | 1115.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 453415000000 | 371071.872 | 07-SEP-14:00 | 58033.2 | 120867.849 | 35831.382 | 1384.179 | 153839.279 | 0 | 1115.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 530659000000 | 358418.896 | 20-OCT-14:00 | 58033.2 | 120867.849 | 34271.55 | 5229.719 | 53765.425 | 0 | 1115.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 558064000000 | 360230.246 | 24-NOV-07:10 | 58033.2 | 96785.431 | 32316.371 | 83874.694 | 0 | 2025 | 1115.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 637217000000 | 369823.599 | 21-DEC-08:09 | 58033.2 | 108826.64 | 32460.344 | 78825.299 | 0 | 0 | 1115.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 6754770000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 453415000000 | 355268.795 |  | 58033.2 | 96785.431 | 32314.63 | 389.035 | 0 | 0 | 1115.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 662581000000 | 404779.735 |  | 58033.2 | 120867.849 | 37306.781 | 120173.834 | 176703.291 | 2025 | 1115.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 100998.08 | 54804.6 | 0 | 155802.68
Cost per Total Building Area ($/m2) | 26.55 | 14.41 | 0 | 40.96
Cost per Net Conditioned Building Area ($/m2) | 26.55 | 14.41 | 0 | 40.96

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 15571.81 | 4093.53 | 4093.53
Net Site Energy | 15571.81 | 4093.53 | 4093.53
Total Source Energy | 34890.86 | 9172.13 | 9172.13
Net Source Energy | 34890.86 | 9172.13 | 9172.13
Area [m2]
Total Building Area | 3804.01
Net Conditioned Building Area | 3804.01
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 964.71 | 8101.31 | 0 | 0 | 0 | 0
Cooling | 447.91 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 879.76 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 31.57 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 1985.76 | 188.37 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 995.16 | 0 | 0 | 0 | 0 | 0
Pumps | 39.76 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 1867.64 | 0 | 0 | 0 | 0 | 694.76
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 69.86 | 0 | 0 | 0 | 240.48
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7212.27 | 8359.54 | 0 | 0 | 0 | 935.24
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
FLOOR 1 ANESTHESIA | 10.03 | Yes | 30.58 | 1 | 8.36 | 2.23 | 22.6 |  | 21.53
FLOOR 1 BIO HAZ | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 CAFE | 39.02 | Yes | 118.93 | 1 | 18.58 | 8.92 | 14 | 1 | 10.76
FLOOR 1 CLEAN | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 CLEAN WORK | 15.33 | Yes | 46.72 | 1 | 0 | 0 | 14 | 5 | 21.53
FLOOR 1 DICTATION | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 DRESSING ROOM | 4.18 | Yes | 12.74 | 1 | 8.36 | 2.32 | 19.4 | 20 | 11.84
FLOOR 1 ELECTRICAL ROOM | 9.1 | Yes | 27.75 | 1 | 6.5 | 0 | 7.53 |  | 53.82
FLOOR 1 ELEVATOR PUMP ROOM | 8.45 | Yes | 25.77 | 1 | 18.58 | 0 | 7.53 |  | 5750.9845
FLOOR 1 HUMID | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 IT HALL | 13.01 | Yes | 39.64 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 IT ROOM | 10.41 | Yes | 31.71 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 LOBBY | 57.79 | Yes | 176.13 | 1 | 20.44 | 8.92 | 10.8 | 3.33 | 11.84
FLOOR 1 LOBBY HALL | 22.3 | Yes | 67.96 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOBBY TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 LOCKER ROOM | 61.32 | Yes | 186.89 | 1 | 20.44 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 1 LOCKER ROOM HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 LOUNGE | 33.45 | Yes | 101.94 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 1 MRI CONTROL ROOM | 15.61 | Yes | 47.57 | 1 | 4.65 | 0 | 22.6 | 5 | 11.84
FLOOR 1 MRI HALL | 13.66 | Yes | 41.63 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 MRI ROOM | 40.88 | Yes | 124.59 | 1 | 0 | 0 | 22.6 | 5 | 573.5623
FLOOR 1 MRI TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 MED GAS | 5.2 | Yes | 15.86 | 1 | 13.94 | 0 | 10.8 |  | 1.08
FLOOR 1 NOURISHMENT | 16.91 | Yes | 51.54 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE HALL | 46.08 | Yes | 140.45 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 NURSE JANITOR | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 NURSE STATION | 24.25 | Yes | 73.91 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 1 NURSE TOILET | 5.02 | Yes | 15.29 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 OFFICE | 44.87 | Yes | 136.77 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 1 OPERATING ROOM 1 | 42.74 | Yes | 130.26 | 1 | 39.95 | 8.92 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 2 | 44.59 | Yes | 135.92 | 1 | 22.3 | 6.69 | 75.3 | 5 | 118.36
FLOOR 1 OPERATING ROOM 3 | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 75.3 | 5 | 118.36
FLOOR 1 PACU | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 24.7 | 5 | 32.29
FLOOR 1 PRE-OP HALL | 49.05 | Yes | 149.51 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 PRE-OP ROOM 1 | 17.56 | Yes | 53.52 | 1 | 3.72 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP ROOM 2 | 31.4 | Yes | 95.71 | 1 | 0 | 0 | 15.1 | 10 | 21.53
FLOOR 1 PRE-OP TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 1 PROCEDURE ROOM | 26.48 | Yes | 80.7 | 1 | 17.65 | 5.57 | 17.2 | 5 | 32.29
FLOOR 1 RECEPTION | 47.29 | Yes | 144.13 | 1 | 12.08 | 3.34 | 10.8 | 3.33 | 11.84
FLOOR 1 RECEPTION HALL | 11.89 | Yes | 36.25 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 RECOVERY ROOM | 50.17 | Yes | 152.91 | 1 | 41.81 | 8.92 | 24.7 | 5 | 32.29
FLOOR 1 SCHEDULING | 11.06 | Yes | 33.7 | 1 | 6.5 | 0.74 | 19.4 | 20 | 11.84
FLOOR 1 SCRUB | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 1 SOIL | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL HOLD | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 SOIL WORK | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 9.68 | 5 | 21.53
FLOOR 1 STEP DOWN | 27.87 | Yes | 84.95 | 1 | 34.37 | 6.69 | 24.7 | 5 | 32.29
FLOOR 1 STERILE HALL | 57.23 | Yes | 174.43 | 1 | 7.43 | 2.23 | 8.61 |  | 4.31
FLOOR 1 STERILE STORAGE | 36.79 | Yes | 112.14 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 STORAGE | 85.47 | Yes | 260.51 | 1 | 58.53 | 8.36 | 10.8 |  | 1.08
FLOOR 1 SUB-STERILE | 18.21 | Yes | 55.5 | 1 | 13.01 | 2.97 | 8.61 |  | 4.31
FLOOR 1 UTILITY HALL | 23.78 | Yes | 72.49 | 1 | 14.86 | 0 | 8.61 |  | 4.31
FLOOR 1 UTILITY JANITOR | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 1 UTILITY ROOM | 33.45 | Yes | 101.94 | 1 | 16.72 | 2.23 | 10.8 |  | 1.08
FLOOR 1 VESTIBULE | 6.69 | Yes | 20.39 | 1 | 7.43 | 0 | 8.61 |  | 4.31
FLOOR 2 CONFERENCE | 31.22 | Yes | 95.14 | 1 | 37.16 | 8.92 | 19.4 | 2 | 10.76
FLOOR 2 CONFERENCE TOILET | 5.95 | Yes | 18.12 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 DICTATION | 6.5 | Yes | 19.82 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 EXAM 1 | 33.45 | Yes | 101.94 | 1 | 39.02 | 8.92 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 2 | 50.17 | Yes | 152.91 | 1 | 16.72 | 3.72 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 3 | 66.89 | Yes | 203.88 | 1 | 22.3 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 4 | 7.8 | Yes | 23.79 | 1 | 6.5 | 2.23 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 5 | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 6 | 20.9 | Yes | 63.71 | 1 | 13.94 | 4.18 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 7 | 73.58 | Yes | 224.27 | 1 | 22.3 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 8 | 25.08 | Yes | 76.46 | 1 | 16.72 | 5.57 | 17.2 | 5 | 11.84
FLOOR 2 EXAM 9 | 36.79 | Yes | 112.14 | 1 | 11.15 | 2.79 | 17.2 | 5 | 11.84
FLOOR 2 EXAM HALL 1 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 2 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 3 | 16.72 | Yes | 50.97 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 4 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 5 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 EXAM HALL 6 | 18.39 | Yes | 56.07 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 2 LOUNGE | 7.43 | Yes | 22.65 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 2 NURSE STATION 1 | 13.94 | Yes | 42.48 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 NURSE STATION 2 | 16.72 | Yes | 50.97 | 1 | 0 | 0 | 22.6 | 5 | 21.53
FLOOR 2 OFFICE | 52.03 | Yes | 158.57 | 1 | 37.16 | 8.92 | 19.4 | 20 | 11.84
FLOOR 2 OFFICE HALL | 41.25 | Yes | 125.73 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION | 91.42 | Yes | 278.64 | 1 | 45.52 | 16.72 | 10.8 | 3.33 | 11.84
FLOOR 2 RECEPTION HALL | 52.4 | Yes | 159.71 | 1 | 87.33 | 0 | 8.61 |  | 4.31
FLOOR 2 RECEPTION TOILET | 11.71 | Yes | 35.68 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 2 SCHEDULING 1 | 30.1 | Yes | 91.75 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 SCHEDULING 2 | 31.77 | Yes | 96.84 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 2 STORAGE 1 | 5.2 | Yes | 15.86 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 2 | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 STORAGE 3 | 13.38 | Yes | 40.78 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 2 UTILITY | 11.71 | Yes | 35.68 | 1 | 8.36 | 2.23 | 10.8 |  | 1.08
FLOOR 2 WORK | 157.01 | Yes | 478.56 | 1 | 24.15 | 5.57 | 19.4 | 20 | 11.84
FLOOR 2 WORK HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 WORK TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 2 X-RAY | 83.61 | Yes | 254.85 | 1 | 0 | 0 | 22.6 | 5 | 14.0206
FLOOR 3 DRESSING ROOM | 3.9 | Yes | 11.89 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 ELEVATOR HALL | 34.37 | Yes | 104.77 | 1 | 3.72 | 0 | 8.61 |  | 4.31
FLOOR 3 HUMID | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 19.4 | 20 | 11.84
FLOOR 3 JANITOR | 5.85 | Yes | 17.84 | 1 | 14.86 | 0 | 10.8 |  | 1.08
FLOOR 3 LOCKER | 11.15 | Yes | 33.98 | 1 | 0 | 0 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE | 70.51 | Yes | 214.93 | 1 | 21.37 | 5.57 | 9.68 | 6.67 | 32.29
FLOOR 3 LOUNGE TOILET | 17.84 | Yes | 54.37 | 1 | 11.15 | 4.18 | 8.61 |  | 4.31
FLOOR 3 MECHANICAL | 32.52 | Yes | 99.11 | 1 | 23.23 | 5.95 | 7.53 |  | 53.82
FLOOR 3 MECHANICAL HALL | 27.87 | Yes | 84.95 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE | 282.05 | Yes | 859.7 | 1 | 68.75 | 19.51 | 19.4 | 20 | 11.84
FLOOR 3 OFFICE HALL | 77.48 | Yes | 236.16 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 OFFICE TOILET | 5.02 | Yes | 15.29 | 1 | 5.57 | 0 | 8.61 |  | 4.31
FLOOR 3 PHYSICAL THERAPY 1 | 120.77 | Yes | 368.12 | 1 | 78.97 | 28.99 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY 2 | 55 | Yes | 167.64 | 1 | 0 | 0 | 17.2 | 5 | 16.15
FLOOR 3 PHYSICAL THERAPY TOILET | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 8.61 |  | 4.31
FLOOR 3 STORAGE 1 | 10.03 | Yes | 30.58 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 STORAGE 2 | 7.8 | Yes | 23.79 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 TREATMENT | 44.22 | Yes | 134.79 | 1 | 0 | 0 | 17.2 | 5 | 11.84
FLOOR 3 UNDEVELOPED 1 | 210.7 | Yes | 642.23 | 1 | 66.89 | 25.64 | 19.4 | 20 | 11.84
FLOOR 3 UNDEVELOPED 2 | 107.02 | Yes | 326.21 | 1 | 52.03 | 13.38 | 19.4 | 20 | 11.84
FLOOR 3 UTILITY | 20.07 | Yes | 61.16 | 1 | 0 | 0 | 10.8 |  | 1.08
FLOOR 3 WORK | 53.33 | Yes | 162.54 | 1 | 38.09 | 8.92 | 19.4 | 20 | 11.84
NE STAIR | 15.61 | Yes | 142.72 | 1 | 97.55 | 12.02 | 8.61 |  | 4.31
NW ELEVATOR | 13.01 | Yes | 118.93 | 1 | 75.25 | 0 | 8.61 |  | 4.31
NW STAIR | 17.84 | Yes | 163.1 | 1 | 111.48 | 11.15 | 8.61 |  | 4.31
SW STAIR | 8.92 | Yes | 81.55 | 1 | 55.74 | 1.11 | 8.61 |  | 4.31
Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Conditioned Total | 3804.01 |  | 11932.15 |  | 1634.16 | 308.29 | 16.9509 | 9.17 | 34.6367
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
4.81e+73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 8.36 | 180 | 90 | S
FLOOR 1 ANESTHESIA SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 0 | 180
FLOOR 1 BIO HAZ SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
5F762C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 18.58 | 180 | 90 | S
FLOOR 1 CAFE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 39.02 | 90 | 180
FLOOR 1 CLEAN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 CLEAN WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.33 | 180 | 180
FLOOR 1 DICTATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 0 | 180
84FB73 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 8.36 | 0 | 90 | N
FLOOR 1 DRESSING ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 4.18 | 0 | 180
7F5C82 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 6.5 | 90 | 90 | E
FLOOR 1 ELECTRICAL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 9.1 | 0 | 180
C732B0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 12.08 | 0 | 90 | N
E02487 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 6.5 | 270 | 90 | W
FLOOR 1 ELEVATOR PUMP ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.45 | 180 | 180
FLOOR 1 HUMID SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
FLOOR 1 IT HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 180 | 180
FLOOR 1 IT ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.41 | 90 | 180
FE5A3C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 20.44 | 270 | 90 | W
FLOOR 1 LOBBY SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.79 | 90 | 180
FLOOR 1 LOBBY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 22.3 | 0 | 180
9D87EC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 5.57 | 270 | 90 | W
FLOOR 1 LOBBY TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 0 | 180
F629C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 20.44 | 0 | 90 | N
FLOOR 1 LOCKER ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 61.32 | 270 | 180
FLOOR 1 LOCKER ROOM HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 180 | 180
FLOOR 1 LOUNGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
C114C1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 4.65 | 0 | 90 | N
FLOOR 1 MRI CONTROL ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 180 | 180
FLOOR 1 MRI HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.66 | 180 | 180
FLOOR 1 MRI ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 40.88 | 90 | 180
ADB8D0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 5.57 | 0 | 90 | N
FLOOR 1 MRI TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 90 | 180
577FC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 6.5 | 90 | 90 | E
E85BB5 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 7.43 | 0 | 90 | N
FLOOR 1 MED GAS SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 180 | 180
FLOOR 1 MED GAS ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 5.2 | 180 | 0
FLOOR 1 NOURISHMENT SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.91 | 270 | 180
FLOOR 1 NURSE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 46.08 | 270 | 180
FLOOR 1 NURSE JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 NURSE STATION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 24.25 | 180 | 180
FLOOR 1 NURSE TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 180 | 180
FLOOR 1 OFFICE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.87 | 0 | 180
879583 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 18.58 | 180 | 90 | S
E326E4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 21.37 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 42.74 | 0 | 180
1D96D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 22.3 | 90 | 90 | E
FLOOR 1 OPERATING ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.59 | 0 | 180
FLOOR 1 OPERATING ROOM 3 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 44.22 | 0 | 180
FLOOR 1 PACU SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 10.03 | 180 | 180
FLOOR 1 PRE-OP HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 49.05 | 180 | 180
84418A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 3.72 | 270 | 90 | W
FLOOR 1 PRE-OP ROOM 1 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.56 | 90 | 180
FLOOR 1 PRE-OP ROOM 2 SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 31.4 | 0 | 180
1535AC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 5.57 | 270 | 90 | W
FLOOR 1 PRE-OP TOILET SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.02 | 270 | 180
6D2616 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 17.65 | 0 | 90 | N
FLOOR 1 PROCEDURE ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 26.48 | 270 | 180
A5A6A3 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 12.08 | 180 | 90 | S
FLOOR 1 RECEPTION SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 47.29 | 270 | 180
FLOOR 1 RECEPTION HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.89 | 0 | 180
28B002 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 41.81 | 180 | 90 | S
FLOOR 1 RECOVERY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 50.17 | 90 | 180
EA6DC8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 6.5 | 180 | 90 | S
FLOOR 1 SCHEDULING SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.06 | 90 | 180
FLOOR 1 SCRUB SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 7.8 | 90 | 180
FLOOR 1 SOIL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 11.71 | 90 | 180
FLOOR 1 SOIL HOLD SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 5.2 | 0 | 180
FLOOR 1 SOIL WORK SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 16.72 | 0 | 180
997723 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 23.23 | 180 | 90 | S
B40F89 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 11.15 | 270 | 90 | W
FLOOR 1 STEP DOWN SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 27.87 | 270 | 180
CEC7BD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 7.43 | 180 | 90 | S
FLOOR 1 STERILE HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 57.23 | 270 | 180
FLOOR 1 NURSE STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 36.79 | 0 | 180
859BC1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 37.16 | 0 | 90 | N
8E5BB9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 21.37 | 270 | 90 | W
FLOOR 1 STORAGE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 85.47 | 270 | 180
FLOOR 1 STORGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 85.47 | 270 | 0
61E610 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 13.01 | 90 | 90 | E
FLOOR 1 SUB-STERILE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 18.21 | 180 | 180
529072 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 14.86 | 90 | 90 | E
FLOOR 1 UTILITY HALL SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 23.78 | 90 | 180
FLOOR 1 UTILITY HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 11.89 | 180 | 0
FLOOR 1 UTILITY JANITOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 3.9 | 90 | 180
D95F04 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 16.72 | 90 | 90 | E
FLOOR 1 UTILITY ROOM SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 33.45 | 180 | 180
3330D8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 7.43 | 270 | 90 | W
FLOOR 1 VESTIBULE SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 6.69 | 90 | 180
208CCF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 11.15 | 90 | 90 | E
AEF992 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 26.01 | 180 | 90 | S
1775A6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 27.87 | 270 | 90 | W
54D065 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 11.15 | 180 | 90 | S
97F00A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 16.72 | 180 | 90 | S
A497E9 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 22.3 | 180 | 90 | S
88A75F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 6.5 | 180 | 90 | S
B4E619 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 23.23 | 90 | 90 | E
9EC269 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 13.94 | 0 | 90 | N
B316F7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 22.3 | 0 | 90 | N
9621FD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 16.72 | 0 | 90 | N
42CEE1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 11.15 | 0 | 90 | N
4979C8 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 5.57 | 180 | 90 | S
8CA0BF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 5.57 | 180 | 90 | S
6C95E7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 5.57 | 180 | 90 | S
F209CC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 5.57 | 0 | 90 | N
155BD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 5.57 | 0 | 90 | N
C5EA55 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 5.57 | 0 | 90 | N
5E657E | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 8.36 | 0 | 90 | N
8177BA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 6.5 | 270 | 90 | W
4B1439 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 37.16 | 90 | 90 | E
4ABC66 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 30.66 | 180 | 90 | S
5B04CF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 14.86 | 270 | 90 | W
8D1BC4 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 87.33 | 180 | 90 | S
4B55FA | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 8.36 | 90 | 90 | E
9C3A6A | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 20.44 | 0 | 90 | N
C52EE0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 3.72 | 0 | 90 | N
1C33AD | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 5.57 | 270 | 90 | W
6CC177 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 5.57 | 270 | 90 | W
FLOOR 3 DRESSING ROOM ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 3.9 | 270 | 0
F7D24D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 3.72 | 0 | 90 | N
FLOOR 3 ELEVATOR HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 34.37 | 0 | 0
FLOOR 3 HUMID ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 10.03 | 270 | 0
DD2E2D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 6.5 | 270 | 90 | W
FC22D1 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 8.36 | 0 | 90 | N
FLOOR 3 JANITOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 5.85 | 0 | 0
FLOOR 3 LOCKER ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 11.15 | 0 | 0
68A2D7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 21.37 | 0 | 90 | N
FLOOR 3 LOUNGE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 70.51 | 270 | 0
CE3FEF | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 11.15 | 0 | 90 | N
FLOOR 3 LOUNGE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 17.84 | 0 | 0
CE618F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 23.23 | 90 | 90 | E
FLOOR 3 MECHANICAL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 32.52 | 0 | 0
FLOOR 3 MECHANICAL HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 27.87 | 0 | 0
5ADC59 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 68.75 | 0 | 90 | N
FLOOR 3 OFFICE ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 282.05 | 180 | 0
D4F411 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE HALL ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 77.48 | 0 | 0
B35AD6 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 5.57 | 270 | 90 | W
FLOOR 3 OFFICE TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 5.02 | 270 | 0
C1BC97 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 60.39 | 180 | 90 | S
D22917 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 18.58 | 90 | 90 | E
FLOOR 3 PHYICAL THERAPY 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 120.77 | 180 | 0
FLOOR 3 PHYSICAL THERAPY 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 55 | 90 | 0
FLOOR 3 PHYSICAL THERAPY TOILET ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 7.8 | 90 | 0
FLOOR 3 STORAGE 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 10.03 | 180 | 0
FLOOR 3 STORAGE 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 7.8 | 180 | 0
FLOOR 3 TREATMENT ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 44.22 | 90 | 0
38B339 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 27.87 | 270 | 90 | W
8DA7DB | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 39.02 | 180 | 90 | S
FLOOR 3 UNDEVELOPED 1 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 210.7 | 0 | 0
1DEE26 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 37.16 | 180 | 90 | S
BE5F2F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 14.86 | 270 | 90 | W
FLOOR 3 UNDEVELOPED 2 ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 107.02 | 180 | 0
FLOOR 3 UTILITY ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 20.07 | 0 | 0
C86329 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 38.09 | 90 | 90 | E
FLOOR 3 WORK ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 53.33 | 90 | 0
88E360 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 66.89 | 0 | 90 | N
DFC6F0 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 19.51 | 90 | 90 | E
E7B55F | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 11.15 | 180 | 90 | S
NE STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 15.61 | 0 | 180
NE STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 15.61 | 0 | 0
FB3814 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 19.51 | 180 | 90 | S
FCD12D | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 55.74 | 270 | 90 | W
NW ELEVATOR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 13.01 | 90 | 180
NW ELEVATOR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 13.01 | 90 | 0
2E2D0C | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 66.89 | 0 | 90 | N
5507DC | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 22.3 | 270 | 90 | W
AF0124 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 22.3 | 90 | 90 | E
NW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 17.84 | 270 | 180
NW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 17.84 | 270 | 0
270BCE | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 22.3 | 270 | 90 | W
850EA7 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.256 | 0.266 | 33.45 | 180 | 90 | S
SW STAIR SLAB | EXT-SLAB | 0.3 | 1.627 | 2.692 | 8.92 | 270 | 180
SW STAIR ROOF | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 8.92 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
78F987 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 4.81e+73 | 180 | S
D8037E | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 2.956 | 0.616 | 0.541 | No | 5F762C | 180 | S
4A8120 | WINDOW-NONRES-FIXED | 2.32 | 2.32 | 2.956 | 0.616 | 0.541 | No | 84FB73 | 0 | N
AAE778 | WINDOW-NONRES-FIXED | 8.92 | 8.92 | 2.956 | 0.616 | 0.541 | No | FE5A3C | 270 | W
3AAD8B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | F629C1 | 0 | N
8128A9 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | F629C1 | 0 | N
9B1541 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 879583 | 180 | S
CF850A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 879583 | 180 | S
A6BA23 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | E326E4 | 90 | E
D10D28 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | E326E4 | 90 | E
38B811 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 1D96D7 | 90 | E
591336 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 1D96D7 | 90 | E
C044D6 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 1D96D7 | 90 | E
18748E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 6D2616 | 0 | N
1D94BE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 6D2616 | 0 | N
137A56 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.616 | 0.541 | No | A5A6A3 | 180 | S
1DA13A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 28B002 | 180 | S
44E54A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 28B002 | 180 | S
8D508E | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 28B002 | 180 | S
B2D381 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 28B002 | 180 | S
757D10 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 2.956 | 0.616 | 0.541 | No | EA6DC8 | 180 | S
24167A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 997723 | 180 | S
2C0938 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 997723 | 180 | S
E33BAE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | B40F89 | 270 | W
8600DD | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | CEC7BD | 180 | S
88E1FC | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 859BC1 | 0 | N
A1ED60 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 859BC1 | 0 | N
E8D997 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 859BC1 | 0 | N
F83F33 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.616 | 0.541 | No | 61E610 | 90 | E
B1F5EE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | D95F04 | 90 | E
F52F3D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 208CCF | 90 | E
80885D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 2.956 | 0.616 | 0.541 | No | AEF992 | 180 | S
2BE8DE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 1775A6 | 270 | W
513E2A | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 1775A6 | 270 | W
BA5CD9 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 1775A6 | 270 | W
FEEF06 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 54D065 | 180 | S
1AD478 | WINDOW-NONRES-FIXED | 3.72 | 3.72 | 2.956 | 0.616 | 0.541 | No | 97F00A | 180 | S
27F0AC | WINDOW-NONRES-FIXED | 5.95 | 5.95 | 2.956 | 0.616 | 0.541 | No | A497E9 | 180 | S
724114 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 88A75F | 180 | S
5635BC | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.616 | 0.541 | No | B4E619 | 90 | E
D538C4 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.616 | 0.541 | No | B4E619 | 90 | E
831C1D | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 2.956 | 0.616 | 0.541 | No | 9EC269 | 0 | N
9BB95F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | B316F7 | 0 | N
C0778D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | B316F7 | 0 | N
2EF63B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 9621FD | 0 | N
7D2D69 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 9621FD | 0 | N
C417C0 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 42CEE1 | 0 | N
4C1F71 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 4B1439 | 90 | E
B4E4BE | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 4B1439 | 90 | E
D23C8B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 4B1439 | 90 | E
EB042B | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 4B1439 | 90 | E
E55A57 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.616 | 0.541 | No | 4ABC66 | 180 | S
EEF55D | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 2.956 | 0.616 | 0.541 | No | 4ABC66 | 180 | S
93D018 | WINDOW-NONRES-FIXED | 6.69 | 6.69 | 2.956 | 0.616 | 0.541 | No | 5B04CF | 270 | W
DD9F5D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | 4B55FA | 90 | E
15B02B | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 9C3A6A | 0 | N
820282 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 9C3A6A | 0 | N
9BA05A | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 68A2D7 | 0 | N
C639E8 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 68A2D7 | 0 | N
A2790A | WINDOW-NONRES-FIXED | 4.18 | 4.18 | 2.956 | 0.616 | 0.541 | No | CE3FEF | 0 | N
79FCEE | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.616 | 0.541 | No | CE618F | 90 | E
EDE617 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.616 | 0.541 | No | CE618F | 90 | E
29FA28 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 5ADC59 | 0 | N
7248C5 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 5ADC59 | 0 | N
944FCE | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 5ADC59 | 0 | N
C41399 | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 5ADC59 | 0 | N
C61F0D | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 5ADC59 | 0 | N
EEC10E | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 5ADC59 | 0 | N
F0B23F | WINDOW-NONRES-FIXED | 2.79 | 2.79 | 2.956 | 0.616 | 0.541 | No | 5ADC59 | 0 | N
3DADE2 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.616 | 0.541 | No | C1BC97 | 180 | S
3DB407 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.616 | 0.541 | No | C1BC97 | 180 | S
5031C8 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.616 | 0.541 | No | C1BC97 | 180 | S
DF3E2C | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.616 | 0.541 | No | C1BC97 | 180 | S
95BA33 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.616 | 0.541 | No | D22917 | 90 | E
F27282 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.616 | 0.541 | No | D22917 | 90 | E
9DF7DE | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.616 | 0.541 | No | 38B339 | 270 | W
D0BE44 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.616 | 0.541 | No | 38B339 | 270 | W
FE9BC9 | WINDOW-NONRES-FIXED | 3.34 | 3.34 | 2.956 | 0.616 | 0.541 | No | 38B339 | 270 | W
B0FB49 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 2.956 | 0.616 | 0.541 | No | 8DA7DB | 180 | S
C087D0 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.616 | 0.541 | No | 8DA7DB | 180 | S
D2CA75 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.616 | 0.541 | No | 8DA7DB | 180 | S
44F571 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 2.956 | 0.616 | 0.541 | No | 1DEE26 | 180 | S
8F59F7 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 2.956 | 0.616 | 0.541 | No | 1DEE26 | 180 | S
6B5226 | WINDOW-NONRES-FIXED | 4.46 | 4.46 | 2.956 | 0.616 | 0.541 | No | BE5F2F | 270 | W
3833A2 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | C86329 | 90 | E
6BD844 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | C86329 | 90 | E
86D536 | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | C86329 | 90 | E
BAF71D | WINDOW-NONRES-FIXED | 2.23 | 2.23 | 2.956 | 0.616 | 0.541 | No | C86329 | 90 | E
142781 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.616 | 0.541 | No | 88E360 | 0 | N
9BC521 | WINDOW-NONRES-FIXED | 5.71 | 5.71 | 2.956 | 0.616 | 0.541 | No | 88E360 | 0 | N
2111A1 | WINDOW-NONRES-FIXED | 0.74 | 0.74 | 2.956 | 0.616 | 0.541 | No | DFC6F0 | 90 | E
93BBC3 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.616 | 0.541 | No | 2E2D0C | 0 | N
E74902 | WINDOW-NONRES-FIXED | 5.57 | 5.57 | 2.956 | 0.616 | 0.541 | No | 2E2D0C | 0 | N
C635A6 | WINDOW-NONRES-FIXED | 1.11 | 1.11 | 2.956 | 0.616 | 0.541 | No | 850EA7 | 180 | S
Total or Average |  |  | 308.29 | 2.96 | 0.616 | 0.541
North Total or Average |  |  | 97.22 | 2.96 | 0.616 | 0.541
Non-North Total or Average |  |  | 211.08 | 2.96 | 0.616 | 0.541
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
HEATSYS1 BOILER | Boiler:HotWater | 227488.15 | 0.7
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
AHU-1_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 312337.1 | 238067.08 | 74270.03 | 0.76 | 2.96
AHU-2_COOLC DXCOIL | Coil:Cooling:DX:TwoSpeed | 266020.23 | 212458.46 | 53561.77 | 0.8 | 3.07
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FLOOR 1 ANESTHESIA VAV BOX REHEAT COIL | Coil:Heating:Water | 3052.43 | -
FLOOR 1 BIO HAZ VAV BOX REHEAT COIL | Coil:Heating:Water | 113.86 | -
FLOOR 1 CAFE VAV BOX REHEAT COIL | Coil:Heating:Water | 16839.16 | -
FLOOR 1 CLEAN VAV BOX REHEAT COIL | Coil:Heating:Water | 1529.1 | -
FLOOR 1 CLEAN WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 1978.97 | -
FLOOR 1 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Water | 927.49 | -
FLOOR 1 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2851.27 | -
FLOOR 1 ELECTRICAL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 1734.39 | -
FLOOR 1 ELEVATOR PUMP ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 148273.27 | -
FLOOR 1 HUMID VAV BOX REHEAT COIL | Coil:Heating:Water | 409.32 | -
FLOOR 1 IT HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 284.66 | -
FLOOR 1 IT ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 828.42 | -
FLOOR 1 LOBBY VAV BOX REHEAT COIL | Coil:Heating:Water | 13457.05 | -
FLOOR 1 LOBBY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 487.99 | -
FLOOR 1 LOBBY TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1695.53 | -
FLOOR 1 LOCKER ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 8955.36 | -
FLOOR 1 LOCKER ROOM HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1008.52 | -
FLOOR 1 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Water | 4617.1 | -
FLOOR 1 MRI CONTROL ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 2277.29 | -
FLOOR 1 MRI HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 298.9 | -
FLOOR 1 MRI ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 69263.71 | -
FLOOR 1 MRI TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1653.17 | -
FLOOR 1 MED GAS VAV BOX REHEAT COIL | Coil:Heating:Water | 3785.57 | -
FLOOR 1 NOURISHMENT VAV BOX REHEAT COIL | Coil:Heating:Water | 2549.77 | -
FLOOR 1 NURSE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1008.52 | -
FLOOR 1 NURSE JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 109.8 | -
FLOOR 1 NURSE STATION VAV BOX REHEAT COIL | Coil:Heating:Water | 3591.5 | -
FLOOR 1 NURSE TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1219.97 | -
FLOOR 1 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Water | 3412.22 | -
FLOOR 1 OPERATING ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 42706.31 | -
FLOOR 1 OPERATING ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 42753.5 | -
FLOOR 1 OPERATING ROOM 3 VAV BOX REHEAT COIL | Coil:Heating:Water | 34545.19 | -
FLOOR 1 PACU VAV BOX REHEAT COIL | Coil:Heating:Water | 1950.74 | -
FLOOR 1 PRE-OP HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 1073.58 | -
FLOOR 1 PRE-OP ROOM 1 VAV BOX REHEAT COIL | Coil:Heating:Water | 2561.96 | -
FLOOR 1 PRE-OP ROOM 2 VAV BOX REHEAT COIL | Coil:Heating:Water | 4581.7 | -
FLOOR 1 PRE-OP TOILET VAV BOX REHEAT COIL | Coil:Heating:Water | 1650.17 | -
FLOOR 1 PROCEDURE ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 9658.2 | -
FLOOR 1 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Water | 7563.06 | -
FLOOR 1 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 260.26 | -
FLOOR 1 RECOVERY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 16526.95 | -
FLOOR 1 SCHEDULING VAV BOX REHEAT COIL | Coil:Heating:Water | 2233.34 | -
FLOOR 1 SCRUB VAV BOX REHEAT COIL | Coil:Heating:Water | 170.8 | -
FLOOR 1 SOIL VAV BOX REHEAT COIL | Coil:Heating:Water | 2846.62 | -
FLOOR 1 SOIL HOLD VAV BOX REHEAT COIL | Coil:Heating:Water | 1265.15 | -
FLOOR 1 SOIL WORK VAV BOX REHEAT COIL | Coil:Heating:Water | 4066.6 | -
FLOOR 1 STEP DOWN VAV BOX REHEAT COIL | Coil:Heating:Water | 10450.56 | -
FLOOR 1 STERILE HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 2877.19 | -
FLOOR 1 STERILE STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 805.19 | -
FLOOR 1 STORAGE VAV BOX REHEAT COIL | Coil:Heating:Water | 21528.43 | -
FLOOR 1 SUB-STERILE VAV BOX REHEAT COIL | Coil:Heating:Water | 4660.88 | -
FLOOR 1 UTILITY HALL VAV BOX REHEAT COIL | Coil:Heating:Water | 6359.54 | -
FLOOR 1 UTILITY JANITOR VAV BOX REHEAT COIL | Coil:Heating:Water | 85.4 | -
FLOOR 1 UTILITY ROOM VAV BOX REHEAT COIL | Coil:Heating:Water | 6837.66 | -
FLOOR 1 VESTIBULE VAV BOX REHEAT COIL | Coil:Heating:Water | 2837.14 | -
FLOOR 2 CONFERENCE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4909.47 | 1
FLOOR 2 CONFERENCE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 DICTATION VAV BOX REHEAT COIL | Coil:Heating:Electric | 303.99 | 1
FLOOR 2 EXAM 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 6091.89 | 1
FLOOR 2 EXAM 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3736.96 | 1
FLOOR 2 EXAM 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 5271.48 | 1
FLOOR 2 EXAM 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1182.13 | 1
FLOOR 2 EXAM 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3205 | 1
FLOOR 2 EXAM 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1775.75 | 1
FLOOR 2 EXAM 7 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3939.29 | 1
FLOOR 2 EXAM 8 VAV BOX REHEAT COIL | Coil:Heating:Electric | 2189.81 | 1
FLOOR 2 EXAM 9 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1993.2 | 1
FLOOR 2 EXAM HALL 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 398.12 | 1
FLOOR 2 EXAM HALL 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 398.12 | 1
FLOOR 2 EXAM HALL 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 398.12 | 1
FLOOR 2 EXAM HALL 4 VAV BOX REHEAT COIL | Coil:Heating:Electric | 384.88 | 1
FLOOR 2 EXAM HALL 5 VAV BOX REHEAT COIL | Coil:Heating:Electric | 384.88 | 1
FLOOR 2 EXAM HALL 6 VAV BOX REHEAT COIL | Coil:Heating:Electric | 383.89 | 1
FLOOR 2 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1201.06 | 1
FLOOR 2 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 489.95 | 1
FLOOR 2 NURSE STATION 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 937.99 | 1
FLOOR 2 NURSE STATION 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1121.47 | 1
FLOOR 2 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 6512.12 | 1
FLOOR 2 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 874.27 | 1
FLOOR 2 RECEPTION VAV BOX REHEAT COIL | Coil:Heating:Electric | 8739.02 | 1
FLOOR 2 RECEPTION HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1783.93 | 1
FLOOR 2 RECEPTION TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 0 | 1
FLOOR 2 SCHEDULING 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1260.02 | 1
FLOOR 2 SCHEDULING 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 1327.99 | 1
FLOOR 2 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 92.37 | 1
FLOOR 2 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 193.75 | 1
FLOOR 2 STORAGE 3 VAV BOX REHEAT COIL | Coil:Heating:Electric | 231.64 | 1
FLOOR 2 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 981.34 | 1
FLOOR 2 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6324.8 | 1
FLOOR 2 WORK HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1624.36 | 1
FLOOR 2 WORK TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 518.96 | 1
FLOOR 2 X-RAY VAV BOX REHEAT COIL | Coil:Heating:Electric | 4630.18 | 1
FLOOR 3 DRESSING ROOM VAV BOX REHEAT COIL | Coil:Heating:Electric | 221.18 | 1
FLOOR 3 ELEVATOR HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 1039.86 | 1
FLOOR 3 HUMID VAV BOX REHEAT COIL | Coil:Heating:Electric | 509.8 | 1
FLOOR 3 JANITOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1245.94 | 1
FLOOR 3 LOCKER VAV BOX REHEAT COIL | Coil:Heating:Electric | 728.61 | 1
FLOOR 3 LOUNGE VAV BOX REHEAT COIL | Coil:Heating:Electric | 4571.41 | 1
FLOOR 3 LOUNGE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 1531.29 | 1
FLOOR 3 MECHANICAL VAV BOX REHEAT COIL | Coil:Heating:Electric | 4135.26 | 1
FLOOR 3 MECHANICAL HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 849.57 | 1
FLOOR 3 OFFICE VAV BOX REHEAT COIL | Coil:Heating:Electric | 17015.21 | 1
FLOOR 3 OFFICE HALL VAV BOX REHEAT COIL | Coil:Heating:Electric | 2270.04 | 1
FLOOR 3 OFFICE TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 558.96 | 1
FLOOR 3 PHYSICAL THERAPY 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 15439.04 | 1
FLOOR 3 PHYSICAL THERAPY 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 3062.55 | 1
FLOOR 3 PHYSICAL THERAPY TOILET VAV BOX REHEAT COIL | Coil:Heating:Electric | 574.72 | 1
FLOOR 3 STORAGE 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 266.06 | 1
FLOOR 3 STORAGE 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 207.3 | 1
FLOOR 3 TREATMENT VAV BOX REHEAT COIL | Coil:Heating:Electric | 2261.86 | 1
FLOOR 3 UNDEVELOPED 1 VAV BOX REHEAT COIL | Coil:Heating:Electric | 15133.94 | 1
FLOOR 3 UNDEVELOPED 2 VAV BOX REHEAT COIL | Coil:Heating:Electric | 11204.66 | 1
FLOOR 3 UTILITY VAV BOX REHEAT COIL | Coil:Heating:Electric | 508.02 | 1
FLOOR 3 WORK VAV BOX REHEAT COIL | Coil:Heating:Electric | 6993.08 | 1
NE STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2332.54 | 1
NW ELEVATOR VAV BOX REHEAT COIL | Coil:Heating:Electric | 1184.05 | 1
NW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 2431.75 | 1
SW STAIR VAV BOX REHEAT COIL | Coil:Heating:Electric | 975.84 | 1
AHU-1_HEATC | Coil:Heating:Water | 72370.27 | -
AHU-2_HEATC | Coil:Heating:Water | 115275.68 | -
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FLOOR 1 ANESTHESIA EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 25.15 | 1 | Zone Exhaust Fans
FLOOR 1 LOBBY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 MRI CONTROL ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.08 | 29.33 | 1 | Zone Exhaust Fans
FLOOR 1 MRI ROOM EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.21 | 76.81 | 1 | Zone Exhaust Fans
FLOOR 1 MRI TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 NURSE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 PRE-OP TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL HOLD EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 16.27 | 1 | Zone Exhaust Fans
FLOOR 1 SOIL WORK EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.14 | 52.37 | 1 | Zone Exhaust Fans
FLOOR 2 CONFERENCE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.05 | 18.6 | 1 | Zone Exhaust Fans
FLOOR 2 RECEPTION TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.1 | 36.65 | 1 | Zone Exhaust Fans
FLOOR 2 WORK TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 LOUNGE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.15 | 55.84 | 1 | Zone Exhaust Fans
FLOOR 3 OFFICE TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.04 | 15.72 | 1 | Zone Exhaust Fans
FLOOR 3 PHYSICAL THERAPY TOILET EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.07 | 24.45 | 1 | Zone Exhaust Fans
AHU-1_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 17 | 28613.77 | 1 | Fan Energy
AHU-2_FAN | Fan:VariableVolume | 0.6 | 1017.59 | 16.07 | 27227.76 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
HEATSYS1 PUMP | Pump:ConstantSpeed | INTERMITTENT | 179352 | 1252.65 | 0.9
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 8.07 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 3 | 845000 | 0.78 | 0.22 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 199159.236 | 230.6035 | 1042.7473 | 0 | 0.0036 | 209230.3202 | 76594.9296
February | 177313.6616 | 205.4391 | 931.0939 | 0 | 0.0032 | 186827.276 | 68213.3498
March | 171632.9442 | 200.6455 | 938.6748 | 0 | 0.0033 | 188355.7658 | 66303.1313
April | 147793.5375 | 174.9182 | 853.106 | 0 | 0.0029 | 171193.8801 | 57423.3937
May | 144438.7762 | 171.755 | 850.6293 | 0 | 0.0029 | 170699.8974 | 56244.1618
June | 126248.6313 | 149.3871 | 728.0726 | 0 | 0.0025 | 146103.145 | 49047.4515
July | 126456.5073 | 149.2702 | 721.6782 | 0 | 0.0025 | 144818.6166 | 49072.3588
August | 121048.87 | 142.3584 | 679.7603 | 0 | 0.0024 | 136404.9882 | 46892.5567
September | 118492.2487 | 139.0884 | 659.8939 | 0 | 0.0023 | 132417.4557 | 45861.6338
October | 148041.9068 | 174.5121 | 839.8927 | 0 | 0.0029 | 168539.7318 | 57412.1581
November | 173646.9593 | 202.178 | 932.4924 | 0 | 0.0032 | 187111.9523 | 66954.6658
December | 193421.702 | 224.4211 | 1022.3511 | 0 | 0.0036 | 205139.6662 | 74459.2609
Annual Sum or Average | 1847690 | 2164.5766 | 10200.3925 | 0 | 0.0354 | 2046840 | 714479.0519
Minimum of Months | 118492.2487 | 139.0884 | 659.8939 | 0 | 0.0023 | 132417.4557 | 45861.6338
Maximum of Months | 199159.236 | 230.6035 | 1042.7473 | 0 | 0.0036 | 209230.3202 | 76594.9296
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 737246000000 | 422081.726 | 13-JAN-09:09 | 58033.2 | 120867.849 | 31895.804 | 119899.684 | 0 | 2025 | 1260.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 658306000000 | 414082.014 | 03-FEB-09:09 | 58033.2 | 120867.849 | 31931.664 | 108000.862 | 0 | 2025 | 1260.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 663692000000 | 387525.623 | 14-MAR-08:09 | 58033.2 | 120867.849 | 31907.015 | 85149.813 | 0 | 0 | 1260.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 603220000000 | 362460.735 | 10-APR-06:10 | 58033.2 | 96785.431 | 31789.687 | 84021.698 | 0 | 0 | 1260.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 601480000000 | 383753.809 | 25-MAY-12:00 | 58033.2 | 120867.849 | 34823.466 | 2447.092 | 66321.487 | 0 | 1260.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 514810000000 | 366142.926 | 12-JUN-14:00 | 58033.2 | 120867.849 | 33096.063 | 3435.029 | 60042.902 | 0 | 1260.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 510284000000 | 344229.763 | 21-JUL-16:00 | 58033.2 | 120867.849 | 35777.781 | 987.136 | 127303.081 | 0 | 1260.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 480638000000 | 374182.867 | 11-AUG-14:00 | 58033.2 | 120867.849 | 34375.736 | 3363.475 | 65802.459 | 0 | 1260.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 466587000000 | 351696.231 | 07-SEP-15:00 | 58033.2 | 120867.849 | 33612.327 | 5012.262 | 56401.742 | 0 | 1260.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 593868000000 | 368119.745 | 30-OCT-08:09 | 58033.2 | 120867.849 | 31800.927 | 76271.339 | 0 | 2025 | 1260.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 659309000000 | 390496.73 | 06-NOV-09:09 | 58033.2 | 120867.849 | 31798.218 | 92499.606 | 0 | 0 | 1260.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 722832000000 | 407124.777 | 29-DEC-09:09 | 58033.2 | 120867.849 | 31948.47 | 102753.51 | 0 | 2025 | 1260.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 7212270000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 466587000000 | 344229.763 |  | 58033.2 | 96785.431 | 31789.687 | 987.136 | 0 | 0 | 1260.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 737246000000 | 422081.726 |  | 58033.2 | 120867.849 | 35777.781 | 119899.684 | 127303.081 | 2025 | 1260.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 179056.79 | 35056.27 | 0 | 214113.06
Cost per Total Building Area ($/m2) | 47.07 | 9.22 | 0 | 56.29
Cost per Net Conditioned Building Area ($/m2) | 47.07 | 9.22 | 0 | 56.29

## Picture
DOE Commercial Building Benchmark - Outpatient Health Care

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
Floor 1 Anesthesia Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 Anesthesia Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 Anesthesia Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 Anesthesia Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 MRI Control Room Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 MRI Control Room Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 MRI Control Room Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 MRI Control Room Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 MRI Room Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 MRI Room Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 MRI Room Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 MRI Room Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 Operating Room 1 humidity sched | Any number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Floor 1 Operating Room 1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 Operating Room 1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 Operating Room 1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 Operating Room 1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 Operating Room 2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 Operating Room 2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 Operating Room 2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 Operating Room 2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 Operating Room 3 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 Operating Room 3 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 Operating Room 3 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 Operating Room 3 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 PACU Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 PACU Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 PACU Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 PACU Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 Pre-Op Room 1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 Pre-Op Room 1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 Pre-Op Room 1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 Pre-Op Room 1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 Pre-Op Room 2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 Pre-Op Room 2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 Pre-Op Room 2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 Pre-Op Room 2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 Procedure Room Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 Procedure Room Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 Procedure Room Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 Procedure Room Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 Recovery Room Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 Recovery Room Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 Recovery Room Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 Recovery Room Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 1 Step Down Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 1 Step Down Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 1 Step Down Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 1 Step Down Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 2 X-Ray Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 2 X-Ray Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 2 X-Ray Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 2 X-Ray Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 3 Physical Therapy 1 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 3 Physical Therapy 1 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 3 Physical Therapy 1 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 3 Physical Therapy 1 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Floor 3 Physical Therapy 2 Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Floor 3 Physical Therapy 2 Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Floor 3 Physical Therapy 2 Water Equipment Temp Sched | Temperature | Through 12/31 | All | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 1176 | 8232 | 429240
Floor 3 Physical Therapy 2 Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
AHU-1_OAminOAFracSchedule | Fraction | Through 12/31 | All | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 7.92 | 55.44 | 2890.8
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720
HeatSys1 Loop Setpoint Sched | Temperature | Through 12/31 | All | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 82.2 | 1972.8 | 13809.6 | 720072
Hours_of_operation | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.75 | 1 | 1 | 1 | 0.75 | 1 | 1 | 1 | 1 | 1 | 0.52 | 0.52 | 0.52 | 0.28 | 0.2 | 0.2 | 13.64 | 82.96 | 4325.77
|  |  | Sat, WinterDesign | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.46 | 0.7 | 0.7 | 0.7 | 0.51 | 0.51 | 0.51 | 0.51 | 0.51 | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 8.36
|  |  | Sun, Hol, Other | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 6.4
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.17 | 0.58 | 0.66 | 0.78 | 0.82 | 0.71 | 0.82 | 0.78 | 0.74 | 0.63 | 0.41 | 0.18 | 0.18 | 0.18 | 0.1 | 0.01 | 0.01 | 7.83 | 41.88 | 2183.74
|  |  | Sat, WinterDesign | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.2 | 0.28 | 0.3 | 0.3 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.1 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 2.49
|  |  | Sun, Hol, Other | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.24
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
INFIL_SCH | fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12
INFIL_HALF_ON_SCH | fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12
|  |  | SummerDesign, WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 266.4 | 1864.8 | 97236
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | 13.5 | 74.75 | 3897.68
|  |  | SummerDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.3 | 0.3 | 0.1 | 0.1 | 13.5
|  |  | WinterDesign | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 5.6
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 5.6
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.65
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 16.4 | 102.6 | 5349.86
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 16.4
|  |  | WinterDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 11.6
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 11.6
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 9
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | 12.5 | 66.7 | 3477.93
|  |  | SummerDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.05 | 12.5
|  |  | WinterDesign | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 3.75
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 3.75
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.45
HTGSETP_SCH | Temperature | Through 12/31 | WD | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6 | 3278.8 | 170966
|  |  | SummerDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 475.6
|  |  | WinterDesign | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
|  |  | Sats | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 461.6
|  |  | Sun, Hol, Other | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2
CLGSETP_SCH | Temperature | Through 12/31 | WD | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6 | 3995.6 | 208342
|  |  | SummerDesign | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 563.6
|  |  | WinterDesign | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
|  |  | Sats | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 577.6
|  |  | Sun, Hol, Other | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600
OR_HTGSETP_SCH | Temperature | Through 12/31 | All | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 439.2 | 3074.4 | 160308
OR_CLGSETP_SCH | Temperature | Through 12/31 | All | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 18.3 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 489.9 | 3429.3 | 178813.5
MinRelHumSetSch | Humidity | Through 12/31 | All | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 960 | 6720 | 350400
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
BLDG_OA_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 72 | 3754.29
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 12
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CAV_SAT_SCH | Temperature | Through 12/31 | All | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 266.4 | 1864.8 | 97236
VAV_SAT_SCH | Temperature | Through 12/31 | All | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 12.8 | 307.2 | 2150.4 | 112128
BLDG_CAV_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6 | 109.2 | 5694
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
|  |  | WinterDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
|  |  | Sat | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 15.6
BLDG_CAV_SCH_HUMID | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18 | 126 | 6570
|  |  | SummerDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
|  |  | WinterDesign | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
|  |  | Sun, Hol, Other | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 18
BLDG_OA_FRAC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 18 | 938.57
|  |  | SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 3
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0