## BuildingSummary
Building Summary Small Hotel pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Small Hotel
| Available Fuel Types | gas, electricity
| Principal Building Activity | Lodging
Form
| Total Floor Area (m2) | 4013.63 | PNNL - 17875 Technical Support Document: The Development of the Advanced Energy Design Guide for Highway Lodging Buildings
| Building Shape | Rectangle
| Aspect Ratio | 3
| Number of Floors | 4
Window Fraction (Window to Wall Ratio)
| South | 0.1524
| East | 0.0313
| North | 0.1139
| West | 0.0395
| Total | 0.1087
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor plus attic
| Floor to Ceiling Height (m) | 3.35 1st floor, 2.74 upper floors
| Floor to Floor Height (m) | 3.35 1st floor, 2.74 upper floors
| Roof type | Attic | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1694.66
| Net Dimensions - Total Area (m2) | 1510.43
| Wall to Skin Ratio | 0.6
Roof
| Construction Type | Attic | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1003.3894
| Net Dimensions - Total Area (m2) | 1003.3894
| Roof to Skin Ratio | 0.4
Window Dimensions (m2)
| South | 96.83
| East | 6.62
| North | 72.38
| West | 8.38
| Total Area (m2) | 184.21
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1661
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Dimensions - Total Area (m2)
Internal Mass
| Construction | 15 cm wood
Dimensions - Total Area (m2)
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.95 | See Benchmark Technical Report
HVAC
| System Type | PTAC | 2003 CBECS
| Heating Type | Unit heater, PTAC electric heat | 2003 CBECS
| Cooling Type | DX | 2003 CBECS
| Fan Control | Constant | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 80 | Winiarski and Halverson, 2008
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 3470.09

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
REARSTAIRSFLR1 | Yes | 1 | 20.07 | 67.3 | 3.3533 | 35.77 | 0 |  | 0 | 9.9549 | 0 |  |  |  |  | 0 |  | 2.1693
CORRIDORFLR1 | Yes | 1 | 150.51 | 504.62 | 3.3527 | 32.7 | 9.82 |  | 0 | 9.5035 | 0 |  |  |  | 0.25 | 37.6275 |  | 0.26448
REARSTORAGEFLR1 | No | 1 | 20.07 | 67.3 | 3.3533 | 35.77 | 0 |  | 0 | 4.9774 | 0 |  |  |  |  | 0 |  | 2.1693
FRONTLOUNGEFLR1 | Yes | 1 | 163.06 | 546.7 | 3.3528 | 94.0201 | 14.83 | 3.0937 | 52.7076 | 14.1516 | 15.4389 |  |  | 8 |  | 421.6604 |  | 0.7019
RESTROOMFLR1 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 0 | 32.61 | 1 | 11.8232 | 10.767 |  |  |  |  | 0 | 188.7788 | 0.49608
MEETINGROOMFLR1 | Yes | 1 | 80.27 | 269.14 | 3.3529 | 32.7 | 4.94 | 1.8581 | 43.2009 | 22.9155 | 12.9047 |  |  | 10 |  | 432.0091 |  | 0.49588
MECHANICALROOMFLR1 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 0 |  | 0 | 10.3453 | 0 |  |  |  | 0.25 | 8.1525 |  | 0.49608
GUESTROOM101 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.64 | 21.74 | 1.5 | 20.6905 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49608
GUESTROOM102 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.64 | 21.74 | 1.5 | 20.6905 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49608
GUESTROOM103 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.65 | 21.74 | 1.5 | 20.6905 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49608
GUESTROOM104 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.65 | 21.74 | 1.5 | 20.6895 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49613
GUESTROOM105 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.64 | 21.74 | 1.5 | 20.6895 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49613
EMPLOYEELOUNGEFLR1 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.64 | 3.0937 | 10.5409 | 17.7339 | 77.1847 |  |  | 8 |  | 84.3269 |  | 0.49613
LAUNDRYROOMFLR1 | Yes | 1 | 97.83 | 327.99 | 3.3527 | 39.86 | 4.94 | 9.2903 | 10.5303 | 11.1826 | 21.8747 | 184.3145 | 255.5145 | 13 |  | 136.8942 |  | 0.496
ELEVATORCOREFLR1 | No | 1 | 15.05 | 50.46 | 3.3528 | 6.13 | 0 |  | 0 | 0 | 128.4161 |  |  |  | 5 | 75.25 |  | 0.49582
EXERCISECENTERFLR1 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.65 | 3.0937 | 10.5409 | 14.7782 | 11.5041 |  |  | 10 |  | 105.4086 |  | 0.49613
FRONTOFFICEFLR1 | Yes | 1 | 130.44 | 437.33 | 3.3527 | 53.14 | 6.58 | 13.0064 | 10.0289 | 21.6803 | 12.9047 |  |  | 10 |  | 100.2888 |  | 0.49593
FRONTSTAIRSFLR1 | Yes | 1 | 20.07 | 67.28 | 3.3523 | 35.77 | 0 |  | 0 | 9.9528 | 0 |  |  |  |  | 0 |  | 2.1699
FRONTSTORAGEFLR1 | No | 1 | 12.54 | 42.05 | 3.3533 | 5.11 | 0 |  | 0 | 5.7543 | 0 |  |  |  |  | 0 |  | 0.49598
REARSTAIRSFLR2 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 8.7747 | 0 |  |  |  |  | 0 |  | 2.1697
CORRIDORFLR2 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 9.2219 | 0 |  |  |  | 0.25 | 31.355 |  | 0.21816
REARSTORAGEFLR2 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 4.3878 | 0 |  |  |  |  | 0 |  | 2.1693
GUESTROOM201 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.5261
GUESTROOM202_205 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591
GUESTROOM206_208 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 18.7728 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 0.49594
GUESTROOM209_212 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591
GUESTROOM213 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49591
GUESTROOM214 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597
GUESTROOM215_218 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596
ELEVATORCOREFLR2 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 0.49621
GUESTROOM219 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597
GUESTROOM220_223 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596
GUESTROOM224 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597
FRONTSTORAGEFLR2 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 4.8911 | 0 |  |  |  |  | 0 |  | 0.49579
FRONTSTAIRSFLR2 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 8.7739 | 0 |  |  |  |  | 0 |  | 2.1693
REARSTAIRSFLR3 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 8.7747 | 0 |  |  |  |  | 0 |  | 2.1697
CORRIDORFLR3 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 9.2219 | 0 |  |  |  | 0.25 | 31.355 |  | 0.21816
REARSTORAGEFLR3 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 4.3878 | 0 |  |  |  |  | 0 |  | 2.1693
GUESTROOM301 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.5261
GUESTROOM302_305 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591
GUESTROOM306_308 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 18.7728 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 0.49594
GUESTROOM309_312 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591
GUESTROOM313 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49591
GUESTROOM314 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597
GUESTROOM315_318 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596
ELEVATORCOREFLR3 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 0.49621
GUESTROOM319 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597
GUESTROOM320_323 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596
GUESTROOM324 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597
FRONTSTORAGEFLR3 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 4.8911 | 0 |  |  |  |  | 0 |  | 0.49579
FRONTSTAIRSFLR3 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 8.7739 | 0 |  |  |  |  | 0 |  | 2.1693
REARSTAIRSFLR4 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 4.3874 | 0 |  |  |  |  | 0 |  | 3.6574
CORRIDORFLR4 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 9.2219 | 0 |  |  |  | 0.25 | 31.355 |  | 1.706
REARSTORAGEFLR4 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 4.3878 | 0 |  |  |  |  | 0 |  | 3.6567
GUESTROOM401 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 3.0138
GUESTROOM402_405 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838
GUESTROOM406_408 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 18.7728 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 1.9838
GUESTROOM409_412 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838
GUESTROOM413 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9837
GUESTROOM414 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9839
GUESTROOM415_418 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838
ELEVATORCOREFLR4 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 1.9838
GUESTROOM419 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9839
GUESTROOM420_423 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838
GUESTROOM424 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9839
FRONTSTORAGEFLR4 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 4.8911 | 0 |  |  |  |  | 0 |  | 1.9832
FRONTSTAIRSFLR4 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 8.7739 | 0 |  |  |  |  | 0 |  | 3.6573
ATTIC | No | 1 | 1092.62 | 1582.44 | 1.4483 | 0 | 0 | [8 empty] | 0 |  | 1
Total Conditioned Zones |  |  | 4013.63 | 11621.75 |  | 1694.6616 | 184.2302 |  | 254.0541
Data Source | [7 empty] | 1 |  | 2 | 4 |  | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] PNNL - 17875 Technical Support Document: The Development of the Advanced Energy Design Guide for Highway Lodging Buildings

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Roof
| Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
| R-value attic floor (m2·K / W) | 1.7606 | 1.7606 | 1.7606 | 1.7606 | 1.7606 | 1.7606 | 1.7606 | 2.0492 | 1.9802 | 2.0704 | 2.5 | 2.3697 | 2.994 | 2.994 | 2.9326 | 2.994
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| CORRIDORFLR1 PTAC DXCOIL | 10.3274 | 10.384 | 10.4117 | 10.6076 | 9.2981 | 10.0871 | 8.0227 | 9.9495 | 10.5685 | 8.7776 | 9.3847 | 9.861 | 9.3973 | 9.401 | 8.4249 | 7.2048
| CORRIDORFLR2 PTAC DXCOIL | 5.8822 | 5.9487 | 6.5347 | 6.0663 | 5.3274 | 6.5384 | 5.1257 | 5.7205 | 6.2559 | 5.4283 | 5.3406 | 5.6758 | 5.2904 | 5.4437 | 4.965 | 4.627
| CORRIDORFLR3 PTAC DXCOIL | 5.5819 | 5.6517 | 6.2326 | 5.681 | 4.8926 | 6.2016 | 4.7403 | 5.3268 | 5.7736 | 5.0385 | 4.9671 | 5.2037 | 4.9082 | 5.0131 | 4.6026 | 4.3214
| CORRIDORFLR4 PTAC DXCOIL | 7.0563 | 7.3894 | 8.4165 | 7.4901 | 6.0491 | 8.1206 | 5.6671 | 6.6818 | 7.1442 | 6.002 | 5.9309 | 6.0889 | 5.4976 | 5.4775 | 5.0676 | 4.6129
| EMPLOYEELOUNGEFLR1 PTAC DXCOIL | 7.7983 | 7.6881 | 7.1077 | 7.1766 | 5.6715 | 6.3272 | 5.0813 | 7.0756 | 6.544 | 5.328 | 6.9044 | 6.34 | 7.2607 | 6.0053 | 6.1253 | 5.0224
| EXERCISECENTERFLR1 PTAC DXCOIL | 3.9394 | 3.9166 | 3.9846 | 4.034 | 3.1729 | 3.9773 | 1.9895 | 3.7056 | 3.0095 | 2.4805 | 3.5848 | 2.8926 | 3.6215 | 2.4531 | 3.1721 | 1.9635
| FRONTLOUNGEFLR1 PTAC DXCOIL | 22.4968 | 24.0824 | 26.1346 | 25.3263 | 19.8441 | 23.8777 | 17.8005 | 25.0133 | 18.2897 | 18.6998 | 22.2547 | 16.9736 | 22.3993 | 15.6604 | 19.6526 | 14.5597
| FRONTOFFICEFLR1 PTAC DXCOIL | 11.0569 | 10.814 | 9.9582 | 10.0089 | 7.2659 | 8.6763 | 5.8911 | 9.6783 | 8.4885 | 6.64 | 9.8207 | 7.7212 | 9.3555 | 7.3327 | 7.3433 | 5.3999
| GUESTROOM101 PTAC DXCOIL | 2.4233 | 2.5821 | 2.5713 | 2.5261 | 2.3085 | 2.3713 | 2.4336 | 2.5427 | 2.3333 | 2.4321 | 2.3349 | 2.1354 | 2.2811 | 2.141 | 1.8843 | 1.9273
| GUESTROOM102 PTAC DXCOIL | 2.4821 | 2.6433 | 2.6417 | 2.5886 | 2.3827 | 2.4564 | 2.5125 | 2.6058 | 2.4134 | 2.5159 | 2.3896 | 2.203 | 2.3363 | 2.2111 | 1.9499 | 1.9998
| GUESTROOM103 PTAC DXCOIL | 2.6547 | 2.8219 | 2.8767 | 2.7608 | 2.4882 | 2.6785 | 2.5295 | 2.7299 | 2.4668 | 2.5821 | 2.5001 | 2.2164 | 2.4385 | 2.2367 | 1.9794 | 1.9902
| GUESTROOM104 PTAC DXCOIL | 2.6222 | 2.5858 | 2.4832 | 2.4069 | 1.8139 | 2.37 | 1.4559 | 2.288 | 2.1502 | 1.6953 | 2.2618 | 1.9011 | 2.1656 | 1.8175 | 1.6666 | 1.5084
| GUESTROOM105 PTAC DXCOIL | 2.5682 | 2.5282 | 2.366 | 2.3666 | 1.8762 | 2.2775 | 1.5913 | 2.2757 | 2.2713 | 1.7737 | 2.2576 | 2.0622 | 2.1716 | 1.9561 | 1.7582 | 1.4679
| GUESTROOM201 PTAC DXCOIL | 4.1354 | 4.2589 | 4.5411 | 4.1009 | 3.7031 | 4.5646 | 3.8704 | 3.8198 | 4.0024 | 3.7154 | 3.6107 | 3.6508 | 3.401 | 3.455 | 3.0752 | 2.8971
| GUESTROOM202_205 PTAC DXCOIL | 10.1212 | 10.9038 | 11.4886 | 10.7704 | 10.1375 | 11.2148 | 11.455 | 10.9162 | 11.0545 | 11.366 | 10.1761 | 10.2985 | 10.0026 | 10.3162 | 9.326 | 10.0568
| GUESTROOM206_208 PTAC DXCOIL | 8.0947 | 8.7502 | 9.2757 | 8.6834 | 8.3591 | 9.1873 | 9.5718 | 8.849 | 9.0696 | 9.4969 | 8.1383 | 8.3353 | 8.0314 | 8.4082 | 7.6022 | 8.3347
| GUESTROOM209_212 PTAC DXCOIL | 9.9547 | 10.7275 | 11.2889 | 10.5906 | 9.9201 | 10.9641 | 11.2104 | 10.734 | 10.8163 | 11.1135 | 10.0138 | 10.0824 | 9.8409 | 10.102 | 9.1272 | 9.8313
| GUESTROOM213 PTAC DXCOIL | 2.7622 | 2.974 | 3.2076 | 2.9383 | 2.7241 | 3.1526 | 2.9816 | 2.9361 | 2.9196 | 3.0152 | 2.7321 | 2.6807 | 2.6769 | 2.7023 | 2.4591 | 2.6155
| GUESTROOM214 PTAC DXCOIL | 2.83 | 2.8114 | 2.995 | 2.7136 | 2.151 | 2.9618 | 1.9797 | 2.5688 | 2.711 | 2.1907 | 2.4431 | 2.442 | 2.4653 | 2.3551 | 2.1526 | 1.9627
| GUESTROOM215_218 PTAC DXCOIL | 10.579 | 10.4809 | 10.5309 | 9.9842 | 8.3724 | 10.6527 | 8.0153 | 9.7442 | 10.626 | 8.5604 | 9.7702 | 9.91 | 9.4737 | 9.4764 | 8.5926 | 8.0209
| GUESTROOM219 PTAC DXCOIL | 3.0396 | 3.0163 | 3.1753 | 3.0061 | 2.5808 | 3.2098 | 2.4752 | 2.8406 | 3.2394 | 2.6366 | 2.8648 | 3.0637 | 2.7783 | 2.9269 | 2.6585 | 2.5207
| GUESTROOM220_223 PTAC DXCOIL | 10.1116 | 10.0133 | 10.0122 | 9.5199 | 7.7764 | 9.9984 | 7.4014 | 9.2793 | 9.8878 | 7.9419 | 9.2759 | 9.1587 | 8.9814 | 8.763 | 7.9429 | 7.3906
| GUESTROOM224 PTAC DXCOIL | 2.7747 | 2.7483 | 2.8639 | 2.6404 | 2.1185 | 2.8496 | 1.9697 | 2.5184 | 2.6904 | 2.152 | 2.4011 | 2.4479 | 2.3057 | 2.3382 | 2.1421 | 1.9772
| GUESTROOM301 PTAC DXCOIL | 4.1234 | 4.2376 | 4.5322 | 4.0698 | 3.637 | 4.5317 | 3.7996 | 3.7699 | 3.9495 | 3.6672 | 3.5724 | 3.6051 | 3.3712 | 3.4166 | 3.0459 | 2.888
| GUESTROOM302_305 PTAC DXCOIL | 10.1048 | 10.6749 | 11.5322 | 10.7634 | 10.0625 | 11.2505 | 11.4473 | 10.8926 | 11.0505 | 11.3687 | 10.2014 | 10.3508 | 10.0275 | 10.3842 | 9.4004 | 10.1811
| GUESTROOM306_308 PTAC DXCOIL | 8.1677 | 8.6295 | 9.4161 | 8.7722 | 8.4169 | 9.3462 | 9.723 | 8.9272 | 9.1811 | 9.6569 | 8.2428 | 8.4787 | 8.1373 | 8.5716 | 7.7642 | 8.5712
| GUESTROOM309_312 PTAC DXCOIL | 10.0888 | 10.6577 | 11.5117 | 10.7473 | 10.045 | 11.2238 | 11.4276 | 10.8773 | 11.0279 | 11.3496 | 10.1876 | 10.328 | 10.0165 | 10.3656 | 9.3845 | 10.164
| GUESTROOM313 PTAC DXCOIL | 2.771 | 2.9307 | 3.2509 | 2.9596 | 2.7292 | 3.2004 | 3.0139 | 2.9558 | 2.9468 | 3.055 | 2.7614 | 2.7162 | 2.7054 | 2.7479 | 2.5073 | 2.6874
| GUESTROOM314 PTAC DXCOIL | 2.8602 | 2.8452 | 3.0728 | 2.7618 | 2.178 | 3.0403 | 2.0234 | 2.605 | 2.7593 | 2.2377 | 2.4836 | 2.4894 | 2.5021 | 2.4042 | 2.21 | 2.0366
| GUESTROOM315_318 PTAC DXCOIL | 10.3247 | 10.2403 | 10.2953 | 9.7108 | 8.0271 | 10.405 | 7.7133 | 9.5027 | 10.233 | 8.255 | 9.5206 | 9.5016 | 9.2247 | 9.1115 | 8.2886 | 7.7743
| GUESTROOM319 PTAC DXCOIL | 2.6997 | 2.679 | 2.7473 | 2.5532 | 2.1233 | 2.769 | 2.0334 | 2.4717 | 2.7035 | 2.1826 | 2.3656 | 2.5049 | 2.4089 | 2.404 | 2.1889 | 2.048
| GUESTROOM320_323 PTAC DXCOIL | 10.221 | 10.1367 | 10.1549 | 9.6438 | 7.9075 | 10.2615 | 7.5967 | 9.403 | 10.0796 | 8.1325 | 9.4174 | 9.3519 | 9.1223 | 8.9685 | 8.1584 | 7.6485
| GUESTROOM324 PTAC DXCOIL | 2.7883 | 2.7676 | 2.9266 | 2.6688 | 2.1249 | 2.9084 | 1.9917 | 2.5392 | 2.7084 | 2.1784 | 2.425 | 2.4644 | 2.3352 | 2.3581 | 2.1753 | 2.0241
| GUESTROOM401 PTAC DXCOIL | 4.3781 | 4.5141 | 4.9513 | 4.3994 | 3.742 | 4.8753 | 3.8199 | 3.9129 | 4.185 | 3.6817 | 3.6695 | 3.7372 | 3.366 | 3.4089 | 3.0696 | 3.3335
| GUESTROOM402_405 PTAC DXCOIL | 11.2965 | 11.6738 | 12.2129 | 11.1715 | 9.8791 | 11.998 | 11.5539 | 10.8732 | 11.3058 | 11.4496 | 10.3362 | 10.4741 | 9.8815 | 9.9873 | 9.1316 | 10.0541
| GUESTROOM406_408 PTAC DXCOIL | 9.1419 | 9.431 | 9.9516 | 9.0743 | 8.157 | 9.8547 | 9.7805 | 8.8406 | 9.284 | 9.6843 | 8.3644 | 8.5695 | 8.0121 | 8.2035 | 7.5011 | 8.4891
| GUESTROOM409_412 PTAC DXCOIL | 11.2955 | 11.6475 | 12.1861 | 11.1468 | 9.8683 | 11.9605 | 11.5488 | 10.8877 | 11.2738 | 11.4466 | 10.3512 | 10.4472 | 9.8753 | 9.9783 | 9.1245 | 10.0542
| GUESTROOM413 PTAC DXCOIL | 3.0749 | 3.1847 | 3.4863 | 3.0995 | 2.6681 | 3.3987 | 3.0466 | 2.9472 | 3.0196 | 3.0771 | 2.7947 | 2.7582 | 2.6658 | 2.6586 | 2.4409 | 2.6593
| GUESTROOM414 PTAC DXCOIL | 3.137 | 3.173 | 3.5871 | 3.1733 | 2.5106 | 3.5083 | 2.2897 | 2.9188 | 3.1116 | 2.5141 | 2.72 | 2.7494 | 2.604 | 2.5587 | 2.3792 | 2.159
| GUESTROOM415_418 PTAC DXCOIL | 11.322 | 11.4283 | 12.0904 | 11.0418 | 9.1949 | 12.0103 | 8.6026 | 10.43 | 11.3991 | 9.1839 | 9.7544 | 10.2829 | 9.1901 | 9.4891 | 8.7623 | 8.1707
| GUESTROOM419 PTAC DXCOIL | 2.938 | 2.9631 | 3.2024 | 2.9073 | 2.3929 | 3.1684 | 2.2249 | 2.6996 | 2.965 | 2.3819 | 2.5158 | 2.6562 | 2.3826 | 2.443 | 2.2575 | 2.0908
| GUESTROOM420_423 PTAC DXCOIL | 11.2513 | 11.3574 | 11.9917 | 10.9494 | 9.1133 | 11.9097 | 8.5275 | 10.362 | 11.2973 | 9.1029 | 9.688 | 10.1846 | 9.1137 | 9.3963 | 8.6774 | 8.0903
| GUESTROOM424 PTAC DXCOIL | 3.0782 | 3.1061 | 3.4562 | 3.0948 | 2.4584 | 3.3886 | 2.253 | 2.8413 | 3.0593 | 2.4539 | 2.6464 | 2.7194 | 2.5371 | 2.523 | 2.345 | 2.1539
| LAUNDRYROOMFLR1 PTAC DXCOIL | 29.8406 | 29.5092 | 29.296 | 28.9597 | 27.2579 | 29.4848 | 26.0331 | 28.1302 | 32.4769 | 26.9816 | 28.0698 | 32.2218 | 28.0934 | 30.4918 | 27.8593 | 26.2669
| MECHANICALROOMFLR1 PTAC DXCOIL | 1.3246 | 1.4376 | 1.3812 | 1.3831 | 1.204 | 1.2377 | 1.2009 | 1.3553 | 1.1055 | 1.1766 | 1.2837 | 1.0482 | 1.2323 | 1.0629 | 0.96561 | 1.1816
| MEETINGROOMFLR1 PTAC DXCOIL | 12.3102 | 12.9481 | 13.6917 | 13.6015 | 12.7507 | 13.9525 | 9.7798 | 13.3495 | 11.82 | 11.1185 | 12.4373 | 11.3875 | 12.579 | 9.8745 | 12.002 | 8.0998
| RESTROOMFLR1 PTAC DXCOIL | 1.6231 | 1.7455 | 1.8262 | 1.8177 | 1.7483 | 1.8258 | 1.7345 | 1.7336 | 1.7605 | 1.7269 | 1.6593 | 1.6958 | 1.654 | 1.6767 | 1.4644 | 1.3919
Heating (kW)
| CORRIDORFLR1 PTAC HEAT COIL | 1.8478 | 1.9515 | 1.6465 | 2.5908 | 1.8413 | 1.927 | 1.6994 | 3.0318 | 2.4433 | 2.0267 | 3.914 | 3.2061 | 4.5822 | 4.3675 | 4.8797 | 6.9434
| CORRIDORFLR2 PTAC HEAT COIL | 1.5398 | 1.6339 | 1.3721 | 2.1506 | 1.2812 | 1.5341 | 1.4162 | 2.3808 | 1.9049 | 1.6937 | 3.0054 | 2.472 | 3.4097 | 3.2128 | 3.5726 | 4.7858
| CORRIDORFLR3 PTAC HEAT COIL | 1.2319 | 2.0769 | 1.4497 | 2.5902 | 1.2812 | 1.9196 | 1.4396 | 2.8098 | 2.322 | 2.0998 | 3.4366 | 2.8986 | 3.8308 | 3.6332 | 4.0023 | 5.243
| CORRIDORFLR4 PTAC HEAT COIL | 1.922 | 3.8181 | 2.8831 | 4.5683 | 2.2473 | 3.591 | 2.8342 | 4.7772 | 4.2519 | 3.6775 | 5.5081 | 5.0214 | 5.8188 | 5.7347 | 6.1392 | 8.0007
| EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | 3.4574 | 4.5642 | 3.8508 | 4.9236 | 3.5958 | 4.1628 | 3.9746 | 5.4808 | 4.3548 | 4.7399 | 6.4028 | 5.1984 | 6.9195 | 6.3053 | 7.0826 | 8.7707
| EXERCISECENTERFLR1 PTAC HEAT COIL | 4.3217 | 5.7052 | 4.8135 | 6.1545 | 4.4948 | 5.2035 | 4.9682 | 6.851 | 5.4435 | 5.9249 | 8.0034 | 6.498 | 8.6494 | 7.8817 | 8.8533 | 10.9634
| FRONTLOUNGEFLR1 PTAC HEAT COIL | 16.6395 | 21.9664 | 18.533 | 23.6961 | 17.3058 | 20.0346 | 19.1286 | 26.378 | 20.9588 | 22.812 | 30.815 | 25.0188 | 33.3019 | 30.7596 | 34.3106 | 44.9394
| FRONTOFFICEFLR1 PTAC HEAT COIL | 3.9288 | 5.9225 | 4.7589 | 7.2078 | 4.0861 | 5.9333 | 4.6389 | 8.0179 | 6.7734 | 6.3217 | 9.8151 | 8.3613 | 10.9393 | 10.3775 | 11.4016 | 14.8778
| FRONTSTAIRSFLR1 UNIT HEATER COIL | 0.13915 | 1.3469 | 0.81631 | 1.854 | 0.42141 | 1.2765 | 0.77851 | 2.1161 | 1.6732 | 1.4235 | 2.9767 | 2.4414 | 3.4537 | 3.2761 | 3.649 | 5.1592
| FRONTSTAIRSFLR2 UNIT HEATER COIL | 0.35119 | 1.2994 | 0.79866 | 1.707 | 0.4908 | 1.1779 | 0.78239 | 1.9038 | 1.5242 | 1.3173 | 2.6112 | 2.1598 | 3.0002 | 2.8481 | 3.1551 | 4.3801
| FRONTSTAIRSFLR3 UNIT HEATER COIL | 0.39522 | 1.3404 | 0.83228 | 1.7426 | 0.5237 | 1.2107 | 0.81886 | 1.9389 | 1.5576 | 1.3543 | 2.6474 | 2.1944 | 3.0353 | 2.8822 | 3.1914 | 4.4167
| FRONTSTAIRSFLR4 UNIT HEATER COIL | 0.49366 | 1.535 | 0.9929 | 1.9726 | 0.64651 | 1.3975 | 0.97468 | 2.1788 | 1.7893 | 1.5413 | 2.9141 | 2.4647 | 3.2964 | 3.1583 | 3.4754 | 4.7938
| FRONTSTORAGEFLR1 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05593 | 0 | 0.1049 | 0.10121 | 0.12505 | 0.28181
| FRONTSTORAGEFLR2 UNIT HEATER COIL | 0 | 0 | 0 | 0.0304 | 0 | 0 | 0 | 0.03733 | 0 | 0 | 0.10916 | 0.07323 | 0.14593 | 0.13775 | 0.15916 | 0.27077
| FRONTSTORAGEFLR3 UNIT HEATER COIL | 0 | 0 | 0 | 0.05292 | 0 | 0 | 0 | 0.05883 | 0.02604 | 0 | 0.1283 | 0.0919 | 0.16407 | 0.1557 | 0.1778 | 0.28966
| FRONTSTORAGEFLR4 UNIT HEATER COIL | 0 | 0.12326 | 0.02792 | 0.19881 | 0 | 0.10497 | 0 | 0.20782 | 0.17095 | 0.10108 | 0.29172 | 0.25881 | 0.32307 | 0.32503 | 0.35026 | 0.52081
| GUESTROOM101 PTAC HEAT COIL | 0.55632 | 1.16 | 0.94674 | 1.4252 | 0.72654 | 1.1882 | 0.91073 | 1.5611 | 1.3525 | 1.2334 | 1.8907 | 1.6337 | 2.1104 | 2.0204 | 2.2007 | 2.872
| GUESTROOM102 PTAC HEAT COIL | 0.55632 | 1.1818 | 0.9667 | 1.4483 | 0.74552 | 1.2093 | 0.93073 | 1.5849 | 1.3758 | 1.2557 | 1.9143 | 1.6568 | 2.1349 | 2.0451 | 2.2257 | 2.8988
| GUESTROOM103 PTAC HEAT COIL | 0.72228 | 1.4264 | 1.1981 | 1.7071 | 0.96108 | 1.4553 | 1.1586 | 1.8396 | 1.6283 | 1.4938 | 2.1841 | 1.9247 | 2.4101 | 2.3226 | 2.5018 | 3.1919
| GUESTROOM104 PTAC HEAT COIL | 0.71345 | 1.4067 | 1.184 | 1.6869 | 0.94804 | 1.4427 | 1.1446 | 1.8226 | 1.6074 | 1.4739 | 2.1744 | 1.9182 | 2.3961 | 2.3083 | 2.4874 | 3.1779
| GUESTROOM105 PTAC HEAT COIL | 0.55632 | 1.1749 | 0.96559 | 1.4426 | 0.73987 | 1.2108 | 0.92857 | 1.583 | 1.3694 | 1.2499 | 1.9202 | 1.6659 | 2.1371 | 2.0473 | 2.2279 | 2.9055
| GUESTROOM201 PTAC HEAT COIL | 1.2044 | 2.199 | 1.6723 | 2.6281 | 1.3537 | 2.066 | 1.6587 | 2.7799 | 2.3784 | 2.1817 | 3.3851 | 2.925 | 3.7436 | 3.5799 | 3.8784 | 4.9851
| GUESTROOM202_205 PTAC HEAT COIL | 2.3896 | 4.4417 | 3.3688 | 5.323 | 2.7204 | 4.1696 | 3.357 | 5.785 | 4.8836 | 4.5609 | 6.9378 | 5.9039 | 7.7056 | 7.3137 | 8.0142 | 10.3021
| GUESTROOM206_208 PTAC HEAT COIL | 1.7827 | 3.4349 | 2.5815 | 4.1515 | 2.0574 | 3.2293 | 2.5692 | 4.5297 | 3.8175 | 3.5517 | 5.4006 | 4.5854 | 6.0115 | 5.7045 | 6.2629 | 8.0681
| GUESTROOM209_212 PTAC HEAT COIL | 2.3293 | 4.3424 | 3.2889 | 5.2058 | 2.6543 | 4.0726 | 3.2793 | 5.6702 | 4.7722 | 4.4659 | 6.8164 | 5.7858 | 7.5764 | 7.1828 | 7.8819 | 10.1513
| GUESTROOM213 PTAC HEAT COIL | 0.81553 | 1.3587 | 1.0777 | 1.5887 | 0.90483 | 1.2886 | 1.073 | 1.6999 | 1.472 | 1.381 | 2.001 | 1.7405 | 2.1967 | 2.1001 | 2.2738 | 2.8569
| GUESTROOM214 PTAC HEAT COIL | 0.78003 | 1.3235 | 1.0453 | 1.5578 | 0.86934 | 1.2603 | 1.0398 | 1.6692 | 1.4379 | 1.3463 | 1.9715 | 1.7142 | 2.1645 | 2.0665 | 2.2421 | 2.8256
| GUESTROOM215_218 PTAC HEAT COIL | 2.2253 | 4.0751 | 3.0328 | 4.9731 | 2.3701 | 3.8428 | 3.0164 | 5.4425 | 4.5231 | 4.2081 | 6.598 | 5.5757 | 7.3502 | 6.9509 | 7.6591 | 9.9693
| GUESTROOM219 PTAC HEAT COIL | 0.55632 | 0.83947 | 0.61963 | 1.0797 | 0.5786 | 0.78102 | 0.63954 | 1.1965 | 0.95546 | 0.86764 | 1.5029 | 1.2357 | 1.6982 | 1.595 | 1.7782 | 2.3964
| GUESTROOM220_223 PTAC HEAT COIL | 2.2253 | 4.2032 | 3.1669 | 5.0935 | 2.5134 | 3.9701 | 3.1526 | 5.5652 | 4.6486 | 4.3383 | 6.722 | 5.6987 | 7.4776 | 7.0771 | 7.7877 | 10.0603
| GUESTROOM224 PTAC HEAT COIL | 0.70261 | 1.2687 | 0.98335 | 1.5042 | 0.79929 | 1.2083 | 0.97687 | 1.6199 | 1.3898 | 1.2956 | 1.9133 | 1.6579 | 2.1029 | 2.0036 | 2.1802 | 2.7529
| GUESTROOM301 PTAC HEAT COIL | 1.2672 | 2.262 | 1.719 | 2.6953 | 1.3994 | 2.117 | 1.7081 | 2.8432 | 2.4358 | 2.234 | 3.4537 | 2.9898 | 3.8087 | 3.6433 | 3.945 | 5.0547
| GUESTROOM302_305 PTAC HEAT COIL | 2.5679 | 4.5839 | 3.4702 | 5.4615 | 2.8315 | 4.2694 | 3.4708 | 5.9209 | 5.0018 | 4.6765 | 7.0731 | 6.0325 | 7.8208 | 7.4266 | 8.1363 | 10.431
| GUESTROOM306_308 PTAC HEAT COIL | 2.0437 | 3.6604 | 2.766 | 4.3765 | 2.253 | 3.413 | 2.7664 | 4.7527 | 4.0248 | 3.754 | 5.6209 | 4.7984 | 6.2192 | 5.9103 | 6.4786 | 8.2967
| GUESTROOM309_312 PTAC HEAT COIL | 2.551 | 4.5501 | 3.4447 | 5.4207 | 2.812 | 4.2367 | 3.4464 | 5.8834 | 4.9658 | 4.6476 | 7.0303 | 5.9909 | 7.7757 | 7.3809 | 8.0909 | 10.3791
| GUESTROOM313 PTAC HEAT COIL | 0.86816 | 1.4037 | 1.111 | 1.6347 | 0.93973 | 1.3229 | 1.1093 | 1.7453 | 1.5127 | 1.4198 | 2.0466 | 1.7839 | 2.2386 | 2.1414 | 2.3177 | 2.9034
| GUESTROOM314 PTAC HEAT COIL | 0.83942 | 1.3765 | 1.0864 | 1.6124 | 0.91129 | 1.301 | 1.0839 | 1.7219 | 1.4863 | 1.3936 | 2.0239 | 1.764 | 2.2139 | 2.1143 | 2.2939 | 2.8786
| GUESTROOM315_318 PTAC HEAT COIL | 2.4979 | 4.4988 | 3.4118 | 5.3892 | 2.7649 | 4.2088 | 3.4114 | 5.8481 | 4.9177 | 4.6042 | 6.9979 | 5.9687 | 7.7369 | 7.3317 | 8.0553 | 10.3453
| GUESTROOM319 PTAC HEAT COIL | 0.59567 | 1.1476 | 0.85183 | 1.3914 | 0.67337 | 1.0707 | 0.84954 | 1.5071 | 1.2611 | 1.1674 | 1.8205 | 1.5484 | 2.0186 | 1.9139 | 2.1041 | 2.7268
| GUESTROOM320_323 PTAC HEAT COIL | 2.4844 | 4.4735 | 3.3908 | 5.3587 | 2.7481 | 4.1843 | 3.3912 | 5.8184 | 4.8897 | 4.5802 | 6.9659 | 5.938 | 7.7032 | 7.2979 | 8.0208 | 10.3003
| GUESTROOM324 PTAC HEAT COIL | 0.77818 | 1.3318 | 1.0346 | 1.5614 | 0.85239 | 1.257 | 1.0323 | 1.6747 | 1.4411 | 1.3517 | 1.9672 | 1.7095 | 2.1531 | 2.0522 | 2.2325 | 2.8063
| GUESTROOM401 PTAC HEAT COIL | 1.4898 | 2.6538 | 2.037 | 3.1466 | 1.6583 | 2.493 | 2.0177 | 3.2987 | 2.8799 | 2.595 | 3.9405 | 3.4861 | 4.2756 | 4.1359 | 4.4498 | 5.7096
| GUESTROOM402_405 PTAC HEAT COIL | 3.4809 | 6.1679 | 4.764 | 7.2695 | 3.8907 | 5.7883 | 4.7287 | 7.7295 | 6.7704 | 6.1146 | 8.9859 | 7.9901 | 9.6524 | 9.365 | 10.1103 | 12.9973
| GUESTROOM406_408 PTAC HEAT COIL | 2.799 | 4.9568 | 3.8269 | 5.8544 | 3.1249 | 4.656 | 3.7986 | 6.2315 | 5.4704 | 4.932 | 7.1846 | 6.3978 | 7.717 | 7.4942 | 8.0919 | 10.3897
| GUESTROOM409_412 PTAC HEAT COIL | 3.47 | 6.1428 | 4.7458 | 7.2384 | 3.8776 | 5.764 | 4.7115 | 7.7016 | 6.7436 | 6.0938 | 8.9526 | 7.9579 | 9.6172 | 9.3294 | 10.075 | 12.9568
| GUESTROOM413 PTAC HEAT COIL | 1.0946 | 1.797 | 1.432 | 2.0843 | 1.2026 | 1.7003 | 1.4214 | 2.1953 | 1.9526 | 1.7774 | 2.5235 | 2.2717 | 2.6958 | 2.6251 | 2.8104 | 3.542
| GUESTROOM414 PTAC HEAT COIL | 1.0789 | 1.79 | 1.4258 | 2.0854 | 1.1897 | 1.6974 | 1.4142 | 2.195 | 1.9494 | 1.7715 | 2.526 | 2.2774 | 2.6965 | 2.624 | 2.814 | 3.5509
| GUESTROOM415_418 PTAC HEAT COIL | 3.4606 | 6.1259 | 4.7496 | 7.2422 | 3.8701 | 5.7672 | 4.7136 | 7.6979 | 6.7299 | 6.0871 | 8.9524 | 7.968 | 9.613 | 9.3119 | 10.0752 | 12.9521
| GUESTROOM419 PTAC HEAT COIL | 0.92779 | 1.665 | 1.2872 | 1.9719 | 1.043 | 1.5688 | 1.2751 | 2.0884 | 1.8324 | 1.6452 | 2.4334 | 2.1749 | 2.61 | 2.5358 | 2.7365 | 3.5246
| GUESTROOM420_423 PTAC HEAT COIL | 3.4244 | 6.0804 | 4.709 | 7.1919 | 3.8324 | 5.7225 | 4.6736 | 7.6475 | 6.6812 | 6.0425 | 8.8988 | 7.9157 | 9.5572 | 9.256 | 10.0183 | 12.8884
| GUESTROOM424 PTAC HEAT COIL | 1.0392 | 1.7521 | 1.3977 | 2.0373 | 1.1558 | 1.6612 | 1.3874 | 2.1504 | 1.9073 | 1.7386 | 2.4701 | 2.224 | 2.6359 | 2.5621 | 2.7526 | 3.4791
| LAUNDRYROOMFLR1 PTAC HEAT COIL | 7.0228 | 7.4168 | 6.2575 | 8.0008 | 6.9978 | 6.7646 | 6.4586 | 8.9064 | 7.0766 | 7.7023 | 10.4045 | 8.4474 | 11.2442 | 10.2462 | 11.5093 | 14.9153
| MECHANICALROOMFLR1 PTAC HEAT COIL | 0.37277 | 0.91993 | 0.77161 | 1.134 | 0.58448 | 0.97049 | 0.73218 | 1.2178 | 1.0753 | 0.96171 | 1.5024 | 1.3185 | 1.6696 | 1.6107 | 1.7353 | 2.264
| MEETINGROOMFLR1 PTAC HEAT COIL | 16.8654 | 22.2646 | 18.7845 | 24.0178 | 17.5407 | 20.3066 | 19.3883 | 26.7361 | 21.2433 | 23.1216 | 31.2333 | 25.3584 | 33.754 | 30.7581 | 34.5498 | 42.7845
| REARSTAIRSFLR1 UNIT HEATER COIL | 0.07035 | 1.237 | 0.72193 | 1.7241 | 0.34007 | 1.161 | 0.68512 | 1.9801 | 1.5429 | 1.3059 | 2.8249 | 2.2877 | 3.3002 | 3.1243 | 3.4935 | 4.9985
| REARSTAIRSFLR2 UNIT HEATER COIL | 0.24302 | 1.1491 | 0.67226 | 1.544 | 0.3783 | 1.0288 | 0.65917 | 1.7406 | 1.3622 | 1.1703 | 2.4393 | 1.9864 | 2.8273 | 2.6761 | 2.9815 | 4.2002
| REARSTAIRSFLR3 UNIT HEATER COIL | 0.27472 | 1.1791 | 0.69309 | 1.5752 | 0.40119 | 1.0526 | 0.68207 | 1.7716 | 1.391 | 1.1972 | 2.4721 | 2.0183 | 2.8591 | 2.7074 | 3.0146 | 4.234
| REARSTAIRSFLR4 UNIT HEATER COIL | 0.36451 | 1.3683 | 0.83562 | 1.7992 | 0.50776 | 1.2328 | 0.81833 | 2.0051 | 1.6168 | 1.3756 | 2.729 | 2.2796 | 3.1097 | 2.9729 | 3.2871 | 4.5976
| REARSTORAGEFLR1 UNIT HEATER COIL | 0 | 0.8019 | 0.47107 | 1.148 | 0.19813 | 0.78909 | 0.42921 | 1.2492 | 1.0225 | 0.80358 | 1.7567 | 1.4765 | 2.0334 | 1.9614 | 2.138 | 2.9969
| REARSTORAGEFLR2 UNIT HEATER COIL | 0.19135 | 0.83051 | 0.50256 | 1.1077 | 0.29079 | 0.76087 | 0.48369 | 1.1786 | 0.97283 | 0.79845 | 1.6015 | 1.3595 | 1.8268 | 1.7617 | 1.909 | 2.6018
| REARSTORAGEFLR3 UNIT HEATER COIL | 0.21794 | 0.84946 | 0.51684 | 1.126 | 0.30708 | 0.77456 | 0.49966 | 1.1964 | 0.98887 | 0.81512 | 1.6199 | 1.3769 | 1.8443 | 1.778 | 1.9265 | 2.616
| REARSTORAGEFLR4 UNIT HEATER COIL | 0.22769 | 0.86118 | 0.52534 | 1.1411 | 0.31522 | 0.78589 | 0.50912 | 1.2138 | 1.0051 | 0.83033 | 1.6382 | 1.3946 | 1.8601 | 1.7929 | 1.9447 | 2.6384
| RESTROOMFLR1 PTAC HEAT COIL | 0.17796 | 0.64573 | 0.55185 | 0.82703 | 0.38476 | 0.72231 | 0.50635 | 0.86707 | 0.79421 | 0.67164 | 1.0638 | 0.96028 | 1.1833 | 1.1618 | 1.231 | 1.6131
HVAC Efficiency
Air Conditioning (COP)
| CORRIDORFLR1 PTAC DXCOIL | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02
| CORRIDORFLR2 PTAC DXCOIL | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02
| CORRIDORFLR3 PTAC DXCOIL | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02
| CORRIDORFLR4 PTAC DXCOIL | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02
| EMPLOYEELOUNGEFLR1 PTAC DXCOIL | 2.93 | 2.94 | 2.96 | 2.96 | 3.01 | 3.01 | 3.02 | 2.95 | 3.02 | 3.02 | 2.95 | 3.02 | 2.94 | 3.02 | 2.98 | 3.02
| EXERCISECENTERFLR1 PTAC DXCOIL | 2.91 | 2.91 | 2.91 | 2.91 | 2.92 | 2.91 | 3.23 | 2.91 | 2.99 | 3.18 | 2.91 | 2.98 | 2.91 | 3.23 | 2.92 | 3.23
| FRONTLOUNGEFLR1 PTAC DXCOIL | 2.91 | 2.91 | 2.91 | 2.91 | 2.96 | 2.93 | 3.02 | 2.91 | 3.01 | 3.01 | 2.91 | 3 | 2.91 | 3.02 | 2.92 | 3.02
| FRONTOFFICEFLR1 PTAC DXCOIL | 2.95 | 2.95 | 2.98 | 2.97 | 3.01 | 3.02 | 3.02 | 2.96 | 3.02 | 3.02 | 2.94 | 3.02 | 2.95 | 3.02 | 2.98 | 3.02
| GUESTROOM101 PTAC DXCOIL | 3.17 | 3.17 | 3.2 | 3.2 | 3.23 | 3.23 | 3.23 | 3.19 | 3.23 | 3.23 | 3.18 | 3.23 | 3.2 | 3.23 | 3.23 | 3.23
| GUESTROOM102 PTAC DXCOIL | 3.17 | 2.97 | 2.99 | 3.2 | 3.23 | 3.23 | 3.23 | 3.2 | 3.23 | 3.23 | 3.19 | 3.23 | 3.2 | 3.23 | 3.23 | 3.23
| GUESTROOM103 PTAC DXCOIL | 2.98 | 2.98 | 3 | 3 | 3.23 | 3.02 | 3.23 | 3 | 3.23 | 3.23 | 3.19 | 3.23 | 3.2 | 3.23 | 3.23 | 3.23
| GUESTROOM104 PTAC DXCOIL | 3.19 | 3.2 | 3.23 | 3.22 | 3.23 | 3.23 | 3.23 | 3.2 | 3.23 | 3.23 | 3.18 | 3.23 | 3.19 | 3.23 | 3.22 | 3.23
| GUESTROOM105 PTAC DXCOIL | 3.19 | 3.19 | 3.22 | 3.22 | 3.23 | 3.23 | 3.23 | 3.2 | 3.23 | 3.23 | 3.18 | 3.23 | 3.19 | 3.23 | 3.23 | 3.23
| GUESTROOM201 PTAC DXCOIL | 3 | 3 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.01 | 3.02 | 3.02 | 3.01 | 3.02 | 3.01 | 3.02 | 3.02 | 3.02
| GUESTROOM202_205 PTAC DXCOIL | 2.98 | 2.98 | 3.01 | 3.01 | 3.02 | 3.02 | 3.02 | 3 | 3.02 | 3.02 | 2.99 | 3.02 | 3.01 | 3.02 | 3.02 | 3.02
| GUESTROOM206_208 PTAC DXCOIL | 2.98 | 2.99 | 3.01 | 3.01 | 3.02 | 3.02 | 3.02 | 3.01 | 3.02 | 3.02 | 3 | 3.02 | 3.01 | 3.02 | 3.02 | 3.02
| GUESTROOM209_212 PTAC DXCOIL | 2.98 | 2.98 | 3 | 3 | 3.02 | 3.02 | 3.02 | 3 | 3.02 | 3.02 | 2.99 | 3.02 | 3 | 3.02 | 3.02 | 3.02
| GUESTROOM213 PTAC DXCOIL | 2.99 | 2.99 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.01 | 3.02 | 3.02 | 3 | 3.02 | 3.01 | 3.02 | 3.23 | 3.23
| GUESTROOM214 PTAC DXCOIL | 3 | 3.01 | 3.02 | 3.02 | 3.23 | 3.02 | 3.23 | 3.23 | 3.02 | 3.23 | 3.23 | 3.23 | 3.22 | 3.23 | 3.23 | 3.23
| GUESTROOM215_218 PTAC DXCOIL | 2.99 | 3 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.01 | 3.02 | 3.02 | 2.99 | 3.02 | 3 | 3.02 | 3.02 | 3.02
| GUESTROOM219 PTAC DXCOIL | 3.01 | 3.02 | 3.02 | 3.02 | 3.23 | 3.02 | 3.23 | 3.02 | 3.02 | 3.23 | 3.01 | 3.02 | 3.02 | 3.02 | 3.02 | 3.23
| GUESTROOM220_223 PTAC DXCOIL | 2.99 | 2.99 | 3.02 | 3.01 | 3.02 | 3.02 | 3.02 | 3 | 3.02 | 3.02 | 2.99 | 3.02 | 3 | 3.02 | 3.02 | 3.02
| GUESTROOM224 PTAC DXCOIL | 3 | 3 | 3.02 | 3.02 | 3.23 | 3.02 | 3.23 | 3.22 | 3.02 | 3.23 | 3.22 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM301 PTAC DXCOIL | 3 | 3 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.01 | 3.02 | 3.02 | 3.01 | 3.02 | 3.01 | 3.02 | 3.02 | 3.02
| GUESTROOM302_305 PTAC DXCOIL | 2.98 | 2.98 | 3.01 | 3.01 | 3.02 | 3.02 | 3.02 | 3 | 3.02 | 3.02 | 3 | 3.02 | 3.01 | 3.02 | 3.02 | 3.02
| GUESTROOM306_308 PTAC DXCOIL | 2.98 | 2.99 | 3.01 | 3.01 | 3.02 | 3.02 | 3.02 | 3.01 | 3.02 | 3.02 | 3 | 3.02 | 3.01 | 3.02 | 3.02 | 3.02
| GUESTROOM309_312 PTAC DXCOIL | 2.98 | 2.98 | 3.01 | 3.01 | 3.02 | 3.02 | 3.02 | 3 | 3.02 | 3.02 | 3 | 3.02 | 3.01 | 3.02 | 3.02 | 3.02
| GUESTROOM313 PTAC DXCOIL | 2.99 | 2.99 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.01 | 3.02 | 3.02 | 3 | 3.02 | 3.01 | 3.02 | 3.23 | 3.02
| GUESTROOM314 PTAC DXCOIL | 3 | 3.01 | 3.02 | 3.02 | 3.23 | 3.02 | 3.23 | 3.23 | 3.02 | 3.23 | 3.23 | 3.23 | 3.22 | 3.23 | 3.23 | 3.23
| GUESTROOM315_318 PTAC DXCOIL | 2.99 | 3 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.01 | 3.02 | 3.02 | 2.99 | 3.02 | 3 | 3.02 | 3.02 | 3.02
| GUESTROOM319 PTAC DXCOIL | 3 | 3 | 3.02 | 3.23 | 3.23 | 3.02 | 3.23 | 3.22 | 3.02 | 3.23 | 3.22 | 3.23 | 3.21 | 3.23 | 3.23 | 3.23
| GUESTROOM320_323 PTAC DXCOIL | 2.99 | 2.99 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3 | 3.02 | 3.02 | 2.99 | 3.02 | 3 | 3.02 | 3.02 | 3.02
| GUESTROOM324 PTAC DXCOIL | 3 | 3.01 | 3.02 | 3.02 | 3.23 | 3.02 | 3.23 | 3.23 | 3.02 | 3.23 | 3.22 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM401 PTAC DXCOIL | 3.01 | 3.01 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.01 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02
| GUESTROOM402_405 PTAC DXCOIL | 3 | 3 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3 | 3.02 | 3.02 | 3 | 3.02 | 3.01 | 3.02 | 3.02 | 3.02
| GUESTROOM406_408 PTAC DXCOIL | 3 | 3 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.01 | 3.02 | 3.02 | 3.01 | 3.02 | 3.01 | 3.02 | 3.02 | 3.02
| GUESTROOM409_412 PTAC DXCOIL | 2.99 | 3 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3 | 3.02 | 3.02 | 3 | 3.02 | 3.01 | 3.02 | 3.02 | 3.02
| GUESTROOM413 PTAC DXCOIL | 3.01 | 3.01 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.01 | 3.02 | 3.02 | 3.01 | 3.02 | 3.02 | 3.02 | 3.23 | 3.02
| GUESTROOM414 PTAC DXCOIL | 3.02 | 3.02 | 3.02 | 3.02 | 3.23 | 3.02 | 3.23 | 3.02 | 3.02 | 3.23 | 3.02 | 3.02 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM415_418 PTAC DXCOIL | 3 | 3.01 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02
| GUESTROOM419 PTAC DXCOIL | 3.01 | 3.01 | 3.02 | 3.02 | 3.23 | 3.02 | 3.23 | 3.02 | 3.02 | 3.23 | 3.23 | 3.02 | 3.23 | 3.23 | 3.23 | 3.23
| GUESTROOM420_423 PTAC DXCOIL | 3 | 3.01 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.01 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02
| GUESTROOM424 PTAC DXCOIL | 3.01 | 3.02 | 3.02 | 3.02 | 3.23 | 3.02 | 3.23 | 3.02 | 3.02 | 3.23 | 3.02 | 3.02 | 3.23 | 3.23 | 3.23 | 3.23
| LAUNDRYROOMFLR1 PTAC DXCOIL | 3 | 3 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02 | 3.02
| MECHANICALROOMFLR1 PTAC DXCOIL | 3.16 | 3.16 | 3.2 | 3.19 | 3.23 | 3.23 | 3.23 | 3.18 | 3.23 | 3.23 | 3.18 | 3.23 | 3.19 | 3.23 | 3.22 | 3.23
| MEETINGROOMFLR1 PTAC DXCOIL | 2.91 | 2.91 | 2.91 | 2.91 | 2.92 | 2.91 | 3.01 | 2.91 | 2.96 | 2.97 | 2.91 | 2.95 | 2.91 | 2.99 | 2.91 | 3.02
| RESTROOMFLR1 PTAC DXCOIL | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23 | 3.23
Heating Efficiency (%)
| CORRIDORFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| CORRIDORFLR2 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| CORRIDORFLR3 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| CORRIDORFLR4 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| EXERCISECENTERFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTLOUNGEFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTOFFICEFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM101 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM102 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM103 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM104 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM105 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM201 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM202_205 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM206_208 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM209_212 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM213 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM214 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM215_218 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM219 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM220_223 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM224 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM301 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM302_305 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM306_308 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM309_312 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM313 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM314 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM315_318 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM319 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM320_323 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM324 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM401 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM402_405 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM406_408 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM409_412 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM413 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM414 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM415_418 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM419 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM420_423 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM424 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| LAUNDRYROOMFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| MECHANICALROOMFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| MEETINGROOMFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| RESTROOMFLR1 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HVAC Control - Economizer
| All Systems | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| CORRIDORFLR1 PTACFAN | 0.62 | 0.63 | 0.63 | 0.64 | 0.56 | 0.61 | 0.48 | 0.6 | 0.64 | 0.53 | 0.57 | 0.6 | 0.57 | 0.57 | 0.51 | 0.44
| CORRIDORFLR2 PTACFAN | 0.35 | 0.36 | 0.39 | 0.37 | 0.32 | 0.39 | 0.31 | 0.35 | 0.38 | 0.33 | 0.32 | 0.34 | 0.32 | 0.33 | 0.3 | 0.28
| CORRIDORFLR3 PTACFAN | 0.33 | 0.34 | 0.38 | 0.34 | 0.3 | 0.37 | 0.29 | 0.32 | 0.35 | 0.3 | 0.3 | 0.31 | 0.3 | 0.3 | 0.28 | 0.26
| CORRIDORFLR4 PTACFAN | 0.43 | 0.45 | 0.51 | 0.45 | 0.37 | 0.49 | 0.34 | 0.4 | 0.43 | 0.36 | 0.36 | 0.37 | 0.33 | 0.33 | 0.31 | 0.28
| EMPLOYEELOUNGEFLR1 PTACFAN | 0.35 | 0.35 | 0.36 | 0.36 | 0.33 | 0.37 | 0.31 | 0.34 | 0.4 | 0.32 | 0.34 | 0.38 | 0.34 | 0.36 | 0.33 | 0.3
| EXERCISECENTERFLR1 PTACFAN | 0.16 | 0.16 | 0.16 | 0.16 | 0.14 | 0.16 | 0.12 | 0.15 | 0.16 | 0.13 | 0.14 | 0.15 | 0.15 | 0.15 | 0.13 | 0.12
| FRONTLOUNGEFLR1 PTACFAN | 0.91 | 0.97 | 1.05 | 1.02 | 1 | 1.07 | 1.08 | 1.01 | 1.05 | 1.08 | 0.9 | 0.95 | 0.9 | 0.95 | 0.84 | 0.88
| FRONTOFFICEFLR1 PTACFAN | 0.53 | 0.53 | 0.53 | 0.52 | 0.43 | 0.52 | 0.36 | 0.48 | 0.51 | 0.4 | 0.45 | 0.47 | 0.45 | 0.44 | 0.39 | 0.33
| FRONTSTAIRSFLR1 UNIT HEATERFAN | 0 | 0.05 | 0.03 | 0.06 | 0.01 | 0.05 | 0.03 | 0.07 | 0.07 | 0.05 | 0.1 | 0.1 | 0.12 | 0.13 | 0.13 | 0.17
| FRONTSTAIRSFLR2 UNIT HEATERFAN | 0.01 | 0.04 | 0.03 | 0.06 | 0.02 | 0.04 | 0.03 | 0.06 | 0.06 | 0.04 | 0.09 | 0.09 | 0.1 | 0.11 | 0.11 | 0.15
| FRONTSTAIRSFLR3 UNIT HEATERFAN | 0.01 | 0.04 | 0.03 | 0.06 | 0.02 | 0.04 | 0.03 | 0.07 | 0.06 | 0.05 | 0.09 | 0.09 | 0.1 | 0.11 | 0.11 | 0.15
| FRONTSTAIRSFLR4 UNIT HEATERFAN | 0.02 | 0.05 | 0.03 | 0.07 | 0.02 | 0.05 | 0.03 | 0.07 | 0.07 | 0.05 | 0.1 | 0.1 | 0.11 | 0.12 | 0.12 | 0.16
| FRONTSTORAGEFLR1 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01
| FRONTSTORAGEFLR2 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01
| FRONTSTORAGEFLR3 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01
| FRONTSTORAGEFLR4 UNIT HEATERFAN | 0 | 0 | 0 | 0.01 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.02
| GUESTROOM101 PTACFAN | 0.12 | 0.13 | 0.14 | 0.14 | 0.14 | 0.14 | 0.15 | 0.14 | 0.14 | 0.15 | 0.12 | 0.13 | 0.13 | 0.13 | 0.11 | 0.12
| GUESTROOM102 PTACFAN | 0.13 | 0.14 | 0.15 | 0.15 | 0.14 | 0.15 | 0.15 | 0.14 | 0.15 | 0.15 | 0.13 | 0.13 | 0.13 | 0.13 | 0.12 | 0.12
| GUESTROOM103 PTACFAN | 0.14 | 0.15 | 0.16 | 0.16 | 0.15 | 0.16 | 0.15 | 0.15 | 0.15 | 0.16 | 0.14 | 0.13 | 0.14 | 0.14 | 0.12 | 0.12
| GUESTROOM104 PTACFAN | 0.14 | 0.14 | 0.15 | 0.14 | 0.11 | 0.14 | 0.09 | 0.13 | 0.13 | 0.1 | 0.12 | 0.11 | 0.12 | 0.11 | 0.1 | 0.09
| GUESTROOM105 PTACFAN | 0.14 | 0.14 | 0.14 | 0.14 | 0.11 | 0.14 | 0.1 | 0.13 | 0.14 | 0.11 | 0.12 | 0.12 | 0.12 | 0.12 | 0.1 | 0.09
| GUESTROOM201 PTACFAN | 0.23 | 0.24 | 0.27 | 0.25 | 0.22 | 0.28 | 0.23 | 0.22 | 0.24 | 0.22 | 0.21 | 0.22 | 0.2 | 0.21 | 0.19 | 0.18
| GUESTROOM202_205 PTACFAN | 0.54 | 0.58 | 0.66 | 0.62 | 0.61 | 0.68 | 0.69 | 0.62 | 0.67 | 0.69 | 0.57 | 0.62 | 0.58 | 0.62 | 0.56 | 0.61
| GUESTROOM206_208 PTACFAN | 0.43 | 0.48 | 0.54 | 0.51 | 0.5 | 0.56 | 0.58 | 0.51 | 0.55 | 0.57 | 0.46 | 0.5 | 0.47 | 0.51 | 0.46 | 0.5
| GUESTROOM209_212 PTACFAN | 0.52 | 0.57 | 0.65 | 0.61 | 0.6 | 0.66 | 0.68 | 0.6 | 0.65 | 0.67 | 0.55 | 0.61 | 0.56 | 0.61 | 0.55 | 0.59
| GUESTROOM213 PTACFAN | 0.15 | 0.16 | 0.19 | 0.17 | 0.16 | 0.19 | 0.18 | 0.17 | 0.18 | 0.18 | 0.16 | 0.16 | 0.16 | 0.16 | 0.15 | 0.16
| GUESTROOM214 PTACFAN | 0.16 | 0.16 | 0.18 | 0.16 | 0.13 | 0.18 | 0.12 | 0.15 | 0.16 | 0.13 | 0.14 | 0.15 | 0.14 | 0.14 | 0.13 | 0.12
| GUESTROOM215_218 PTACFAN | 0.59 | 0.59 | 0.64 | 0.6 | 0.51 | 0.64 | 0.48 | 0.57 | 0.64 | 0.52 | 0.54 | 0.6 | 0.54 | 0.57 | 0.52 | 0.48
| GUESTROOM219 PTACFAN | 0.18 | 0.18 | 0.19 | 0.18 | 0.16 | 0.19 | 0.15 | 0.17 | 0.2 | 0.16 | 0.17 | 0.19 | 0.17 | 0.18 | 0.16 | 0.15
| GUESTROOM220_223 PTACFAN | 0.55 | 0.55 | 0.6 | 0.56 | 0.47 | 0.6 | 0.45 | 0.53 | 0.6 | 0.48 | 0.5 | 0.55 | 0.5 | 0.53 | 0.48 | 0.45
| GUESTROOM224 PTACFAN | 0.16 | 0.16 | 0.17 | 0.16 | 0.13 | 0.17 | 0.12 | 0.15 | 0.16 | 0.13 | 0.14 | 0.15 | 0.14 | 0.14 | 0.13 | 0.12
| GUESTROOM301 PTACFAN | 0.23 | 0.24 | 0.27 | 0.25 | 0.22 | 0.27 | 0.23 | 0.22 | 0.24 | 0.22 | 0.21 | 0.22 | 0.2 | 0.21 | 0.18 | 0.17
| GUESTROOM302_305 PTACFAN | 0.54 | 0.57 | 0.66 | 0.62 | 0.61 | 0.68 | 0.69 | 0.62 | 0.67 | 0.69 | 0.57 | 0.63 | 0.58 | 0.63 | 0.57 | 0.62
| GUESTROOM306_308 PTACFAN | 0.44 | 0.47 | 0.55 | 0.51 | 0.51 | 0.56 | 0.59 | 0.51 | 0.55 | 0.58 | 0.47 | 0.51 | 0.48 | 0.52 | 0.47 | 0.52
| GUESTROOM309_312 PTACFAN | 0.53 | 0.57 | 0.66 | 0.62 | 0.61 | 0.68 | 0.69 | 0.61 | 0.67 | 0.69 | 0.57 | 0.62 | 0.58 | 0.63 | 0.57 | 0.61
| GUESTROOM313 PTACFAN | 0.15 | 0.16 | 0.19 | 0.18 | 0.16 | 0.19 | 0.18 | 0.17 | 0.18 | 0.18 | 0.16 | 0.16 | 0.16 | 0.17 | 0.15 | 0.16
| GUESTROOM314 PTACFAN | 0.16 | 0.17 | 0.19 | 0.17 | 0.13 | 0.18 | 0.12 | 0.16 | 0.17 | 0.14 | 0.15 | 0.15 | 0.15 | 0.15 | 0.13 | 0.12
| GUESTROOM315_318 PTACFAN | 0.57 | 0.57 | 0.62 | 0.58 | 0.48 | 0.63 | 0.47 | 0.55 | 0.62 | 0.5 | 0.52 | 0.57 | 0.52 | 0.55 | 0.5 | 0.47
| GUESTROOM319 PTACFAN | 0.15 | 0.15 | 0.17 | 0.15 | 0.13 | 0.17 | 0.12 | 0.15 | 0.16 | 0.13 | 0.14 | 0.15 | 0.14 | 0.15 | 0.13 | 0.12
| GUESTROOM320_323 PTACFAN | 0.56 | 0.56 | 0.61 | 0.57 | 0.48 | 0.62 | 0.46 | 0.54 | 0.61 | 0.49 | 0.51 | 0.56 | 0.51 | 0.54 | 0.49 | 0.46
| GUESTROOM324 PTACFAN | 0.16 | 0.16 | 0.18 | 0.16 | 0.13 | 0.18 | 0.12 | 0.15 | 0.16 | 0.13 | 0.14 | 0.15 | 0.14 | 0.14 | 0.13 | 0.12
| GUESTROOM401 PTACFAN | 0.25 | 0.26 | 0.3 | 0.27 | 0.23 | 0.29 | 0.23 | 0.23 | 0.25 | 0.22 | 0.22 | 0.23 | 0.2 | 0.21 | 0.19 | 0.2
| GUESTROOM402_405 PTACFAN | 0.63 | 0.65 | 0.73 | 0.67 | 0.6 | 0.72 | 0.7 | 0.62 | 0.68 | 0.69 | 0.59 | 0.63 | 0.57 | 0.6 | 0.55 | 0.61
| GUESTROOM406_408 PTACFAN | 0.52 | 0.54 | 0.6 | 0.55 | 0.49 | 0.6 | 0.59 | 0.51 | 0.56 | 0.59 | 0.48 | 0.52 | 0.47 | 0.5 | 0.45 | 0.51
| GUESTROOM409_412 PTACFAN | 0.63 | 0.65 | 0.73 | 0.67 | 0.6 | 0.72 | 0.7 | 0.62 | 0.68 | 0.69 | 0.59 | 0.63 | 0.57 | 0.6 | 0.55 | 0.61
| GUESTROOM413 PTACFAN | 0.18 | 0.18 | 0.21 | 0.19 | 0.16 | 0.21 | 0.18 | 0.17 | 0.18 | 0.19 | 0.16 | 0.17 | 0.16 | 0.16 | 0.15 | 0.16
| GUESTROOM414 PTACFAN | 0.19 | 0.19 | 0.22 | 0.19 | 0.15 | 0.21 | 0.14 | 0.18 | 0.19 | 0.15 | 0.16 | 0.17 | 0.16 | 0.15 | 0.14 | 0.13
| GUESTROOM415_418 PTACFAN | 0.65 | 0.66 | 0.73 | 0.67 | 0.56 | 0.73 | 0.52 | 0.62 | 0.69 | 0.55 | 0.58 | 0.62 | 0.56 | 0.57 | 0.53 | 0.49
| GUESTROOM419 PTACFAN | 0.17 | 0.17 | 0.19 | 0.18 | 0.14 | 0.19 | 0.13 | 0.16 | 0.18 | 0.14 | 0.15 | 0.16 | 0.14 | 0.15 | 0.14 | 0.13
| GUESTROOM420_423 PTACFAN | 0.64 | 0.66 | 0.72 | 0.66 | 0.55 | 0.72 | 0.52 | 0.61 | 0.68 | 0.55 | 0.57 | 0.62 | 0.55 | 0.57 | 0.52 | 0.49
| GUESTROOM424 PTACFAN | 0.18 | 0.19 | 0.21 | 0.19 | 0.15 | 0.2 | 0.14 | 0.17 | 0.18 | 0.15 | 0.16 | 0.16 | 0.15 | 0.15 | 0.14 | 0.13
| LAUNDRYROOMFLR1 PTACFAN | 1.7 | 1.69 | 1.74 | 1.74 | 1.65 | 1.78 | 1.57 | 1.68 | 1.96 | 1.63 | 1.69 | 1.95 | 1.7 | 1.84 | 1.68 | 1.59
| MECHANICALROOMFLR1 PTACFAN | 0.06 | 0.07 | 0.08 | 0.08 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.06 | 0.07 | 0.06 | 0.06 | 0.07
| MEETINGROOMFLR1 PTACFAN | 0.5 | 0.52 | 0.55 | 0.55 | 0.54 | 0.56 | 0.56 | 0.54 | 0.58 | 0.57 | 0.5 | 0.55 | 0.51 | 0.54 | 0.48 | 0.49
| REARSTAIRSFLR1 UNIT HEATERFAN | 0 | 0.04 | 0.03 | 0.06 | 0.01 | 0.04 | 0.02 | 0.07 | 0.06 | 0.04 | 0.1 | 0.09 | 0.11 | 0.12 | 0.12 | 0.17
| REARSTAIRSFLR2 UNIT HEATERFAN | 0.01 | 0.04 | 0.02 | 0.05 | 0.01 | 0.04 | 0.02 | 0.06 | 0.06 | 0.04 | 0.08 | 0.08 | 0.1 | 0.1 | 0.1 | 0.14
| REARSTAIRSFLR3 UNIT HEATERFAN | 0.01 | 0.04 | 0.02 | 0.05 | 0.01 | 0.04 | 0.02 | 0.06 | 0.06 | 0.04 | 0.08 | 0.08 | 0.1 | 0.1 | 0.11 | 0.14
| REARSTAIRSFLR4 UNIT HEATERFAN | 0.01 | 0.05 | 0.03 | 0.06 | 0.02 | 0.04 | 0.03 | 0.07 | 0.07 | 0.05 | 0.09 | 0.09 | 0.11 | 0.11 | 0.12 | 0.16
| REARSTORAGEFLR1 UNIT HEATERFAN | 0 | 0.03 | 0.02 | 0.04 | 0.01 | 0.03 | 0.01 | 0.04 | 0.04 | 0.03 | 0.06 | 0.06 | 0.07 | 0.08 | 0.08 | 0.1
| REARSTORAGEFLR2 UNIT HEATERFAN | 0.01 | 0.03 | 0.02 | 0.04 | 0.01 | 0.03 | 0.02 | 0.04 | 0.04 | 0.03 | 0.05 | 0.06 | 0.06 | 0.07 | 0.07 | 0.09
| REARSTORAGEFLR3 UNIT HEATERFAN | 0.01 | 0.03 | 0.02 | 0.04 | 0.01 | 0.03 | 0.02 | 0.04 | 0.04 | 0.03 | 0.06 | 0.06 | 0.06 | 0.07 | 0.07 | 0.09
| REARSTORAGEFLR4 UNIT HEATERFAN | 0.01 | 0.03 | 0.02 | 0.04 | 0.01 | 0.03 | 0.02 | 0.04 | 0.04 | 0.03 | 0.06 | 0.06 | 0.06 | 0.07 | 0.07 | 0.09
| RESTROOMFLR1 PTACFAN | 0.1 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.1 | 0.1 | 0.11 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.09 | 0.08
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.078751 | 0.10812 | 0.087182 | 0.10024 | 0.12304 | 0.094712 | 0.1452 | 0.069772 | 0.037198 | 0.071689 | 0.096345 | 0.037205 | 0.05639 | 0.073054 | 0.056896 | 0.093319
| Total Cost ($/m2) | 13.54 | 17.16 | 13.94 | 14.74 | 17.07 | 14.25 | 18.58 | 10.05 | 5.2 | 9.22 | 13.72 | 5.07 | 8.47 | 10.11 | 8.52 | 17.22
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011458 | 0.008197 | 0.0085966 | 0.010897 | 0.0083934 | 0.0081604 | 0.0083928 | 0.010143 | 0.0072354 | 0.0082692 | 0.0090367 | 0.0072434 | 0.008011 | 0.0089075 | 0.0080168 | 0.0042309
| Total Cost ($/m2) | 1.28 | 1.04 | 1.02 | 1.54 | 1.16 | 1.05 | 1.27 | 1.55 | 1.09 | 1.32 | 1.48 | 1.18 | 1.38 | 1.55 | 1.5 | 0.86
Total Utility Costs
| Cost Intensity ($/m2) | 14.82 | 18.2 | 14.96 | 16.28 | 18.24 | 15.3 | 19.85 | 11.6 | 6.29 | 10.53 | 15.19 | 6.25 | 9.85 | 11.65 | 10.01 | 18.08
Energy - End Uses
Electricity (kWh)
| Heating | 16.6667 | 8405.5556 | 2269.4444 | 23855.5556 | 172.2222 | 7122.2222 | 3266.6667 | 45897.2222 | 22250 | 24238.8889 | 65333.3333 | 40394.4444 | 110166.6667 | 72816.6667 | 144847.2222 | 336041.6667
| Cooling | 298616.6667 | 230050 | 239505.5556 | 160477.7778 | 143722.2222 | 190527.7778 | 92027.7778 | 127108.3333 | 127483.3333 | 75825 | 101969.4444 | 94977.7778 | 96230.5556 | 75433.3333 | 62508.3333 | 47266.6667
| Interior Lighting | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667
| Exterior Lighting | 46566.6667 | 46483.3333 | 46472.2222 | 46547.2222 | 46541.6667 | 46494.4444 | 46444.4444 | 46491.6667 | 46483.3333 | 46416.6667 | 46427.7778 | 46436.1111 | 46466.6667 | 46411.1111 | 46397.2222 | 46119.4444
| Interior Equipment | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 33813.8889 | 26708.3333 | 29730.5556 | 21127.7778 | 19313.8889 | 25380.5556 | 12880.5556 | 17205.5556 | 18938.8889 | 11441.6667 | 14483.3333 | 14888.8889 | 15186.1111 | 12972.2222 | 12152.7778 | 13977.7778
| Pumps | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 877691.6667 | 810325 | 816652.7778 | 750686.1111 | 708427.7778 | 768202.7778 | 653294.4444 | 735380.5556 | 713833.3333 | 656594.4444 | 726891.6667 | 695375 | 766725 | 706308.3333 | 764580.5556 | 942080.5556
Gas (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 380710 | 458600 | 413870 | 533680 | 519110 | 467800 | 583300 | 592670 | 581500 | 623360 | 644440 | 641740 | 689170 | 697310 | 762990 | 852320
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 570190 | 648080 | 603350 | 723150 | 708590 | 657280 | 772780 | 782150 | 770980 | 812830 | 833920 | 831220 | 878650 | 886790 | 952470 | 1041800
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 3729890 | 3565250 | 3543300 | 3425620 | 3258920 | 3422810 | 3124640 | 3429520 | 3340780 | 3176570 | 3450730 | 3334560 | 3638860 | 3429500 | 3704970 | 4433290
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0.01175 | 5.9261 | 1.6 | 16.8187 | 0.12142 | 5.0213 | 2.3031 | 32.3586 | 15.6868 | 17.089 | 46.0616 | 28.479 | 77.6701 | 51.3375 | 102.1208 | 236.9174
| Cooling (elec) | 210.5319 | 162.1907 | 168.8571 | 113.1407 | 101.3276 | 134.3266 | 64.8818 | 89.6144 | 89.8788 | 53.4584 | 71.8909 | 66.9616 | 67.8448 | 53.1823 | 44.0699 | 33.3241
| Interior Lighting (elec) | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898
| Exterior Lighting (elec) | 32.8306 | 32.7719 | 32.764 | 32.8169 | 32.813 | 32.7797 | 32.7444 | 32.7777 | 32.7719 | 32.7249 | 32.7327 | 32.7386 | 32.7601 | 32.7209 | 32.7111 | 32.5153
| Interior Equipment (elec) | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 23.8396 | 18.83 | 20.9608 | 14.8956 | 13.6168 | 17.8939 | 9.0811 | 12.1303 | 13.3524 | 8.0666 | 10.2111 | 10.497 | 10.7066 | 9.1457 | 8.568 | 9.8547
| Pumps (elec) | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 618.7936 | 571.2985 | 575.7597 | 529.2516 | 499.4585 | 541.6013 | 460.5882 | 518.4609 | 503.2695 | 462.9148 | 512.476 | 490.256 | 540.5594 | 497.9642 | 539.0476 | 664.1893
Gas (MJ/m2)
| Heating (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 74.5582 | 89.8122 | 81.0523 | 104.5159 | 101.6625 | 91.6139 | 114.2335 | 116.0685 | 113.8809 | 122.0788 | 126.2071 | 125.6783 | 134.967 | 136.5612 | 149.4239 | 166.9183
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 111.666 | 126.92 | 118.16 | 141.6217 | 138.7702 | 128.7217 | 151.3412 | 153.1762 | 150.9887 | 159.1846 | 163.3149 | 162.7861 | 172.0748 | 173.6689 | 186.5317 | 204.0261
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 730.4615 | 698.2184 | 693.9198 | 670.8733 | 638.2268 | 670.323 | 611.9294 | 671.6371 | 654.2582 | 622.0994 | 675.7909 | 653.0401 | 712.6342 | 671.6332 | 725.5812 | 868.2154
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 148.3076 | 158.6312 | 131.6349 | 167.265 | 129.151 | 118.3624 | 120.4084 | 188.7134 | 141.1876 | 120.3192 | 213.8419 | 185.7052 | 239.434 | 217.7847 | 250.0438 | 353.9494
| Feb | 151.6899 | 137.7708 | 131.5205 | 167.0902 | 130.289 | 125.1679 | 127.666 | 150.0241 | 121.5971 | 119.5903 | 157.6295 | 162.5046 | 220.4812 | 203.2877 | 249.2034 | 338.6086
| Mar | 154.5495 | 148.8122 | 149.5569 | 136.8154 | 128.643 | 130.1216 | 123.1301 | 130.4895 | 126.1943 | 128.5565 | 125.3731 | 127.5881 | 145.2961 | 151.9569 | 203.8183 | 252.7142
| Apr | 159.511 | 158.3083 | 150.3089 | 146.7209 | 133.8779 | 147.6205 | 130.2151 | 134.7428 | 135.9685 | 129.4372 | 126.2701 | 133.1972 | 134.6384 | 125.7907 | 120.7924 | 152.3256
| May | 163.7475 | 170.9018 | 173.568 | 160.077 | 139.4109 | 155.7264 | 132.3014 | 145.9314 | 143.5964 | 135.1007 | 141.5467 | 140.4556 | 157.2098 | 132.9724 | 130.8142 | 120.7762
| Jun | 176.9238 | 168.256 | 198.7448 | 163.1736 | 138.2809 | 188.4655 | 133.5802 | 164.704 | 151.8145 | 137.0199 | 152.3195 | 143.837 | 156.6476 | 145.6239 | 146.0665 | 129.6089
| Jul | 170.3435 | 176.2599 | 193.5588 | 173.6018 | 141.4099 | 184.0765 | 150.2206 | 172.7785 | 161.4051 | 144.2823 | 161.8477 | 151.335 | 162.5402 | 141.1385 | 152.229 | 135.6114
| Aug | 171.3447 | 182.8112 | 198.1943 | 164.5161 | 143.4553 | 178.021 | 133.4053 | 174.0476 | 158.1694 | 144.6127 | 166.8625 | 147.9752 | 161.8754 | 145.1399 | 153.4074 | 128.942
| Sep | 166.1049 | 167.2118 | 180.1391 | 155.8789 | 142.29 | 163.047 | 142.0715 | 149.1504 | 146.1028 | 149.823 | 145.6925 | 141.0954 | 141.7002 | 141.7821 | 138.0641 | 123.4681
| Oct | 164.4431 | 158.5911 | 154.0727 | 145.6178 | 137.8728 | 143.6152 | 132.401 | 142.7177 | 137.3121 | 130.2247 | 135.5272 | 135.2841 | 137.1624 | 129.1039 | 131.6373 | 168.7044
| Nov | 155.8492 | 147.7074 | 135.5971 | 130.573 | 132.3251 | 128.3074 | 124.872 | 137.5504 | 125.2225 | 126.6155 | 134.9455 | 123.6094 | 141.5455 | 128.1599 | 187.3595 | 232.0892
| Dec | 148.3019 | 146.4011 | 131.0496 | 153.4969 | 129.3045 | 121.9828 | 119.4962 | 159.9281 | 138.9903 | 123.9434 | 192.2331 | 173.2218 | 249.3894 | 225.5628 | 243.9861 | 295.2434
Time of Peak Electrical Demand
| Jan | 06-JAN-20:00 | 14-JAN-06:15 | 29-JAN-20:15 | 14-JAN-07:15 | 26-JAN-20:30 | 18-JAN-20:30 | 15-JAN-20:15 | 31-JAN-07:15 | 04-JAN-07:15 | 02-JAN-07:00 | 07-JAN-06:15 | 06-JAN-06:15 | 06-JAN-06:15 | 07-JAN-06:15 | 09-JAN-07:15 | 13-JAN-06:15
| Feb | 20-FEB-08:00 | 20-FEB-20:30 | 28-FEB-20:15 | 10-FEB-07:15 | 12-FEB-20:30 | 27-FEB-20:15 | 15-FEB-20:15 | 01-FEB-07:15 | 14-FEB-20:15 | 21-FEB-20:45 | 09-FEB-06:15 | 16-FEB-06:15 | 04-FEB-06:15 | 26-FEB-06:15 | 02-FEB-07:15 | 05-FEB-06:15
| Mar | 13-MAR-19:15 | 26-MAR-19:15 | 17-MAR-19:15 | 28-MAR-19:15 | 04-MAR-20:00 | 31-MAR-19:00 | 30-MAR-19:30 | 09-MAR-20:00 | 20-MAR-19:15 | 29-MAR-19:00 | 14-MAR-19:00 | 26-MAR-19:15 | 05-MAR-21:00 | 04-MAR-06:15 | 09-MAR-06:15 | 14-MAR-06:00
| Apr | 01-APR-19:15 | 30-APR-19:15 | 02-APR-19:15 | 15-APR-19:15 | 11-APR-19:15 | 21-APR-19:15 | 29-APR-19:15 | 05-APR-19:15 | 22-APR-19:15 | 29-APR-19:15 | 28-APR-19:30 | 25-APR-19:30 | 02-APR-19:00 | 30-APR-19:30 | 15-APR-19:15 | 09-APR-05:15
| May | 15-MAY-19:15 | 26-MAY-19:15 | 28-MAY-19:30 | 14-MAY-19:30 | 29-MAY-19:15 | 31-MAY-19:15 | 25-MAY-19:15 | 15-MAY-19:15 | 30-MAY-19:15 | 04-MAY-19:30 | 30-MAY-19:15 | 23-MAY-19:15 | 27-MAY-19:45 | 25-MAY-19:00 | 31-MAY-19:00 | 29-MAY-19:00
| Jun | 27-JUN-19:15 | 13-JUN-19:30 | 27-JUN-19:45 | 19-JUN-19:00 | 28-JUN-19:15 | 27-JUN-19:15 | 16-JUN-19:30 | 30-JUN-19:45 | 28-JUN-19:30 | 17-JUN-20:15 | 16-JUN-19:30 | 27-JUN-19:30 | 29-JUN-19:00 | 25-JUN-20:30 | 14-JUN-19:00 | 23-JUN-19:00
| Jul | 04-JUL-19:15 | 03-JUL-19:30 | 11-JUL-19:45 | 02-JUL-19:00 | 10-JUL-19:15 | 25-JUL-19:15 | 02-JUL-19:30 | 24-JUL-19:30 | 30-JUL-19:15 | 24-JUL-19:00 | 13-JUL-19:30 | 17-JUL-19:30 | 15-JUL-19:00 | 30-JUL-19:00 | 06-JUL-19:00 | 29-JUL-19:30
| Aug | 21-AUG-19:15 | 06-AUG-19:15 | 01-AUG-19:30 | 14-AUG-19:30 | 16-AUG-19:15 | 04-AUG-19:15 | 27-AUG-19:15 | 03-AUG-19:15 | 01-AUG-19:15 | 06-AUG-19:45 | 04-AUG-19:15 | 29-AUG-19:15 | 25-AUG-19:15 | 11-AUG-19:45 | 13-AUG-19:30 | 19-AUG-20:00
| Sep | 10-SEP-19:15 | 15-SEP-19:15 | 09-SEP-19:15 | 10-SEP-19:15 | 25-SEP-19:15 | 01-SEP-19:00 | 28-SEP-19:00 | 09-SEP-19:15 | 02-SEP-19:15 | 02-SEP-19:15 | 06-SEP-19:15 | 01-SEP-19:15 | 14-SEP-19:15 | 02-SEP-19:15 | 08-SEP-19:15 | 09-SEP-19:45
| Oct | 06-OCT-19:15 | 29-OCT-19:30 | 02-OCT-19:15 | 01-OCT-19:15 | 05-OCT-19:15 | 03-OCT-19:15 | 13-OCT-19:15 | 20-OCT-19:30 | 01-OCT-19:15 | 09-OCT-19:15 | 30-OCT-19:30 | 01-OCT-19:15 | 08-OCT-19:15 | 06-OCT-19:15 | 07-OCT-19:15 | 22-OCT-07:15
| Nov | 01-NOV-19:15 | 26-NOV-20:45 | 02-NOV-19:15 | 22-NOV-20:00 | 09-NOV-20:30 | 11-NOV-08:00 | 12-NOV-20:30 | 04-NOV-19:15 | 09-NOV-20:00 | 29-NOV-07:15 | 02-NOV-19:30 | 18-NOV-20:00 | 30-NOV-07:15 | 30-NOV-07:15 | 25-NOV-07:15 | 23-NOV-06:15
| Dec | 17-DEC-20:15 | 02-DEC-20:15 | 13-DEC-20:30 | 22-DEC-07:15 | 18-DEC-20:30 | 05-DEC-20:15 | 17-DEC-20:15 | 21-DEC-07:15 | 29-DEC-07:15 | 11-DEC-07:15 | 31-DEC-07:15 | 12-DEC-07:15 | 31-DEC-06:15 | 11-DEC-06:15 | 31-DEC-06:15 | 29-DEC-06:15
Source Energy
| Total Source Energy (GJ) | 11103.35 | 11302.88 | 9957.92 | 9880.78 | 8667.08 | 10610.05 | 8122.88 | 10321.11 | 9368.51 | 5005.25 | 10189.84 | 9213.8 | 10446.32 | 9806.83 | 10500.42 | 13252.05
| Total Source Energy (MJ/m2) | 2174.48 | 2213.56 | 1950.16 | 1935.05 | 1697.36 | 2077.87 | 1590.79 | 2021.29 | 1834.73 | 980.23 | 1995.58 | 1804.43 | 2045.81 | 1920.57 | 2056.4 | 2595.28
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09
| Total Building | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09
Emissions
| Carbon Equivalent (kg) | 250989.1089 | 281979.8181 | 257407.54 | 244278.9563 | 95568.6854 | 270948.0555 | 90283.1002 | 212550.7902 | 305502.5358 | 62480.0856 | 402579.1989 | 299048.1563 | 278288.8437 | 274102.7699 | 278886.552 | 283876.019
| CO2 (kg) | 587077.0065 | 712008.0015 | 611192.829 | 562495.282 | 257955.2211 | 647915.1746 | 244097.5209 | 485773.0767 | 719623.6339 | 155950.041 | 937610.3172 | 705191.5845 | 650815.3205 | 646535.602 | 652970.409 | 718331.5878
| NOX (kg) | 1009.9508 | 922.1427 | 1008.4241 | 1047.63 | 222.6748 | 1037.4653 | 210.9899 | 926.7769 | 1228.5983 | 220.9751 | 1667.6219 | 1200.6197 | 1145.6433 | 1107.595 | 1146.0494 | 881.2098
| SO2 (kg) | 3757.0287 | 3865.4302 | 3284.0872 | 2635.0984 | 2061.6294 | 4225.9044 | 1901.2169 | 2684.6426 | 3117.3756 | 507.7128 | 4898.8865 | 3036.7839 | 1809.8276 | 1886.1659 | 1804.79 | 4795.8474
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0172 | 0.0109 | 0.009 | 0.0097 | 0.001 | 0.008 | 0.0009 | 0.0109 | 0.0122 | 0.0021 | 0.0148 | 0.0119 | 0.0133 | 0.0132 | 0.0133 | 0.0163
| Water for Electricity (m3) | 464.9647 | 1318.5 | 24258.2 | 4686.98 | 12438.4 | 21074.9 | 11470.4 | 166.959 | 3241.38 | 6708.29 | 1127.73 | 3157.56 | 1189.53 | 44740.5 | 1186.2 | 962.5051

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3729.89 | 730.46 | 943.47
Net Site Energy | 3729.89 | 730.46 | 943.47
Total Source Energy | 11103.35 | 2174.48 | 2808.57
Net Source Energy | 11103.35 | 2174.48 | 2808.57
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.06 | 0 | 0 | 0 | 0 | 0
Cooling | 1075.02 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.64 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 121.73 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 380.71 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3159.69 | 570.19 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 72.38 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 111.83 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10327.4 | 8248.03 | 2079.37 | 0.8 | 3.02
CORRIDORFLR2 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5882.17 | 4687.98 | 1194.19 | 0.8 | 3.02
CORRIDORFLR3 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5581.88 | 4422.55 | 1159.33 | 0.79 | 3.02
CORRIDORFLR4 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7056.3 | 5635.55 | 1420.75 | 0.8 | 3.02
EMPLOYEELOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7798.32 | 5499.81 | 2298.51 | 0.71 | 2.93
EXERCISECENTERFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3939.42 | 2663.37 | 1276.04 | 0.68 | 2.91
FRONTLOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 22496.79 | 15209.7 | 7287.09 | 0.68 | 2.91
FRONTOFFICEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11056.85 | 7980.12 | 3076.73 | 0.72 | 2.95
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2423.27 | 1793.79 | 629.48 | 0.74 | 3.17
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2482.06 | 1845.33 | 636.73 | 0.74 | 3.17
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2654.74 | 1998.74 | 656 | 0.75 | 2.98
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2622.22 | 1999.64 | 622.58 | 0.76 | 3.19
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2568.25 | 1951.47 | 616.78 | 0.76 | 3.19
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4135.38 | 3206.03 | 929.35 | 0.78 | 3
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10121.16 | 7620.76 | 2500.4 | 0.75 | 2.98
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8094.74 | 6126.88 | 1967.85 | 0.76 | 2.98
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9954.74 | 7466.66 | 2488.08 | 0.75 | 2.98
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2762.2 | 2111.74 | 650.47 | 0.76 | 2.99
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2829.96 | 2203.68 | 626.28 | 0.78 | 3
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10578.96 | 8142.79 | 2436.17 | 0.77 | 2.99
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3039.65 | 2391.62 | 648.03 | 0.79 | 3.01
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10111.61 | 7724.07 | 2387.53 | 0.76 | 2.99
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2774.66 | 2152.51 | 622.15 | 0.78 | 3
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4123.38 | 3195.42 | 927.96 | 0.77 | 3
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10104.81 | 7620.48 | 2484.33 | 0.75 | 2.98
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8167.7 | 6202.73 | 1964.97 | 0.76 | 2.98
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10088.77 | 7599.07 | 2489.7 | 0.75 | 2.98
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2771.01 | 2122.46 | 648.55 | 0.77 | 2.99
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2860.21 | 2230.99 | 629.21 | 0.78 | 3
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10324.72 | 7914.81 | 2409.92 | 0.77 | 2.99
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2699.69 | 2085.05 | 614.63 | 0.77 | 3
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10220.97 | 7821.89 | 2399.09 | 0.77 | 2.99
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2788.26 | 2166.08 | 622.18 | 0.78 | 3
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4378.1 | 3426.64 | 951.46 | 0.78 | 3.01
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11296.51 | 8707.87 | 2588.63 | 0.77 | 3
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9141.87 | 7090.71 | 2051.16 | 0.78 | 3
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11295.53 | 8696.63 | 2598.9 | 0.77 | 2.99
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3074.93 | 2401.63 | 673.3 | 0.78 | 3.01
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3137.01 | 2481.34 | 655.67 | 0.79 | 3.02
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11321.95 | 8810.81 | 2511.14 | 0.78 | 3
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2937.98 | 2299.69 | 638.28 | 0.78 | 3.01
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11251.31 | 8747.16 | 2504.15 | 0.78 | 3
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3078.21 | 2428.05 | 650.16 | 0.79 | 3.01
LAUNDRYROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29840.58 | 23221.96 | 6618.62 | 0.78 | 3
MECHANICALROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1324.64 | 965.64 | 359 | 0.73 | 3.16
MEETINGROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12310.24 | 8322.75 | 3987.49 | 0.68 | 2.91
RESTROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1623.14 | 1296.33 | 326.81 | 0.8 | 3.23
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1847.85 | 1
CORRIDORFLR2 PTAC HEAT COIL | Coil:Heating:Electric | 1539.85 | 1
CORRIDORFLR3 PTAC HEAT COIL | Coil:Heating:Electric | 1231.88 | 1
CORRIDORFLR4 PTAC HEAT COIL | Coil:Heating:Electric | 1921.96 | 1
EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 3457.36 | 1
EXERCISECENTERFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 4321.7 | 1
FRONTLOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 16639.5 | 1
FRONTOFFICEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 3928.82 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 139.15 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 351.19 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 395.22 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 493.66 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 556.32 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 556.32 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 722.28 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 713.45 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 556.32 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1204.4 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 2389.56 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 1782.7 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 2329.34 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 815.53 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 780.03 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2225.28 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 556.32 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 2225.28 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 702.61 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1267.21 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 2567.93 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2043.66 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 2550.98 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 868.16 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 839.42 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 2497.95 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 595.67 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 2484.35 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 778.18 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1489.85 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 3480.91 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 2798.98 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 3470.03 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1094.64 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1078.94 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 3460.64 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 927.79 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 3424.36 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1039.22 | 1
LAUNDRYROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 7022.77 | 1
MECHANICALROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 372.77 | 1
MEETINGROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 16865.37 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 70.35 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 243.02 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 274.72 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 364.51 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 191.35 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 217.94 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 227.69 | 1
RESTROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 177.96 | 1
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDORFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 397.12 | 1 | PTAC Fan
CORRIDORFLR2 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.35 | 225.16 | 1 | PTAC Fan
CORRIDORFLR3 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.33 | 210.93 | 1 | PTAC Fan
CORRIDORFLR4 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 271.34 | 1 | PTAC Fan
EMPLOYEELOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.35 | 223.69 | 1 | PTAC Fan
EXERCISECENTERFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.98 | 1 | PTAC Fan
FRONTLOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.91 | 576.67 | 1 | PTAC Fan
FRONTOFFICEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 336.22 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.43 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.09 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.23 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.53 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.38 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.12 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 89.38 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.94 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.33 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.23 | 148.9 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 340.81 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 275.92 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 332.2 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.35 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 102.91 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 374.78 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 113.12 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 352.05 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.05 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.23 | 148.34 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 341.52 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 280.56 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 340 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 97.08 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.41 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 362.39 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.38 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 357.35 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.86 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.25 | 161.04 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 401.53 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 329.52 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 400.4 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 112.57 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 118.11 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.65 | 411.15 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 108.09 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.64 | 407.68 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 115.19 | 1 | PTAC Fan
LAUNDRYROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.7 | 1083.63 | 1 | PTAC Fan
MECHANICALROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.06 | 41.28 | 1 | PTAC Fan
MEETINGROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 315.55 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.22 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.75 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.85 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.13 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.59 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.68 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.71 | 1 | Unit Heater Fans
RESTROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 62.42 | 1 | PTAC Fan
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 45446.4731 | 77.7974 | 287.8118 | 0 | 0.0013 | 35618.8958 | 19390.9141
February | 41546.459 | 71.165 | 263.4584 | 0 | 0.0012 | 32605.0163 | 17731.2688
March | 46131.9181 | 79.0903 | 293.0936 | 0 | 0.0013 | 36272.6571 | 19695.3556
April | 46891.9395 | 80.5966 | 299.5221 | 0 | 0.0014 | 37068.389 | 20040.2018
May | 50964.9152 | 87.8081 | 327.1988 | 0 | 0.0015 | 40493.7751 | 21802.0089
June | 51216.6965 | 88.3919 | 329.9964 | 0 | 0.0015 | 40840.1197 | 21924.7539
July | 54726.1839 | 94.5497 | 353.4033 | 0 | 0.0016 | 43737.0249 | 23437.2079
August | 54488.9655 | 94.1105 | 351.6397 | 0 | 0.0016 | 43518.7396 | 23332.6659
September | 51716.9931 | 89.2214 | 332.9525 | 0 | 0.0015 | 41205.9441 | 22135.5167
October | 51445.5602 | 88.5808 | 329.8487 | 0 | 0.0015 | 40821.6896 | 22002.0733
November | 46791.3207 | 80.3469 | 298.2758 | 0 | 0.0014 | 36914.0855 | 19989.5158
December | 45709.5817 | 78.2922 | 289.8276 | 0 | 0.0013 | 35868.4019 | 19507.6261
Annual Sum or Average | 587077.0065 | 1009.9508 | 3757.0287 | 0 | 0.0172 | 464964.7386 | 250989.1089
Minimum of Months | 41546.459 | 71.165 | 263.4584 | 0 | 0.0012 | 32605.0163 | 17731.2688
Maximum of Months | 54726.1839 | 94.5497 | 353.4033 | 0 | 0.0016 | 43737.0249 | 23437.2079
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 242050000000 | 148307.645 | 06-JAN-20:00 | 57185.041 | 38824.77 | 4339.333 | 0 | 37223.723 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 221569000000 | 151689.873 | 20-FEB-08:00 | 41071.521 | 57998.833 | 5303.851 | 0 | 47230.89 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 246493000000 | 154549.525 | 13-MAR-19:15 | 57185.041 | 38824.77 | 4938.061 | 0 | 42866.874 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 251900000000 | 159510.975 | 01-APR-19:15 | 57040.442 | 38772.136 | 5414.836 | 0 | 47548.783 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 275178000000 | 163747.527 | 15-MAY-19:15 | 57185.041 | 38824.77 | 5742.921 | 0 | 51260.017 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 277531000000 | 176923.794 | 27-JUN-19:15 | 57185.041 | 38824.77 | 6793.343 | 0 | 63385.862 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 297217000000 | 170343.529 | 04-JUL-19:15 | 57112.741 | 38807.225 | 6332.899 | 0 | 57355.884 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 295734000000 | 171344.723 | 21-AUG-19:15 | 57185.041 | 38824.77 | 6347.533 | 0 | 58252.601 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 280017000000 | 166104.853 | 10-SEP-19:15 | 57112.741 | 38807.225 | 5954.653 | 0 | 53495.455 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 277406000000 | 164443.109 | 06-OCT-19:15 | 57185.041 | 38824.77 | 5764.207 | 0 | 51934.312 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 250852000000 | 155849.16 | 01-NOV-19:15 | 57185.041 | 38824.77 | 5011.62 | 0 | 44092.95 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 243746000000 | 148301.901 | 17-DEC-20:15 | 57112.741 | 38807.225 | 4392.033 | 0 | 37255.123 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 3159690000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 221569000000 | 148301.901 |  | 41071.521 | 38772.136 | 4339.333 | 0 | 37223.723 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 297217000000 | 176923.794 |  | 57185.041 | 57998.833 | 6793.343 | 0 | 63385.862 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 69119.2 | 6533.03 | 0 | 75652.23
Cost per Total Building Area ($/m2) | 13.54 | 1.28 | 0 | 14.82
Cost per Net Conditioned Building Area ($/m2) | 17.48 | 1.65 | 0 | 19.14

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3565.25 | 698.22 | 901.82
Net Site Energy | 3565.25 | 698.22 | 901.82
Total Source Energy | 11302.88 | 2213.56 | 2859.04
Net Source Energy | 11302.88 | 2213.56 | 2859.04
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 30.26 | 0 | 0 | 0 | 0 | 0
Cooling | 828.18 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.34 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 96.15 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 458.6 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2917.17 | 648.08 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 72.38 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 111.83 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10384 | 8293.24 | 2090.76 | 0.8 | 3.02
CORRIDORFLR2 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5948.66 | 4750.93 | 1197.73 | 0.8 | 3.02
CORRIDORFLR3 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5651.73 | 4483.87 | 1167.86 | 0.79 | 3.02
CORRIDORFLR4 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7389.41 | 5901.59 | 1487.82 | 0.8 | 3.02
EMPLOYEELOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7688.08 | 5451.96 | 2236.12 | 0.71 | 2.94
EXERCISECENTERFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3916.57 | 2647.93 | 1268.64 | 0.68 | 2.91
FRONTLOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24082.37 | 16281.68 | 7800.68 | 0.68 | 2.91
FRONTOFFICEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10813.95 | 7857.77 | 2956.18 | 0.73 | 2.95
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2582.1 | 1921.39 | 660.71 | 0.74 | 3.17
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2643.34 | 1974.94 | 668.4 | 0.75 | 2.97
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2821.94 | 2131.42 | 690.52 | 0.76 | 2.98
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2585.85 | 1981.74 | 604.11 | 0.77 | 3.2
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2528.16 | 1930.16 | 598 | 0.76 | 3.19
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4258.92 | 3322.99 | 935.92 | 0.78 | 3
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10903.76 | 8250.34 | 2653.42 | 0.76 | 2.98
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8750.19 | 6663.43 | 2086.76 | 0.76 | 2.99
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10727.46 | 8095.23 | 2632.22 | 0.75 | 2.98
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2973.96 | 2281.57 | 692.39 | 0.77 | 2.99
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2811.4 | 2200.05 | 611.35 | 0.78 | 3.01
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10480.92 | 8110.47 | 2370.45 | 0.77 | 3
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3016.28 | 2385.49 | 630.79 | 0.79 | 3.02
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10013.34 | 7690.51 | 2322.83 | 0.77 | 2.99
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2748.34 | 2143.1 | 605.24 | 0.78 | 3
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4237.61 | 3304.11 | 933.49 | 0.78 | 3
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10674.92 | 8048.44 | 2626.48 | 0.75 | 2.98
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8629.45 | 6564.08 | 2065.37 | 0.76 | 2.99
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10657.74 | 8033.37 | 2624.37 | 0.75 | 2.98
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2930.71 | 2245.78 | 684.93 | 0.77 | 2.99
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2845.24 | 2230.65 | 614.59 | 0.78 | 3.01
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10240.32 | 7894.23 | 2346.09 | 0.77 | 3
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2679.01 | 2080.58 | 598.44 | 0.78 | 3
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10136.67 | 7801.16 | 2335.51 | 0.77 | 2.99
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2767.57 | 2160.47 | 607.1 | 0.78 | 3.01
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4514.15 | 3558.01 | 956.14 | 0.79 | 3.01
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11673.83 | 9016.43 | 2657.4 | 0.77 | 3
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9431.04 | 7334.17 | 2096.87 | 0.78 | 3
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11647.51 | 8992.89 | 2654.62 | 0.77 | 3
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3184.74 | 2491.82 | 692.92 | 0.78 | 3.01
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3173.01 | 2527.67 | 645.34 | 0.8 | 3.02
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11428.34 | 8947.58 | 2480.76 | 0.78 | 3.01
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2963.08 | 2337.11 | 625.97 | 0.79 | 3.01
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11357.42 | 8883.58 | 2473.84 | 0.78 | 3.01
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3106.1 | 2466.92 | 639.18 | 0.79 | 3.02
LAUNDRYROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29509.2 | 23018.27 | 6490.93 | 0.78 | 3
MECHANICALROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1437.59 | 1059.05 | 378.54 | 0.74 | 3.16
MEETINGROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12948.06 | 8753.96 | 4194.09 | 0.68 | 2.91
RESTROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1745.51 | 1394.06 | 351.45 | 0.8 | 3.23
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1951.53 | 1
CORRIDORFLR2 PTAC HEAT COIL | Coil:Heating:Electric | 1633.85 | 1
CORRIDORFLR3 PTAC HEAT COIL | Coil:Heating:Electric | 2076.87 | 1
CORRIDORFLR4 PTAC HEAT COIL | Coil:Heating:Electric | 3818.14 | 1
EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 4564.19 | 1
EXERCISECENTERFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 5705.24 | 1
FRONTLOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 21966.42 | 1
FRONTOFFICEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 5922.51 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1346.89 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1299.37 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1340.44 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1535.04 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 123.26 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1160.02 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1181.77 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1426.38 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1406.68 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1174.93 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 2199.04 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 4441.69 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 3434.91 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 4342.43 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1358.7 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1323.53 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 4075.15 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 839.47 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 4203.22 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1268.67 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 2261.97 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 4583.88 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 3660.37 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 4550.08 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1403.68 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1376.45 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 4498.78 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1147.56 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 4473.51 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1331.84 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2653.83 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 6167.88 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 4956.78 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 6142.75 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1796.97 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1789.95 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 6125.85 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1665.04 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 6080.37 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1752.12 | 1
LAUNDRYROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 7416.81 | 1
MECHANICALROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 919.93 | 1
MEETINGROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 22264.6 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1237.05 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1149.07 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1179.14 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1368.35 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 801.9 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 830.51 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 849.46 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 861.18 | 1
RESTROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 645.73 | 1
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDORFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 399.3 | 1 | PTAC Fan
CORRIDORFLR2 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.36 | 228.75 | 1 | PTAC Fan
CORRIDORFLR3 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.34 | 214.2 | 1 | PTAC Fan
CORRIDORFLR4 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 284.15 | 1 | PTAC Fan
EMPLOYEELOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.35 | 223.66 | 1 | PTAC Fan
EXERCISECENTERFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.4 | 1 | PTAC Fan
FRONTLOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.97 | 617.31 | 1 | PTAC Fan
FRONTOFFICEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 334.37 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.19 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 4.04 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 4.17 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.77 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.38 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.56 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 87.4 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 95.72 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.71 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 87.91 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.24 | 155.57 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 371.38 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 302.49 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 363.11 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.57 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.37 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 375.81 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 113.53 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 352.97 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.26 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.24 | 154.55 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 360.58 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 297.54 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 359.78 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 102.78 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 105.05 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 364.04 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.84 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 358.98 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 101.21 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.26 | 168.64 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.65 | 416.79 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 341.95 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.65 | 415.52 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 117.06 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 121.34 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.66 | 420.66 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 110.87 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.66 | 417.16 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 118 | 1 | PTAC Fan
LAUNDRYROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.69 | 1077.26 | 1 | PTAC Fan
MECHANICALROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.07 | 45.96 | 1 | PTAC Fan
MEETINGROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 331.9 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.85 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.57 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.67 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.26 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.49 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.58 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.64 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.68 | 1 | Unit Heater Fans
RESTROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 67.12 | 1 | PTAC Fan
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 53898.9588 | 69.5068 | 288.4211 | 0 | 0.0008 | 98378.8931 | 21307.2753
February | 46093.7589 | 59.3834 | 245.8407 | 0 | 0.0007 | 83854.6972 | 18214.2446
March | 52938.7389 | 68.2995 | 283.7159 | 0 | 0.0008 | 96774.1201 | 20931.6681
April | 56388.9408 | 72.956 | 305.0799 | 0 | 0.0009 | 104062.2112 | 22322.3013
May | 63322.2542 | 82.1207 | 345.3142 | 0 | 0.001 | 117786.9697 | 25092.0072
June | 66128.9155 | 85.919 | 362.8377 | 0 | 0.001 | 123764.9724 | 26224.5849
July | 72043.4204 | 93.701 | 396.6552 | 0 | 0.0011 | 135300.6283 | 28582.6539
August | 70553.1998 | 91.735 | 388.0613 | 0 | 0.0011 | 132369.0884 | 27987.8398
September | 64628.6307 | 83.9314 | 354.0694 | 0 | 0.001 | 120773.9013 | 25624.6827
October | 60969.769 | 79.006 | 331.5916 | 0 | 0.0009 | 113105.8832 | 24151.5874
November | 53701.1904 | 69.4006 | 289.4473 | 0 | 0.0008 | 98729.6217 | 21248.2784
December | 51340.2242 | 66.1834 | 274.3959 | 0 | 0.0008 | 93594.8788 | 20292.6945
Annual Sum or Average | 712008.0015 | 922.1427 | 3865.4302 | 0 | 0.0109 | 1318500 | 281979.8181
Minimum of Months | 46093.7589 | 59.3834 | 245.8407 | 0 | 0.0007 | 83854.6972 | 18214.2446
Maximum of Months | 72043.4204 | 93.701 | 396.6552 | 0 | 0.0011 | 135300.6283 | 28582.6539
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 217663000000 | 158631.247 | 14-JAN-06:15 | 29080.703 | 25635.382 | 4886.106 | 88294.277 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 185529000000 | 137770.783 | 20-FEB-20:30 | 57112.741 | 38807.225 | 3364.142 | 0 | 27751.895 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 214113000000 | 148812.224 | 26-MAR-19:15 | 57112.741 | 38807.225 | 4540.968 | 0 | 37616.511 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 230238000000 | 158308.336 | 30-APR-19:15 | 57112.741 | 38807.225 | 5361.837 | 0 | 46291.754 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 260604000000 | 170901.803 | 26-MAY-19:15 | 57185.041 | 38824.77 | 6392.613 | 0 | 57764.601 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 273830000000 | 168256.035 | 13-JUN-19:30 | 57185.041 | 38824.77 | 6227.353 | 0 | 55284.092 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 299353000000 | 176259.918 | 03-JUL-19:30 | 57185.041 | 38824.77 | 6821.396 | 0 | 62693.933 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 292867000000 | 182811.219 | 06-AUG-19:15 | 57112.741 | 38807.225 | 7367.683 | 0 | 68788.791 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 267212000000 | 167211.761 | 15-SEP-19:15 | 57185.041 | 38824.77 | 6035.817 | 0 | 54431.355 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 250247000000 | 158591.109 | 29-OCT-19:30 | 57112.741 | 38807.225 | 5316.182 | 0 | 46620.182 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 218439000000 | 147707.417 | 26-NOV-20:45 | 57112.741 | 38807.225 | 4340.354 | 0 | 36712.319 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 207079000000 | 146401.096 | 02-DEC-20:15 | 57040.442 | 38772.136 | 4161.37 | 0 | 35692.37 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2917170000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 185529000000 | 137770.783 |  | 29080.703 | 25635.382 | 3364.142 | 0 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 299353000000 | 182811.219 |  | 57185.041 | 38824.77 | 7367.683 | 88294.277 | 68788.791 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 87608.69 | 5312.33 | 0 | 92921.02
Cost per Total Building Area ($/m2) | 17.16 | 1.04 | 0 | 18.2
Cost per Net Conditioned Building Area ($/m2) | 22.16 | 1.34 | 0 | 23.5

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3543.3 | 693.92 | 896.27
Net Site Energy | 3543.3 | 693.92 | 896.27
Total Source Energy | 9957.92 | 1950.16 | 2518.83
Net Source Energy | 9957.92 | 1950.16 | 2518.83
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 8.17 | 0 | 0 | 0 | 0 | 0
Cooling | 862.22 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.3 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 107.03 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 413.87 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2939.95 | 603.35 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 72.38 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 111.83 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10411.7 | 8315.36 | 2096.34 | 0.8 | 3.02
CORRIDORFLR2 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6534.65 | 5218.93 | 1315.72 | 0.8 | 3.02
CORRIDORFLR3 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6232.61 | 4977.7 | 1254.9 | 0.8 | 3.02
CORRIDORFLR4 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8416.45 | 6721.84 | 1694.61 | 0.8 | 3.02
EMPLOYEELOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7107.67 | 5248.04 | 1859.63 | 0.74 | 2.96
EXERCISECENTERFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3984.6 | 2693.92 | 1290.68 | 0.68 | 2.91
FRONTLOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26134.56 | 17669.14 | 8465.42 | 0.68 | 2.91
FRONTOFFICEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9958.22 | 7507.91 | 2450.31 | 0.75 | 2.98
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2571.27 | 1969.3 | 601.97 | 0.77 | 3.2
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2641.7 | 2030.86 | 610.84 | 0.77 | 2.99
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2876.72 | 2236.68 | 640.04 | 0.78 | 3
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2483.18 | 1969.63 | 513.56 | 0.79 | 3.23
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2366.03 | 1864.35 | 501.68 | 0.79 | 3.22
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4541.12 | 3626.79 | 914.33 | 0.8 | 3.02
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11488.56 | 8970.43 | 2518.13 | 0.78 | 3.01
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9275.74 | 7283.47 | 1992.27 | 0.79 | 3.01
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11288.91 | 8794.63 | 2494.28 | 0.78 | 3
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3207.62 | 2538.08 | 669.54 | 0.79 | 3.02
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2994.99 | 2391.96 | 603.03 | 0.8 | 3.02
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10530.89 | 8410.55 | 2120.34 | 0.8 | 3.02
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3175.33 | 2535.99 | 639.34 | 0.8 | 3.02
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10012.19 | 7957.58 | 2054.61 | 0.79 | 3.02
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2863.93 | 2287.3 | 576.64 | 0.8 | 3.02
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4532.24 | 3619.7 | 912.54 | 0.8 | 3.02
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11532.25 | 9008.63 | 2523.62 | 0.78 | 3.01
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9416.13 | 7407.18 | 2008.95 | 0.79 | 3.01
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11511.66 | 8990.54 | 2521.12 | 0.78 | 3.01
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3250.86 | 2576.26 | 674.6 | 0.79 | 3.02
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3072.83 | 2454.13 | 618.7 | 0.8 | 3.02
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10295.3 | 8222.4 | 2072.91 | 0.8 | 3.02
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2747.29 | 2194.14 | 553.15 | 0.8 | 3.02
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10154.87 | 8110.24 | 2044.63 | 0.8 | 3.02
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2926.6 | 2337.35 | 589.26 | 0.8 | 3.02
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4951.34 | 3954.41 | 996.93 | 0.8 | 3.02
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12212.86 | 9718.28 | 2494.58 | 0.8 | 3.02
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9951.61 | 7947.91 | 2003.7 | 0.8 | 3.02
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12186.09 | 9694.4 | 2491.69 | 0.8 | 3.02
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3486.25 | 2784.31 | 701.94 | 0.8 | 3.02
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3587.14 | 2864.89 | 722.25 | 0.8 | 3.02
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12090.4 | 9656.07 | 2434.34 | 0.8 | 3.02
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3202.42 | 2557.63 | 644.79 | 0.8 | 3.02
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11991.71 | 9577.24 | 2414.47 | 0.8 | 3.02
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3456.24 | 2760.34 | 695.9 | 0.8 | 3.02
LAUNDRYROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29295.97 | 23195.82 | 6100.15 | 0.79 | 3.02
MECHANICALROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1381.17 | 1057.91 | 323.27 | 0.77 | 3.2
MEETINGROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13691.67 | 9256.71 | 4434.96 | 0.68 | 2.91
RESTROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1826.25 | 1458.54 | 367.71 | 0.8 | 3.23
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1646.49 | 1
CORRIDORFLR2 PTAC HEAT COIL | Coil:Heating:Electric | 1372.06 | 1
CORRIDORFLR3 PTAC HEAT COIL | Coil:Heating:Electric | 1449.74 | 1
CORRIDORFLR4 PTAC HEAT COIL | Coil:Heating:Electric | 2883.1 | 1
EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 3850.79 | 1
EXERCISECENTERFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 4813.48 | 1
FRONTLOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 18532.96 | 1
FRONTOFFICEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 4758.88 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 816.31 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 798.66 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 832.28 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 992.9 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 27.92 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 946.74 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 966.7 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1198.07 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1184.03 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 965.59 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1672.32 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 3368.76 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2581.47 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 3288.86 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1077.67 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1045.3 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 3032.77 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 619.63 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 3166.87 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 983.35 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1718.98 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 3470.2 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2766.02 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 3444.66 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1110.95 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1086.4 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 3411.82 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 851.83 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 3390.85 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1034.63 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2036.95 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 4763.97 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 3826.91 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 4745.82 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1431.97 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1425.85 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 4749.57 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1287.24 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 4709.02 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1397.68 | 1
LAUNDRYROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 6257.53 | 1
MECHANICALROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 771.61 | 1
MEETINGROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 18784.54 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 721.93 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 672.26 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 693.09 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 835.62 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 471.07 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 502.56 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 516.84 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 525.34 | 1
RESTROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 551.85 | 1
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDORFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 400.36 | 1 | PTAC Fan
CORRIDORFLR2 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.39 | 251.28 | 1 | PTAC Fan
CORRIDORFLR3 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.38 | 239.66 | 1 | PTAC Fan
CORRIDORFLR4 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 323.64 | 1 | PTAC Fan
EMPLOYEELOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.36 | 228.49 | 1 | PTAC Fan
EXERCISECENTERFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 102.14 | 1 | PTAC Fan
FRONTLOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.05 | 669.92 | 1 | PTAC Fan
FRONTOFFICEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 336.36 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.63 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.58 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.69 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 3.2 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.06 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 93.33 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.26 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.07 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.34 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.27 | 174.62 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.66 | 420.33 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 343.65 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.65 | 410.95 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 120.86 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 115.17 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.64 | 404.95 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 122.1 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 380.95 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 110.13 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.27 | 174.28 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.66 | 422.36 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 350.26 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.66 | 421.4 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 122.91 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 118.16 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 395.89 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 105.64 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 390.49 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 112.54 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.3 | 190.4 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.73 | 465.9 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 382.67 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.73 | 464.61 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.21 | 134.06 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.22 | 137.94 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.73 | 464.92 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 123.14 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.72 | 461.12 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.21 | 132.9 | 1 | PTAC Fan
LAUNDRYROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.74 | 1105.45 | 1 | PTAC Fan
MECHANICALROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.08 | 48.39 | 1 | PTAC Fan
MEETINGROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 350.96 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.33 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.17 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.24 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.7 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.52 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.62 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.67 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.7 | 1 | Unit Heater Fans
RESTROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 70.23 | 1 | PTAC Fan
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 42833.9784 | 69.8477 | 224.1871 | 0 | 0.0006 | 1655940 | 17956.3323
February | 38878.7157 | 63.4416 | 203.8012 | 0 | 0.0006 | 1505360 | 16302.6638
March | 46682.1779 | 76.5298 | 247.2724 | 0 | 0.0007 | 1826470 | 19610.685
April | 47545.1878 | 78.282 | 254.2842 | 0 | 0.0007 | 1878280 | 20007.341
May | 52360.4441 | 86.5886 | 282.7749 | 0 | 0.0008 | 2088750 | 22071.8995
June | 58485.7985 | 97.1856 | 319.237 | 0 | 0.0009 | 2358110 | 24701.2406
July | 64267.9748 | 106.9942 | 352.2484 | 0 | 0.001 | 2601960 | 27163.5904
August | 62666.2803 | 104.2505 | 342.9112 | 0 | 0.0009 | 2532990 | 26478.8107
September | 57611.6746 | 95.6179 | 313.6327 | 0 | 0.0009 | 2316700 | 24320.4136
October | 51625.1731 | 85.2174 | 277.6807 | 0 | 0.0008 | 2051110 | 21746.2517
November | 45128.912 | 74.0726 | 239.6902 | 0 | 0.0007 | 1770470 | 18967.1956
December | 43106.5118 | 70.3963 | 226.3672 | 0 | 0.0006 | 1672040 | 18081.1157
Annual Sum or Average | 611192.829 | 1008.4241 | 3284.0872 | 0 | 0.009 | 24258200 | 257407.54
Minimum of Months | 38878.7157 | 63.4416 | 203.8012 | 0 | 0.0006 | 1505360 | 16302.6638
Maximum of Months | 64267.9748 | 106.9942 | 352.2484 | 0 | 0.001 | 2601960 | 27163.5904
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 200690000000 | 131634.865 | 29-JAN-20:15 | 57112.741 | 38807.225 | 3044.57 | 0 | 21935.55 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 182441000000 | 131520.513 | 28-FEB-20:15 | 57185.041 | 38824.77 | 3075.45 | 0 | 21700.473 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 221358000000 | 149556.883 | 17-MAR-19:15 | 57185.041 | 38824.77 | 4934.473 | 0 | 37877.821 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 227637000000 | 150308.886 | 02-APR-19:15 | 57112.741 | 38807.225 | 5038.916 | 0 | 38615.225 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 253144000000 | 173568.034 | 28-MAY-19:30 | 57112.741 | 38807.225 | 7166.457 | 0 | 59746.832 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 285789000000 | 198744.764 | 27-JUN-19:45 | 57185.041 | 38824.77 | 8866.653 | 0 | 83133.522 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 315343000000 | 193558.767 | 11-JUL-19:45 | 57185.041 | 38824.77 | 8490.651 | 0 | 78323.527 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 306983000000 | 198194.334 | 01-AUG-19:30 | 57185.041 | 38824.77 | 8825.652 | 0 | 82624.093 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 280771000000 | 180139.143 | 09-SEP-19:15 | 57040.442 | 38772.136 | 7541.225 | 0 | 66050.562 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 248583000000 | 154072.661 | 02-OCT-19:15 | 57185.041 | 38824.77 | 5333.428 | 0 | 41994.643 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 214571000000 | 135597.088 | 02-NOV-19:15 | 57185.041 | 38824.77 | 3497.621 | 0 | 25354.878 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 202642000000 | 131049.644 | 13-DEC-20:30 | 57185.041 | 38824.77 | 2879.469 | 0 | 21425.585 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2939950000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 182441000000 | 131049.644 |  | 57040.442 | 38772.136 | 2879.469 | 0 | 21425.585 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 315343000000 | 198744.764 |  | 57185.041 | 38824.77 | 8866.653 | 0 | 83133.522 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 71197.58 | 5186.74 | 0 | 76384.32
Cost per Total Building Area ($/m2) | 13.94 | 1.02 | 0 | 14.96
Cost per Net Conditioned Building Area ($/m2) | 18.01 | 1.31 | 0 | 19.32

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3425.62 | 670.87 | 866.5
Net Site Energy | 3425.62 | 670.87 | 866.5
Total Source Energy | 9880.78 | 1935.05 | 2499.32
Net Source Energy | 9880.78 | 1935.05 | 2499.32
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 85.88 | 0 | 0 | 0 | 0 | 0
Cooling | 577.72 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.57 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 76.06 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 533.68 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2702.47 | 723.15 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.278 | 1.58 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 72.38 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 111.83 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10607.58 | 8471.8 | 2135.78 | 0.8 | 3.02
CORRIDORFLR2 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6066.28 | 4844.86 | 1221.41 | 0.8 | 3.02
CORRIDORFLR3 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5681.03 | 4537.19 | 1143.85 | 0.8 | 3.02
CORRIDORFLR4 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7490.14 | 5982.04 | 1508.1 | 0.8 | 3.02
EMPLOYEELOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7176.61 | 5274.43 | 1902.19 | 0.73 | 2.96
EXERCISECENTERFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4033.98 | 2727.31 | 1306.67 | 0.68 | 2.91
FRONTLOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25326.26 | 17122.66 | 8203.6 | 0.68 | 2.91
FRONTOFFICEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10008.94 | 7500.45 | 2508.49 | 0.75 | 2.97
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2526.11 | 1942.63 | 583.48 | 0.77 | 3.2
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2588.62 | 1998.51 | 590.11 | 0.77 | 3.2
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2760.84 | 2152.73 | 608.11 | 0.78 | 3
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2406.88 | 1896.18 | 510.7 | 0.79 | 3.22
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2366.65 | 1859.39 | 507.26 | 0.79 | 3.22
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4100.86 | 3275.18 | 825.69 | 0.8 | 3.02
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10770.41 | 8422.46 | 2347.94 | 0.78 | 3.01
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8683.36 | 6833.22 | 1850.14 | 0.79 | 3.01
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10590.61 | 8260.91 | 2329.7 | 0.78 | 3
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2938.27 | 2326.89 | 611.37 | 0.79 | 3.02
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2713.57 | 2167.21 | 546.36 | 0.8 | 3.02
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9984.18 | 7948.05 | 2036.13 | 0.8 | 3.02
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3006.1 | 2400.84 | 605.26 | 0.8 | 3.02
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9519.89 | 7522.64 | 1997.25 | 0.79 | 3.01
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2640.4 | 2108.77 | 531.63 | 0.8 | 3.02
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4069.82 | 3250.38 | 819.44 | 0.8 | 3.02
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10763.39 | 8416.26 | 2347.13 | 0.78 | 3.01
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8772.18 | 6913.26 | 1858.92 | 0.79 | 3.01
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10747.31 | 8401.38 | 2345.94 | 0.78 | 3.01
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2959.58 | 2346.14 | 613.44 | 0.79 | 3.02
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2761.84 | 2205.76 | 556.08 | 0.8 | 3.02
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9710.77 | 7714.11 | 1996.66 | 0.79 | 3.02
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2553.2 | 2039.13 | 514.07 | 0.8 | 3.23
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9643.8 | 7636.05 | 2007.76 | 0.79 | 3.02
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2668.85 | 2131.49 | 537.36 | 0.8 | 3.02
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4399.43 | 3513.62 | 885.8 | 0.8 | 3.02
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11171.51 | 8879.23 | 2292.28 | 0.79 | 3.02
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9074.34 | 7247.27 | 1827.07 | 0.8 | 3.02
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11146.8 | 8856.74 | 2290.06 | 0.79 | 3.02
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3099.5 | 2475.43 | 624.07 | 0.8 | 3.02
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3173.34 | 2534.4 | 638.94 | 0.8 | 3.02
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11041.75 | 8818.55 | 2223.2 | 0.8 | 3.02
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2907.27 | 2321.91 | 585.36 | 0.8 | 3.02
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10949.43 | 8744.82 | 2204.61 | 0.8 | 3.02
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3094.83 | 2471.7 | 623.13 | 0.8 | 3.02
LAUNDRYROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28959.66 | 23072.72 | 5886.94 | 0.8 | 3.02
MECHANICALROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1383.11 | 1055.94 | 327.17 | 0.76 | 3.19
MEETINGROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13601.54 | 9195.77 | 4405.77 | 0.68 | 2.91
RESTROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1817.66 | 1451.69 | 365.98 | 0.8 | 3.23
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 2590.81 | 1
CORRIDORFLR2 PTAC HEAT COIL | Coil:Heating:Electric | 2150.55 | 1
CORRIDORFLR3 PTAC HEAT COIL | Coil:Heating:Electric | 2590.24 | 1
CORRIDORFLR4 PTAC HEAT COIL | Coil:Heating:Electric | 4568.26 | 1
EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 4923.59 | 1
EXERCISECENTERFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 6154.48 | 1
FRONTLOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 23696.1 | 1
FRONTOFFICEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 7207.82 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1853.97 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1706.96 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1742.61 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1972.63 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 30.4 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 52.92 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 198.81 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1425.21 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1448.33 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1707.1 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1686.94 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1442.61 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 2628.14 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 5322.99 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 4151.54 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 5205.76 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1588.71 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1557.82 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 4973.05 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1079.7 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 5093.48 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1504.19 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 2695.32 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 5461.53 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 4376.51 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 5420.68 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1634.7 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1612.44 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 5389.23 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1391.38 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 5358.74 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1561.38 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 3146.63 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 7269.47 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 5854.35 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 7238.37 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2084.32 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2085.35 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 7242.24 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1971.9 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 7191.86 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2037.28 | 1
LAUNDRYROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 8000.83 | 1
MECHANICALROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1133.95 | 1
MEETINGROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 24017.77 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1724.13 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1544.05 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1575.18 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1799.2 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1147.96 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1107.65 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1126 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1141.09 | 1
RESTROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 827.03 | 1
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDORFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.64 | 407.9 | 1 | PTAC Fan
CORRIDORFLR2 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.37 | 233.27 | 1 | PTAC Fan
CORRIDORFLR3 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.34 | 218.45 | 1 | PTAC Fan
CORRIDORFLR4 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 288.02 | 1 | PTAC Fan
EMPLOYEELOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.36 | 228.14 | 1 | PTAC Fan
EXERCISECENTERFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.4 | 1 | PTAC Fan
FRONTLOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.02 | 649.2 | 1 | PTAC Fan
FRONTOFFICEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 333.29 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.96 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.49 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.61 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.35 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.1 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.17 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.64 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 89.31 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 92.33 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.7 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 89.82 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 87.79 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.25 | 157.69 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 395.4 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 323.26 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 386.6 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 110.92 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.35 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 381.22 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 115.59 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 357.65 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 101.53 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.25 | 156.5 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 395.06 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 327.62 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 394.23 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 111.97 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.2 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 369.08 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 98.18 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 363.93 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 102.63 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.27 | 169.17 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.67 | 425.09 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 348.94 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.67 | 423.85 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 119.19 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 122.03 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.67 | 424.59 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 111.79 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.66 | 421.04 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 119.01 | 1 | PTAC Fan
LAUNDRYROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.74 | 1107.73 | 1 | PTAC Fan
MECHANICALROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.08 | 48.09 | 1 | PTAC Fan
MEETINGROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 348.65 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.55 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.97 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 5.07 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.79 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.69 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.56 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.62 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.67 | 1 | Unit Heater Fans
RESTROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 69.9 | 1 | PTAC Fan
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 45221.3103 | 83.6028 | 208.8049 | 0 | 0.0008 | 371389.5931 | 19581.2906
February | 40677.8301 | 75.1781 | 187.7031 | 0 | 0.0007 | 333856.7629 | 17611.6049
March | 41793.3892 | 77.0731 | 192.0339 | 0 | 0.0007 | 341558.0199 | 18079.2008
April | 43338.3624 | 80.3717 | 201.3359 | 0 | 0.0007 | 358107.1974 | 18789.038
May | 48954.245 | 91.3451 | 230.1641 | 0 | 0.0008 | 409388.2043 | 21275.3604
June | 51091.8238 | 95.786 | 242.4313 | 0 | 0.0009 | 431211.8156 | 22246.1137
July | 55455.1538 | 104.254 | 264.5457 | 0 | 0.001 | 470549.4771 | 24172.5418
August | 54744.1109 | 102.8928 | 261.0339 | 0 | 0.001 | 464302.7715 | 23860.3456
September | 51002.6264 | 95.6551 | 242.1863 | 0 | 0.0009 | 430776.4508 | 22210.6346
October | 45895.7518 | 85.496 | 215.0872 | 0 | 0.0008 | 382569.7556 | 19933.0158
November | 40831.3632 | 75.5824 | 189.0028 | 0 | 0.0007 | 336169.5101 | 17689.2149
December | 43489.3149 | 80.393 | 200.7692 | 0 | 0.0007 | 357096.8198 | 18830.5952
Annual Sum or Average | 562495.282 | 1047.63 | 2635.0984 | 0 | 0.0097 | 4686980 | 244278.9563
Minimum of Months | 40677.8301 | 75.1781 | 187.7031 | 0 | 0.0007 | 333856.7629 | 17611.6049
Maximum of Months | 55455.1538 | 104.254 | 264.5457 | 0 | 0.001 | 470549.4771 | 24172.5418
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 214140000000 | 167264.951 | 14-JAN-07:15 | 30350.287 | 41065.016 | 3677.81 | 81437.06 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 192499000000 | 167090.173 | 10-FEB-07:15 | 37896.934 | 51279.599 | 2473.377 | 64705.485 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 196939000000 | 136815.411 | 28-MAR-19:15 | 57185.041 | 38824.77 | 3594.329 | 0 | 26476.493 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 206481000000 | 146720.855 | 15-APR-19:15 | 57040.442 | 38772.136 | 4642.991 | 0 | 35530.508 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 236049000000 | 160077.026 | 14-MAY-19:30 | 57112.741 | 38807.225 | 5882.387 | 0 | 47539.894 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 248633000000 | 163173.621 | 19-JUN-19:00 | 57185.041 | 38824.77 | 6168.812 | 0 | 50260.22 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 271314000000 | 173601.828 | 02-JUL-19:00 | 57112.741 | 38807.225 | 7059.61 | 0 | 59887.473 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 267713000000 | 164516.086 | 14-AUG-19:30 | 57185.041 | 38824.77 | 6222.69 | 0 | 51548.806 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 248382000000 | 155878.934 | 10-SEP-19:15 | 57112.741 | 38807.225 | 5486.039 | 0 | 43738.15 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 220586000000 | 145617.758 | 01-OCT-19:15 | 57112.741 | 38807.225 | 4491.767 | 0 | 34471.245 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 193832000000 | 130572.994 | 22-NOV-20:00 | 57185.041 | 38824.77 | 2795.022 | 0 | 21033.383 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 205899000000 | 153496.92 | 22-DEC-07:15 | 37896.934 | 51279.599 | 1929.542 | 51656.067 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2702470000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 192499000000 | 130572.994 |  | 30350.287 | 38772.136 | 1929.542 | 0 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 271314000000 | 173601.828 |  | 57185.041 | 51279.599 | 7059.61 | 81437.06 | 59887.473 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 75249.49 | 7880.41 | 0 | 83129.9
Cost per Total Building Area ($/m2) | 14.74 | 1.54 | 0 | 16.28
Cost per Net Conditioned Building Area ($/m2) | 19.03 | 1.99 | 0 | 21.03

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3258.92 | 638.23 | 824.34
Net Site Energy | 3258.92 | 638.23 | 824.34
Total Source Energy | 8667.08 | 1697.36 | 2192.32
Net Source Energy | 8667.08 | 1697.36 | 2192.32
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.62 | 0 | 0 | 0 | 0 | 0
Cooling | 517.4 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.55 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 69.53 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 519.11 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2550.34 | 708.59 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 72.38 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 111.83 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9298.12 | 7425.99 | 1872.13 | 0.8 | 3.02
CORRIDORFLR2 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5327.4 | 4254.76 | 1072.64 | 0.8 | 3.02
CORRIDORFLR3 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4892.64 | 3907.53 | 985.11 | 0.8 | 3.02
CORRIDORFLR4 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6049.14 | 4831.18 | 1217.96 | 0.8 | 3.02
EMPLOYEELOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5671.49 | 4429.09 | 1242.4 | 0.78 | 3.01
EXERCISECENTERFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3172.86 | 2203.05 | 969.81 | 0.69 | 2.92
FRONTLOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19844.13 | 14628.1 | 5216.03 | 0.74 | 2.96
FRONTOFFICEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7265.89 | 5724.83 | 1541.06 | 0.79 | 3.01
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2308.49 | 1843.69 | 464.8 | 0.8 | 3.23
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2382.72 | 1902.97 | 479.75 | 0.8 | 3.23
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2488.21 | 1987.22 | 500.99 | 0.8 | 3.23
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1813.92 | 1448.7 | 365.22 | 0.8 | 3.23
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1876.2 | 1498.44 | 377.76 | 0.8 | 3.23
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3703.05 | 2957.46 | 745.59 | 0.8 | 3.02
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10137.49 | 8096.36 | 2041.13 | 0.8 | 3.02
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8359.08 | 6676.02 | 1683.06 | 0.8 | 3.02
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9920.15 | 7922.78 | 1997.37 | 0.8 | 3.02
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2724.06 | 2175.59 | 548.48 | 0.8 | 3.02
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2150.96 | 1717.87 | 433.08 | 0.8 | 3.23
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8372.42 | 6686.67 | 1685.74 | 0.8 | 3.02
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2580.75 | 2061.13 | 519.62 | 0.8 | 3.23
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7776.37 | 6210.64 | 1565.73 | 0.8 | 3.02
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2118.48 | 1691.94 | 426.55 | 0.8 | 3.23
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3636.97 | 2904.68 | 732.28 | 0.8 | 3.02
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10062.52 | 8036.48 | 2026.03 | 0.8 | 3.02
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8416.88 | 6722.19 | 1694.69 | 0.8 | 3.02
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10045.05 | 8022.53 | 2022.52 | 0.8 | 3.02
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2729.25 | 2179.73 | 549.52 | 0.8 | 3.02
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2177.99 | 1739.46 | 438.53 | 0.8 | 3.23
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8027.05 | 6410.85 | 1616.21 | 0.8 | 3.02
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2123.34 | 1695.82 | 427.52 | 0.8 | 3.23
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7907.47 | 6315.34 | 1592.13 | 0.8 | 3.02
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2124.92 | 1697.08 | 427.84 | 0.8 | 3.23
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3741.97 | 2988.54 | 753.43 | 0.8 | 3.02
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9879.09 | 7889.99 | 1989.1 | 0.8 | 3.02
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8156.96 | 6514.6 | 1642.36 | 0.8 | 3.02
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9868.31 | 7881.38 | 1986.93 | 0.8 | 3.02
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2668.06 | 2130.86 | 537.2 | 0.8 | 3.02
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2510.61 | 2005.11 | 505.5 | 0.8 | 3.23
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9194.89 | 7343.55 | 1851.34 | 0.8 | 3.02
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2392.85 | 1911.06 | 481.79 | 0.8 | 3.23
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9113.27 | 7278.36 | 1834.91 | 0.8 | 3.02
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2458.4 | 1963.41 | 494.99 | 0.8 | 3.23
LAUNDRYROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27257.92 | 21769.68 | 5488.24 | 0.8 | 3.02
MECHANICALROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1204 | 961.58 | 242.42 | 0.8 | 3.23
MEETINGROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12750.66 | 8765.19 | 3985.47 | 0.69 | 2.92
RESTROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1748.26 | 1396.26 | 352 | 0.8 | 3.23
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1841.28 | 1
CORRIDORFLR2 PTAC HEAT COIL | Coil:Heating:Electric | 1281.21 | 1
CORRIDORFLR3 PTAC HEAT COIL | Coil:Heating:Electric | 1281.21 | 1
CORRIDORFLR4 PTAC HEAT COIL | Coil:Heating:Electric | 2247.25 | 1
EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 3595.8 | 1
EXERCISECENTERFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 4494.76 | 1
FRONTLOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 17305.79 | 1
FRONTOFFICEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 4086.14 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 421.41 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 490.8 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 523.7 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 646.51 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 726.54 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 745.52 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 961.08 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 948.04 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 739.87 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1353.69 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 2720.44 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2057.37 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 2654.33 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 904.83 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 869.34 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2370.06 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 578.6 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 2513.36 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 799.29 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1399.4 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 2831.53 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2253.04 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 2811.97 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 939.73 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 911.29 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 2764.9 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 673.37 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 2748.09 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 852.39 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1658.26 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 3890.67 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 3124.88 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 3877.63 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1202.56 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1189.66 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 3870.09 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1043 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 3832.4 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1155.78 | 1
LAUNDRYROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 6997.82 | 1
MECHANICALROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 584.48 | 1
MEETINGROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 17540.71 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 340.07 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 378.3 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 401.19 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 507.76 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 198.13 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 290.79 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 307.08 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 315.22 | 1
RESTROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 384.76 | 1
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDORFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 357.54 | 1 | PTAC Fan
CORRIDORFLR2 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.32 | 204.86 | 1 | PTAC Fan
CORRIDORFLR3 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.3 | 188.14 | 1 | PTAC Fan
CORRIDORFLR4 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.37 | 232.61 | 1 | PTAC Fan
EMPLOYEELOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.33 | 207.58 | 1 | PTAC Fan
EXERCISECENTERFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 87.39 | 1 | PTAC Fan
FRONTLOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1 | 635.42 | 1 | PTAC Fan
FRONTOFFICEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 271.23 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.31 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.53 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.63 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.01 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.77 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.62 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 95.68 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 69.75 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 72.15 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.22 | 142.39 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 389.82 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 321.43 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 381.46 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.75 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.71 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 321.95 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 99.24 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 299.03 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.46 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.22 | 139.85 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 386.94 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 323.66 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 386.27 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.95 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 83.75 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 308.67 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.65 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 304.07 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.71 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.23 | 143.89 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 379.88 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 313.66 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 379.47 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 102.6 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.54 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 353.57 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 92.01 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 350.44 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.53 | 1 | PTAC Fan
LAUNDRYROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.65 | 1048.16 | 1 | PTAC Fan
MECHANICALROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.07 | 46.3 | 1 | PTAC Fan
MEETINGROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 341.98 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.06 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.18 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.25 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.58 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.62 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.9 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.96 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.98 | 1 | Unit Heater Fans
RESTROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 67.23 | 1 | PTAC Fan
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 20717.7831 | 17.9008 | 162.6053 | 0 | 0.0001 | 981032.6561 | 7666.5618
February | 18831.3579 | 16.2701 | 147.9535 | 0 | 0.0001 | 892636 | 6968.9649
March | 20888.0714 | 18.0449 | 164.4936 | 0 | 0.0001 | 992427.3527 | 7731.26
April | 20456.6479 | 17.6667 | 162.0852 | 0 | 0.0001 | 977901.2422 | 7574.5959
May | 21645.8158 | 18.6856 | 172.9488 | 0 | 0.0001 | 1043450 | 8019.3133
June | 21222.8989 | 18.3148 | 170.5883 | 0 | 0.0001 | 1029210 | 7865.7393
July | 23012.782 | 19.8493 | 186.7837 | 0 | 0.0001 | 1126930 | 8534.6321
August | 23454.4807 | 20.2273 | 190.9177 | 0 | 0.0001 | 1151870 | 8700.1177
September | 22705.5482 | 19.5832 | 184.4988 | 0 | 0.0001 | 1113150 | 8421.3269
October | 22783.5248 | 19.6586 | 183.6743 | 0 | 0.0001 | 1108170 | 8445.7992
November | 21083.016 | 18.2022 | 168.012 | 0 | 0.0001 | 1013660 | 7809.4653
December | 21153.2944 | 18.2713 | 167.0681 | 0 | 0.0001 | 1007960 | 7830.9091
Annual Sum or Average | 257955.2211 | 222.6748 | 2061.6294 | 0 | 0.001 | 12438400 | 95568.6854
Minimum of Months | 18831.3579 | 16.2701 | 147.9535 | 0 | 0.0001 | 892636 | 6968.9649
Maximum of Months | 23454.4807 | 20.2273 | 190.9177 | 0 | 0.0001 | 1151870 | 8700.1177
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 201149000000 | 129151 | 26-JAN-20:30 | 57185.041 | 38824.77 | 2792.173 | 0 | 19614.238 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 183024000000 | 130288.955 | 12-FEB-20:30 | 57112.741 | 38807.225 | 2902.259 | 0 | 20731.951 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 203485000000 | 128643.004 | 04-MAR-20:00 | 57040.442 | 38772.136 | 2746.54 | 0 | 19349.108 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 200506000000 | 133877.92 | 11-APR-19:15 | 57185.041 | 38824.77 | 3402.434 | 0 | 23730.897 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 213946000000 | 139410.891 | 29-MAY-19:15 | 57112.741 | 38807.225 | 3923.837 | 0 | 28832.31 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 211027000000 | 138280.868 | 28-JUN-19:15 | 57185.041 | 38824.77 | 3746.581 | 0 | 27789.698 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 231063000000 | 141409.929 | 10-JUL-19:15 | 57185.041 | 38824.77 | 4127.742 | 0 | 30537.597 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 236178000000 | 143455.285 | 16-AUG-19:15 | 57185.041 | 38824.77 | 4267.385 | 0 | 32443.311 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 228237000000 | 142290 | 25-SEP-19:15 | 57185.041 | 38824.77 | 4213.315 | 0 | 31332.096 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 227216000000 | 137872.823 | 05-OCT-19:15 | 57185.041 | 38824.77 | 3690.059 | 0 | 27438.174 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 207839000000 | 132325.05 | 09-NOV-20:30 | 57185.041 | 38824.77 | 3038.934 | 0 | 22541.527 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 206670000000 | 129304.518 | 18-DEC-20:30 | 57185.041 | 38824.77 | 2807.972 | 0 | 19751.957 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2550340000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 183024000000 | 128643.004 |  | 57040.442 | 38772.136 | 2746.54 | 0 | 19349.108 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 236178000000 | 143455.285 |  | 57185.041 | 38824.77 | 4267.385 | 0 | 32443.311 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 87168 | 5947.48 | 0 | 93115.48
Cost per Total Building Area ($/m2) | 17.07 | 1.16 | 0 | 18.24
Cost per Net Conditioned Building Area ($/m2) | 22.05 | 1.5 | 0 | 23.55

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3422.81 | 670.32 | 865.79
Net Site Energy | 3422.81 | 670.32 | 865.79
Total Source Energy | 10610.05 | 2077.87 | 2683.79
Net Source Energy | 10610.05 | 2077.87 | 2683.79
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 25.64 | 0 | 0 | 0 | 0 | 0
Cooling | 685.9 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.38 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 91.37 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 467.8 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2765.53 | 657.28 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.306 | 1.623 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 72.38 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 111.83 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10087.15 | 8056.16 | 2031 | 0.8 | 3.02
CORRIDORFLR2 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6538.42 | 5221.95 | 1316.48 | 0.8 | 3.02
CORRIDORFLR3 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6201.56 | 4952.91 | 1248.65 | 0.8 | 3.02
CORRIDORFLR4 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8120.65 | 6485.6 | 1635.05 | 0.8 | 3.02
EMPLOYEELOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6327.18 | 4958.12 | 1369.07 | 0.78 | 3.01
EXERCISECENTERFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3977.31 | 2688.99 | 1288.32 | 0.68 | 2.91
FRONTLOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 23877.73 | 16806.57 | 7071.15 | 0.7 | 2.93
FRONTOFFICEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8676.3 | 6914.82 | 1761.48 | 0.8 | 3.02
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2371.29 | 1893.84 | 477.45 | 0.8 | 3.23
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2456.4 | 1961.82 | 494.58 | 0.8 | 3.23
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2678.51 | 2139.21 | 539.3 | 0.8 | 3.02
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2369.97 | 1892.79 | 477.18 | 0.8 | 3.23
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2277.47 | 1818.91 | 458.56 | 0.8 | 3.23
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4564.6 | 3645.54 | 919.06 | 0.8 | 3.02
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11214.8 | 8956.76 | 2258.04 | 0.8 | 3.02
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9187.28 | 7337.47 | 1849.81 | 0.8 | 3.02
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10964.11 | 8756.55 | 2207.57 | 0.8 | 3.02
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3152.63 | 2517.87 | 634.77 | 0.8 | 3.02
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2961.76 | 2365.42 | 596.33 | 0.8 | 3.02
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10652.71 | 8507.85 | 2144.87 | 0.8 | 3.02
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3209.79 | 2563.52 | 646.28 | 0.8 | 3.02
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9998.41 | 7985.28 | 2013.13 | 0.8 | 3.02
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2849.61 | 2275.86 | 573.75 | 0.8 | 3.02
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4531.69 | 3619.26 | 912.43 | 0.8 | 3.02
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11250.45 | 8985.23 | 2265.22 | 0.8 | 3.02
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9346.21 | 7464.4 | 1881.81 | 0.8 | 3.02
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11223.83 | 8963.97 | 2259.86 | 0.8 | 3.02
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3200.4 | 2556.01 | 644.38 | 0.8 | 3.02
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3040.31 | 2428.16 | 612.15 | 0.8 | 3.02
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10405.01 | 8310.02 | 2094.99 | 0.8 | 3.02
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2769.01 | 2211.49 | 557.53 | 0.8 | 3.02
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10261.53 | 8195.42 | 2066.1 | 0.8 | 3.02
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2908.42 | 2322.82 | 585.59 | 0.8 | 3.02
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4875.34 | 3893.71 | 981.62 | 0.8 | 3.02
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11997.96 | 9582.23 | 2415.73 | 0.8 | 3.02
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9854.68 | 7870.49 | 1984.19 | 0.8 | 3.02
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11960.54 | 9552.35 | 2408.19 | 0.8 | 3.02
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3398.74 | 2714.42 | 684.32 | 0.8 | 3.02
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3508.32 | 2801.94 | 706.38 | 0.8 | 3.02
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12010.28 | 9592.08 | 2418.21 | 0.8 | 3.02
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3168.41 | 2530.47 | 637.94 | 0.8 | 3.02
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11909.74 | 9511.78 | 2397.96 | 0.8 | 3.02
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3388.62 | 2706.34 | 682.28 | 0.8 | 3.02
LAUNDRYROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29484.82 | 23548.2 | 5936.61 | 0.8 | 3.02
MECHANICALROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1237.72 | 988.51 | 249.21 | 0.8 | 3.23
MEETINGROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13952.55 | 9433.08 | 4519.46 | 0.68 | 2.91
RESTROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1825.78 | 1458.17 | 367.61 | 0.8 | 3.23
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1927.04 | 1
CORRIDORFLR2 PTAC HEAT COIL | Coil:Heating:Electric | 1534.07 | 1
CORRIDORFLR3 PTAC HEAT COIL | Coil:Heating:Electric | 1919.62 | 1
CORRIDORFLR4 PTAC HEAT COIL | Coil:Heating:Electric | 3591.02 | 1
EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 4162.8 | 1
EXERCISECENTERFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 5203.5 | 1
FRONTLOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 20034.61 | 1
FRONTOFFICEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 5933.27 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1276.51 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1177.94 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1210.67 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1397.45 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 104.97 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1188.18 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1209.32 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1455.34 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1442.7 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1210.82 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 2066.02 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 4169.61 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 3229.26 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 4072.63 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1288.57 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1260.29 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 3842.85 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 781.02 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 3970.1 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1208.26 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 2117 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 4269.35 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 3412.99 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 4236.73 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1322.94 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1301.04 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 4208.8 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1070.65 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 4184.31 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1257.02 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2493.04 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 5788.27 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 4656.03 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 5764.03 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1700.29 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1697.37 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 5767.2 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1568.77 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 5722.49 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1661.21 | 1
LAUNDRYROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 6764.55 | 1
MECHANICALROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 970.49 | 1
MEETINGROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 20306.58 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1161.01 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1028.76 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1052.63 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1232.84 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 789.09 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 760.87 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 774.56 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 785.89 | 1
RESTROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 722.31 | 1
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDORFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 387.88 | 1 | PTAC Fan
CORRIDORFLR2 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.39 | 251.42 | 1 | PTAC Fan
CORRIDORFLR3 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.37 | 238.47 | 1 | PTAC Fan
CORRIDORFLR4 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 312.27 | 1 | PTAC Fan
EMPLOYEELOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.37 | 233.35 | 1 | PTAC Fan
EXERCISECENTERFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 101.95 | 1 | PTAC Fan
FRONTLOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.07 | 681.44 | 1 | PTAC Fan
FRONTOFFICEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 332.11 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.28 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.95 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 4.06 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.69 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.35 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.18 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.46 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.13 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 87.58 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.28 | 175.52 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.68 | 431.25 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 353.28 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.66 | 421.61 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 121.23 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 113.89 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.64 | 409.63 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 123.43 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 384.47 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 109.58 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.27 | 174.26 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.68 | 432.62 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 359.39 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.68 | 431.59 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 123.07 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 116.91 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 400.11 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.48 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 394.59 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 111.84 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.29 | 187.47 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.72 | 461.36 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 378.94 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.72 | 459.92 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.21 | 130.69 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.21 | 134.91 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.73 | 461.83 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 121.84 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.72 | 457.97 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.2 | 130.3 | 1 | PTAC Fan
LAUNDRYROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.78 | 1133.79 | 1 | PTAC Fan
MECHANICALROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.07 | 47.59 | 1 | PTAC Fan
MEETINGROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 357.65 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.89 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.45 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.53 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 4.14 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.65 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.55 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.6 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.64 | 1 | Unit Heater Fans
RESTROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 70.21 | 1 | PTAC Fan
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 47864.0648 | 75.9069 | 305.2781 | 0 | 0.0006 | 1522420 | 19939.6388
February | 43031.5156 | 68.2457 | 274.4808 | 0 | 0.0005 | 1368830 | 17926.7261
March | 47427.2064 | 75.3306 | 303.5862 | 0 | 0.0006 | 1513980 | 19769.7504
April | 50386.764 | 80.4724 | 326.6762 | 0 | 0.0006 | 1629150 | 21049.2661
May | 54698.2572 | 87.7121 | 357.955 | 0 | 0.0007 | 1785150 | 22887.1855
June | 61720.1309 | 99.4881 | 408.7578 | 0 | 0.0008 | 2038530 | 25878.9577
July | 67989.0564 | 109.8239 | 452.4439 | 0 | 0.0009 | 2256400 | 28531.4687
August | 67163.205 | 108.4556 | 446.6266 | 0 | 0.0008 | 2227390 | 28181.3452
September | 59929.7724 | 96.5207 | 396.1342 | 0 | 0.0007 | 1975570 | 25119.7934
October | 53707.5021 | 86.0409 | 350.6961 | 0 | 0.0007 | 1748950 | 22464.0558
November | 46668.0049 | 74.3283 | 300.6408 | 0 | 0.0006 | 1499300 | 19474.45
December | 47329.695 | 75.1402 | 302.6287 | 0 | 0.0006 | 1509210 | 19725.4178
Annual Sum or Average | 647915.1746 | 1037.4653 | 4225.9044 | 0 | 0.008 | 21074900 | 270948.0555
Minimum of Months | 43031.5156 | 68.2457 | 274.4808 | 0 | 0.0005 | 1368830 | 17926.7261
Maximum of Months | 67989.0564 | 109.8239 | 452.4439 | 0 | 0.0009 | 2256400 | 28531.4687
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 199777000000 | 118362.417 | 18-JAN-20:30 | 57185.041 | 38824.77 | 1462.232 | 0 | 10155.596 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 179623000000 | 125167.896 | 27-FEB-20:15 | 57185.041 | 38824.77 | 2342.896 | 0 | 16080.411 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 198671000000 | 130121.619 | 31-MAR-19:00 | 57185.041 | 38824.77 | 2947.348 | 0 | 20429.681 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 213783000000 | 147620.48 | 21-APR-19:15 | 57185.041 | 38824.77 | 4867.145 | 0 | 36008.746 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 234255000000 | 155726.398 | 31-MAY-19:15 | 57185.041 | 38824.77 | 5689.178 | 0 | 43292.63 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 267504000000 | 188465.468 | 27-JUN-19:15 | 57185.041 | 38824.77 | 8552.103 | 0 | 73168.776 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 296094000000 | 184076.544 | 25-JUL-19:15 | 57185.041 | 38824.77 | 7991.271 | 0 | 69340.684 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 292287000000 | 178020.981 | 04-AUG-19:15 | 57185.041 | 38824.77 | 7501.836 | 0 | 63774.555 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 259242000000 | 163046.983 | 01-SEP-19:00 | 57185.041 | 38824.77 | 6327.652 | 0 | 49974.742 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 229504000000 | 143615.241 | 03-OCT-19:15 | 57185.041 | 38824.77 | 4505.454 | 0 | 32365.197 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 196744000000 | 128307.404 | 11-NOV-08:00 | 41071.521 | 57998.833 | 3561.521 | 0 | 25590.75 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 198044000000 | 121982.788 | 05-DEC-20:15 | 57185.041 | 38824.77 | 1947.147 | 0 | 13291.052 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2765530000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 179623000000 | 118362.417 |  | 41071.521 | 38824.77 | 1462.232 | 0 | 10155.596 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 296094000000 | 188465.468 |  | 57185.041 | 57998.833 | 8552.103 | 0 | 73168.776 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 72757.64 | 5363.68 | 0 | 78121.32
Cost per Total Building Area ($/m2) | 14.25 | 1.05 | 0 | 15.3
Cost per Net Conditioned Building Area ($/m2) | 18.4 | 1.36 | 0 | 19.76

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3124.64 | 611.93 | 790.37
Net Site Energy | 3124.64 | 611.93 | 790.37
Total Source Energy | 8122.88 | 1590.79 | 2054.67
Net Source Energy | 8122.88 | 1590.79 | 2054.67
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 11.76 | 0 | 0 | 0 | 0 | 0
Cooling | 331.3 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.2 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 46.37 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 583.3 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2351.86 | 772.78 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.272 | 1.571 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 72.38 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 111.83 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8022.68 | 6407.36 | 1615.33 | 0.8 | 3.02
CORRIDORFLR2 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5125.74 | 4093.7 | 1032.04 | 0.8 | 3.02
CORRIDORFLR3 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4740.31 | 3785.87 | 954.44 | 0.8 | 3.02
CORRIDORFLR4 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5667.13 | 4526.09 | 1141.05 | 0.8 | 3.02
EMPLOYEELOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5081.3 | 4058.21 | 1023.09 | 0.8 | 3.02
EXERCISECENTERFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1989.49 | 1588.91 | 400.57 | 0.8 | 3.23
FRONTLOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17800.46 | 14216.43 | 3584.03 | 0.8 | 3.02
FRONTOFFICEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5891.11 | 4704.97 | 1186.14 | 0.8 | 3.02
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2433.6 | 1943.61 | 489.99 | 0.8 | 3.23
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2512.51 | 2006.63 | 505.88 | 0.8 | 3.23
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2529.51 | 2020.2 | 509.3 | 0.8 | 3.23
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1455.87 | 1162.74 | 293.13 | 0.8 | 3.23
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1591.34 | 1270.93 | 320.41 | 0.8 | 3.23
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3870.37 | 3091.09 | 779.28 | 0.8 | 3.02
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11455.03 | 9148.62 | 2306.41 | 0.8 | 3.02
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9571.77 | 7644.55 | 1927.23 | 0.8 | 3.02
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11210.39 | 8953.24 | 2257.15 | 0.8 | 3.02
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2981.58 | 2381.26 | 600.33 | 0.8 | 3.02
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1979.74 | 1581.13 | 398.61 | 0.8 | 3.23
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8015.32 | 6401.48 | 1613.84 | 0.8 | 3.02
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2475.17 | 1976.81 | 498.36 | 0.8 | 3.23
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7401.45 | 5911.21 | 1490.24 | 0.8 | 3.02
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1969.71 | 1573.12 | 396.59 | 0.8 | 3.23
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3799.56 | 3034.54 | 765.02 | 0.8 | 3.02
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11447.3 | 9142.44 | 2304.85 | 0.8 | 3.02
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9723.02 | 7765.34 | 1957.68 | 0.8 | 3.02
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11427.61 | 9126.72 | 2300.89 | 0.8 | 3.02
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3013.94 | 2407.1 | 606.84 | 0.8 | 3.02
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2023.42 | 1616.02 | 407.41 | 0.8 | 3.23
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7713.32 | 6160.28 | 1553.04 | 0.8 | 3.02
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2033.37 | 1623.96 | 409.41 | 0.8 | 3.23
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7596.7 | 6067.14 | 1529.56 | 0.8 | 3.02
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1991.65 | 1590.64 | 401.01 | 0.8 | 3.23
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3819.92 | 3050.8 | 769.12 | 0.8 | 3.02
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11553.88 | 9227.57 | 2326.31 | 0.8 | 3.02
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9780.45 | 7811.21 | 1969.24 | 0.8 | 3.02
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11548.8 | 9223.51 | 2325.29 | 0.8 | 3.02
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3046.61 | 2433.19 | 613.42 | 0.8 | 3.02
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2289.7 | 1828.68 | 461.02 | 0.8 | 3.23
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8602.59 | 6870.51 | 1732.09 | 0.8 | 3.02
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2224.94 | 1776.96 | 447.98 | 0.8 | 3.23
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8527.48 | 6810.51 | 1716.96 | 0.8 | 3.02
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2253.02 | 1799.38 | 453.63 | 0.8 | 3.23
LAUNDRYROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26033.12 | 20791.49 | 5241.63 | 0.8 | 3.02
MECHANICALROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1200.87 | 959.08 | 241.79 | 0.8 | 3.23
MEETINGROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9779.84 | 7631.37 | 2148.47 | 0.78 | 3.01
RESTROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1734.49 | 1385.26 | 349.23 | 0.8 | 3.23
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1699.41 | 1
CORRIDORFLR2 PTAC HEAT COIL | Coil:Heating:Electric | 1416.16 | 1
CORRIDORFLR3 PTAC HEAT COIL | Coil:Heating:Electric | 1439.56 | 1
CORRIDORFLR4 PTAC HEAT COIL | Coil:Heating:Electric | 2834.19 | 1
EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 3974.55 | 1
EXERCISECENTERFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 4968.19 | 1
FRONTLOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 19128.61 | 1
FRONTOFFICEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 4638.91 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 778.51 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 782.39 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 818.86 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 974.68 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 910.73 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 930.73 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1158.58 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1144.61 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 928.57 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1658.75 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 3357.02 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2569.15 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 3279.27 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1073.01 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1039.79 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 3016.45 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 639.54 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 3152.64 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 976.87 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1708.07 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 3470.85 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2766.38 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 3446.42 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1109.27 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1083.86 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 3411.41 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 849.54 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 3391.21 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1032.25 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2017.66 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 4728.71 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 3798.62 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 4711.51 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1421.4 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1414.22 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 4713.6 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1275.13 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 4673.58 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1387.43 | 1
LAUNDRYROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 6458.65 | 1
MECHANICALROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 732.18 | 1
MEETINGROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 19388.28 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 685.12 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 659.17 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 682.07 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 818.33 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 429.21 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 483.69 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 499.66 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 509.12 | 1
RESTROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 506.35 | 1
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDORFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 308.5 | 1 | PTAC Fan
CORRIDORFLR2 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.31 | 197.1 | 1 | PTAC Fan
CORRIDORFLR3 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.29 | 182.28 | 1 | PTAC Fan
CORRIDORFLR4 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.34 | 217.92 | 1 | PTAC Fan
EMPLOYEELOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.31 | 195.39 | 1 | PTAC Fan
EXERCISECENTERFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.5 | 1 | PTAC Fan
FRONTLOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.08 | 684.49 | 1 | PTAC Fan
FRONTOFFICEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.36 | 226.53 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.41 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.43 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.54 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 3.02 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 93.58 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.61 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 97.27 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 55.98 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 61.19 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.23 | 148.83 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.69 | 440.48 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 368.07 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.68 | 431.08 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 114.65 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.13 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 308.22 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 95.18 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 284.61 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75.74 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.23 | 146.11 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.69 | 440.19 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 373.88 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.69 | 439.43 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 115.9 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 77.81 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 296.6 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.19 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 292.12 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.59 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.23 | 146.89 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.7 | 444.28 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 376.09 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.7 | 444.09 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 117.15 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.05 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 330.8 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 85.56 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 327.91 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 86.64 | 1 | PTAC Fan
LAUNDRYROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.57 | 1001.06 | 1 | PTAC Fan
MECHANICALROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.07 | 46.18 | 1 | PTAC Fan
MEETINGROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 357.31 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.12 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.04 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.11 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.54 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.33 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.5 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.55 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.58 | 1 | Unit Heater Fans
RESTROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 66.7 | 1 | PTAC Fan
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 20107.5299 | 17.3934 | 154.2609 | 0 | 0.0001 | 930675.1382 | 7429.8938
February | 18462.3937 | 15.9682 | 142.0316 | 0 | 0.0001 | 856896.0773 | 6823.1984
March | 19998.3891 | 17.2992 | 153.3869 | 0 | 0.0001 | 925402.1126 | 7389.4535
April | 19591.1024 | 16.9412 | 151.2785 | 0 | 0.0001 | 912686.2405 | 7242.0583
May | 20492.1704 | 17.7139 | 159.3965 | 0 | 0.0001 | 961668.0709 | 7578.6872
June | 20073.0333 | 17.3456 | 157.214 | 0 | 0.0001 | 948504.6732 | 7426.9643
July | 21321.1161 | 18.4163 | 168.3788 | 0 | 0.0001 | 1015870 | 7892.9913
August | 21354.5637 | 18.4445 | 168.7685 | 0 | 0.0001 | 1018220 | 7905.7566
September | 21317.9553 | 18.4092 | 169.1506 | 0 | 0.0001 | 1020530 | 7894.252
October | 21536.3218 | 18.6051 | 169.5689 | 0 | 0.0001 | 1023050 | 7971.1051
November | 19880.9414 | 17.187 | 154.3889 | 0 | 0.0001 | 931454.8263 | 7351.8616
December | 19962.0039 | 17.2662 | 153.3927 | 0 | 0.0001 | 925438.3478 | 7376.8782
Annual Sum or Average | 244097.5209 | 210.9899 | 1901.2169 | 0 | 0.0009 | 11470400 | 90283.1002
Minimum of Months | 18462.3937 | 15.9682 | 142.0316 | 0 | 0.0001 | 856896.0773 | 6823.1984
Maximum of Months | 21536.3218 | 18.6051 | 169.5689 | 0 | 0.0001 | 1023050 | 7971.1051
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 190823000000 | 120408.418 | 15-JAN-20:15 | 57112.741 | 38807.225 | 1696.114 | 0 | 12057.558 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 175696000000 | 127665.97 | 15-FEB-20:15 | 57185.041 | 38824.77 | 2535.585 | 0 | 18385.796 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 189742000000 | 123130.077 | 30-MAR-19:30 | 57185.041 | 38824.77 | 1985.33 | 0 | 14400.158 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 187135000000 | 130215.119 | 29-APR-19:15 | 57040.442 | 38772.136 | 2923.317 | 0 | 20744.446 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 197178000000 | 132301.389 | 25-MAY-19:15 | 57185.041 | 38824.77 | 3082.324 | 0 | 22474.475 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 194479000000 | 133580.187 | 16-JUN-19:30 | 57185.041 | 38824.77 | 3311.416 | 0 | 23524.182 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 208292000000 | 150220.565 | 02-JUL-19:30 | 57112.741 | 38807.225 | 5111.527 | 0 | 38454.293 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 208774000000 | 133405.303 | 27-AUG-19:15 | 57112.741 | 38807.225 | 3247.835 | 0 | 23502.723 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 209247000000 | 142071.489 | 28-SEP-19:00 | 57185.041 | 38824.77 | 4276.108 | 0 | 31050.791 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 209763000000 | 132400.978 | 13-OCT-19:15 | 57185.041 | 38824.77 | 3118.586 | 0 | 22537.803 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 190983000000 | 124871.966 | 12-NOV-20:30 | 57112.741 | 38807.225 | 2212.796 | 0 | 16004.424 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 189750000000 | 119496.226 | 17-DEC-20:15 | 57112.741 | 38807.225 | 1574.759 | 0 | 11266.721 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2351860000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 175696000000 | 119496.226 |  | 57040.442 | 38772.136 | 1574.759 | 0 | 11266.721 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 209763000000 | 150220.565 |  | 57185.041 | 38824.77 | 5111.527 | 0 | 38454.293 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 94855.88 | 6485.76 | 0 | 101341.64
Cost per Total Building Area ($/m2) | 18.58 | 1.27 | 0 | 19.85
Cost per Net Conditioned Building Area ($/m2) | 23.99 | 1.64 | 0 | 25.63

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3429.52 | 671.64 | 867.49
Net Site Energy | 3429.52 | 671.64 | 867.49
Total Source Energy | 10321.11 | 2021.29 | 2610.7
Net Source Energy | 10321.11 | 2021.29 | 2610.7
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 165.23 | 0 | 0 | 0 | 0 | 0
Cooling | 457.59 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.37 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 61.94 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 592.67 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2647.37 | 782.15 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.011 | 1.191 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.488 | 0.554 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.488 | 0.554 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.488 | 0.554 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.488 | 0.554 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 72.38 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 111.83 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9949.46 | 7946.19 | 2003.27 | 0.8 | 3.02
CORRIDORFLR2 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5720.48 | 4568.69 | 1151.79 | 0.8 | 3.02
CORRIDORFLR3 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5326.76 | 4254.25 | 1072.52 | 0.8 | 3.02
CORRIDORFLR4 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6681.79 | 5336.45 | 1345.34 | 0.8 | 3.02
EMPLOYEELOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7075.57 | 5127.81 | 1947.76 | 0.72 | 2.95
EXERCISECENTERFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3705.61 | 2505.3 | 1200.31 | 0.68 | 2.91
FRONTLOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25013.33 | 16911.09 | 8102.24 | 0.68 | 2.91
FRONTOFFICEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9678.27 | 7114.3 | 2563.98 | 0.74 | 2.96
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2542.67 | 1936.59 | 606.08 | 0.76 | 3.19
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2605.81 | 1992.42 | 613.39 | 0.76 | 3.2
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2729.86 | 2104.71 | 625.15 | 0.77 | 3
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2287.97 | 1768.76 | 519.21 | 0.77 | 3.2
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2275.71 | 1757.75 | 517.96 | 0.77 | 3.2
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3819.77 | 2992.83 | 826.94 | 0.78 | 3.01
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10916.15 | 8461.87 | 2454.28 | 0.78 | 3
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8848.98 | 6908.16 | 1940.83 | 0.78 | 3.01
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10734.05 | 8299.92 | 2434.13 | 0.77 | 3
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2936.08 | 2300.05 | 636.04 | 0.78 | 3.01
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2568.83 | 2036.29 | 532.55 | 0.79 | 3.23
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9744.22 | 7640.14 | 2104.08 | 0.78 | 3.01
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2840.57 | 2268.64 | 571.93 | 0.8 | 3.02
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9279.33 | 7220.12 | 2059.21 | 0.78 | 3
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2518.4 | 1990.33 | 528.07 | 0.79 | 3.22
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3769.89 | 2954.41 | 815.48 | 0.78 | 3.01
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10892.59 | 8440.92 | 2451.67 | 0.77 | 3
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8927.23 | 6977.93 | 1949.3 | 0.78 | 3.01
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10877.26 | 8427.3 | 2449.96 | 0.77 | 3
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2955.75 | 2317.61 | 638.14 | 0.78 | 3.01
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2605 | 2069.25 | 535.75 | 0.79 | 3.23
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9502.7 | 7421.83 | 2080.87 | 0.78 | 3.01
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2471.67 | 1947.85 | 523.82 | 0.79 | 3.22
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9403.04 | 7331.81 | 2071.24 | 0.78 | 3
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2539.15 | 2009.22 | 529.93 | 0.79 | 3.23
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3912.93 | 3096.03 | 816.9 | 0.79 | 3.02
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10873.23 | 8473.53 | 2399.7 | 0.78 | 3
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8840.61 | 6930.48 | 1910.13 | 0.78 | 3.01
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10887.72 | 8474.06 | 2413.67 | 0.78 | 3
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2947.15 | 2323.28 | 623.87 | 0.79 | 3.01
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2918.82 | 2331.13 | 587.69 | 0.8 | 3.02
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10429.99 | 8261.52 | 2168.48 | 0.79 | 3.02
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2699.59 | 2149.12 | 550.47 | 0.8 | 3.02
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10361.95 | 8199.7 | 2162.25 | 0.79 | 3.02
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2841.35 | 2269.26 | 572.09 | 0.8 | 3.02
LAUNDRYROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28130.15 | 22327.89 | 5802.26 | 0.79 | 3.02
MECHANICALROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1355.25 | 1019.32 | 335.92 | 0.75 | 3.18
MEETINGROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13349.53 | 9025.4 | 4324.14 | 0.68 | 2.91
RESTROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1733.63 | 1384.57 | 349.06 | 0.8 | 3.23
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 3031.77 | 1
CORRIDORFLR2 PTAC HEAT COIL | Coil:Heating:Electric | 2380.82 | 1
CORRIDORFLR3 PTAC HEAT COIL | Coil:Heating:Electric | 2809.78 | 1
CORRIDORFLR4 PTAC HEAT COIL | Coil:Heating:Electric | 4777.17 | 1
EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 5480.83 | 1
EXERCISECENTERFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 6851.04 | 1
FRONTLOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 26378.01 | 1
FRONTOFFICEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 8017.92 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 2116.08 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1903.82 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1938.94 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2178.83 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 37.33 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 58.83 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 207.82 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1561.12 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1584.9 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1839.58 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1822.57 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1582.96 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 2779.91 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 5785.04 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 4529.69 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 5670.2 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1699.87 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1669.23 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 5442.46 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1196.5 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 5565.18 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1619.88 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 2843.17 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 5920.85 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 4752.68 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 5883.41 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1745.32 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1721.88 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 5848.06 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1507.06 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 5818.36 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1674.67 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 3298.72 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 7729.52 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 6231.54 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 7701.55 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2195.27 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2195.04 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 7697.86 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2088.35 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 7647.5 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2150.42 | 1
LAUNDRYROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 8906.36 | 1
MECHANICALROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1217.85 | 1
MEETINGROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 26736.08 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1980.09 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1740.58 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1771.56 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2005.06 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1249.2 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1178.57 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1196.36 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1213.75 | 1
RESTROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 867.07 | 1
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDORFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 382.59 | 1 | PTAC Fan
CORRIDORFLR2 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.35 | 219.97 | 1 | PTAC Fan
CORRIDORFLR3 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.32 | 204.83 | 1 | PTAC Fan
CORRIDORFLR4 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.4 | 256.94 | 1 | PTAC Fan
EMPLOYEELOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.34 | 217.36 | 1 | PTAC Fan
EXERCISECENTERFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.99 | 1 | PTAC Fan
FRONTLOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.01 | 641.18 | 1 | PTAC Fan
FRONTOFFICEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 307.81 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.59 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.93 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.04 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.79 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.12 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.18 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.65 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 87.93 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.92 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 97.07 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.86 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.26 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.22 | 140.83 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 392.95 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 323.63 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 384.22 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 108.21 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 97.18 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 359.83 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 109.23 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 336.86 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.64 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.22 | 139.06 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 391.82 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 327.4 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 391.09 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 109.16 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 98.99 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 347.89 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 92.31 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 342.96 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 95.68 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.23 | 147.43 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 396.1 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 326.34 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 395.5 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 110.14 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 112.24 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 393.91 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.08 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 390.51 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 109.26 | 1 | PTAC Fan
LAUNDRYROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.68 | 1067.22 | 1 | PTAC Fan
MECHANICALROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.07 | 45.52 | 1 | PTAC Fan
MEETINGROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 342.19 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.17 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.42 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.52 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.25 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.89 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.67 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.73 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.78 | 1 | Unit Heater Fans
RESTROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 66.66 | 1 | PTAC Fan
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 44439.2402 | 84.5701 | 244.4199 | 0 | 0.001 | 15200.5054 | 19424.9999
February | 36668.8365 | 69.4094 | 199.621 | 0 | 0.0008 | 12414.3347 | 15994.3202
March | 36138.1266 | 68.0263 | 194.6417 | 0 | 0.0008 | 12104.5552 | 15728.2213
April | 34641.8539 | 65.3846 | 187.5488 | 0 | 0.0008 | 11663.5128 | 15093.0043
May | 39306.2834 | 74.86 | 216.5094 | 0 | 0.0009 | 13464.7654 | 17186.6336
June | 43360.4817 | 83.3461 | 243.0638 | 0 | 0.001 | 15116.434 | 19029.2572
July | 47448.7938 | 91.591 | 268.1152 | 0 | 0.0011 | 16674.5373 | 20858.797
August | 47427.1834 | 91.5927 | 268.2331 | 0 | 0.0011 | 16681.8808 | 20853.2708
September | 41009.7316 | 78.7696 | 229.5663 | 0 | 0.0009 | 14276.9894 | 17992.3034
October | 38803.1744 | 74.0283 | 214.4363 | 0 | 0.0009 | 13335.8838 | 16978.2123
November | 35953.0026 | 68.1715 | 196.3705 | 0 | 0.0008 | 12212.2277 | 15692.7909
December | 40576.3686 | 77.0274 | 222.1166 | 0 | 0.0009 | 13813.3991 | 17718.9795
Annual Sum or Average | 485773.0767 | 926.7769 | 2684.6426 | 0 | 0.0109 | 166959.0256 | 212550.7902
Minimum of Months | 34641.8539 | 65.3846 | 187.5488 | 0 | 0.0008 | 11663.5128 | 15093.0043
Maximum of Months | 47448.7938 | 91.5927 | 268.2331 | 0 | 0.0011 | 16681.8808 | 20858.797
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 241025000000 | 188713.39 | 31-JAN-07:15 | 37896.934 | 51279.599 | 3203.611 | 85598.467 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 196847000000 | 150024.066 | 01-FEB-07:15 | 37896.934 | 51279.599 | 1598.917 | 48513.837 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 191935000000 | 130489.503 | 09-MAR-20:00 | 57185.041 | 38824.77 | 2690.002 | 0 | 21054.911 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 184941000000 | 134742.777 | 05-APR-19:15 | 57185.041 | 38824.77 | 3271.017 | 0 | 24727.171 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 213503000000 | 145931.428 | 15-MAY-19:15 | 57185.041 | 38824.77 | 4315.948 | 0 | 34870.891 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 239692000000 | 164703.954 | 30-JUN-19:45 | 57185.041 | 38824.77 | 6073.511 | 0 | 51885.854 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 264398000000 | 172778.518 | 24-JUL-19:30 | 57185.041 | 38824.77 | 6694.371 | 0 | 59339.557 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 264515000000 | 174047.601 | 03-AUG-19:15 | 57185.041 | 38824.77 | 6786.103 | 0 | 60516.909 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 226382000000 | 149150.429 | 09-SEP-19:15 | 57040.442 | 38772.136 | 4756.531 | 0 | 37846.542 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 211459000000 | 142717.664 | 20-OCT-19:30 | 57185.041 | 38824.77 | 3992.714 | 0 | 31980.361 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 193642000000 | 137550.379 | 04-NOV-19:15 | 57040.442 | 38772.136 | 3472.507 | 0 | 27530.516 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 219031000000 | 159928.112 | 21-DEC-07:15 | 37896.934 | 51279.599 | 1921.745 | 58095.055 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2647370000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 184941000000 | 130489.503 |  | 37896.934 | 38772.136 | 1598.917 | 0 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 264515000000 | 188713.39 |  | 57185.041 | 51279.599 | 6786.103 | 85598.467 | 60516.909 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 51308.83 | 7933 | 0 | 59241.83
Cost per Total Building Area ($/m2) | 10.05 | 1.55 | 0 | 11.6
Cost per Net Conditioned Building Area ($/m2) | 12.98 | 2.01 | 0 | 14.99

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3340.78 | 654.26 | 845.04
Net Site Energy | 3340.78 | 654.26 | 845.04
Total Source Energy | 9368.51 | 1834.73 | 2369.74
Net Source Energy | 9368.51 | 1834.73 | 2369.74
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 80.1 | 0 | 0 | 0 | 0 | 0
Cooling | 458.94 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.34 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 68.18 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 581.5 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2569.8 | 770.98 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.045 | 1.238 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.505 | 0.576 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.505 | 0.576 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.505 | 0.576 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.505 | 0.576 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 72.38 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 111.83 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10568.48 | 8440.57 | 2127.91 | 0.8 | 3.02
CORRIDORFLR2 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6255.93 | 4996.33 | 1259.6 | 0.8 | 3.02
CORRIDORFLR3 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5773.62 | 4611.13 | 1162.49 | 0.8 | 3.02
CORRIDORFLR4 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7144.24 | 5705.79 | 1438.46 | 0.8 | 3.02
EMPLOYEELOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6544.03 | 5226.43 | 1317.61 | 0.8 | 3.02
EXERCISECENTERFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3009.52 | 2291.55 | 717.98 | 0.76 | 2.99
FRONTLOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18289.66 | 14283.02 | 4006.63 | 0.78 | 3.01
FRONTOFFICEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8488.53 | 6779.41 | 1709.12 | 0.8 | 3.02
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2333.3 | 1863.5 | 469.8 | 0.8 | 3.23
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2413.42 | 1927.49 | 485.93 | 0.8 | 3.23
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2466.83 | 1970.15 | 496.68 | 0.8 | 3.23
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2150.2 | 1717.27 | 432.93 | 0.8 | 3.23
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2271.26 | 1813.96 | 457.31 | 0.8 | 3.23
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4002.44 | 3196.57 | 805.87 | 0.8 | 3.02
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11054.5 | 8828.73 | 2225.77 | 0.8 | 3.02
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9069.61 | 7243.49 | 1826.12 | 0.8 | 3.02
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10816.27 | 8638.47 | 2177.8 | 0.8 | 3.02
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2919.59 | 2331.74 | 587.84 | 0.8 | 3.02
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2711.04 | 2165.18 | 545.85 | 0.8 | 3.02
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10626 | 8486.51 | 2139.49 | 0.8 | 3.02
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3239.45 | 2587.2 | 652.25 | 0.8 | 3.02
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9887.83 | 7896.97 | 1990.86 | 0.8 | 3.02
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2690.39 | 2148.7 | 541.7 | 0.8 | 3.02
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3949.53 | 3154.31 | 795.22 | 0.8 | 3.02
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11050.46 | 8825.51 | 2224.95 | 0.8 | 3.02
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9181.14 | 7332.57 | 1848.57 | 0.8 | 3.02
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11027.85 | 8807.45 | 2220.4 | 0.8 | 3.02
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2946.75 | 2353.44 | 593.31 | 0.8 | 3.02
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2759.29 | 2203.72 | 555.57 | 0.8 | 3.02
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10232.97 | 8172.62 | 2060.35 | 0.8 | 3.02
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2703.46 | 2159.13 | 544.33 | 0.8 | 3.02
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10079.6 | 8050.12 | 2029.47 | 0.8 | 3.02
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2708.37 | 2163.06 | 545.32 | 0.8 | 3.02
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4184.98 | 3342.36 | 842.62 | 0.8 | 3.02
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11305.82 | 9029.46 | 2276.37 | 0.8 | 3.02
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9283.96 | 7414.68 | 1869.28 | 0.8 | 3.02
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11273.79 | 9003.87 | 2269.92 | 0.8 | 3.02
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3019.65 | 2411.66 | 607.99 | 0.8 | 3.02
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3111.63 | 2485.12 | 626.51 | 0.8 | 3.02
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11399.1 | 9103.95 | 2295.15 | 0.8 | 3.02
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2964.96 | 2367.98 | 596.98 | 0.8 | 3.02
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11297.26 | 9022.62 | 2274.64 | 0.8 | 3.02
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3059.33 | 2443.35 | 615.98 | 0.8 | 3.02
LAUNDRYROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 32476.87 | 25937.82 | 6539.05 | 0.8 | 3.02
MECHANICALROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1105.47 | 882.89 | 222.58 | 0.8 | 3.23
MEETINGROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11820 | 8648.86 | 3171.15 | 0.73 | 2.96
RESTROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1760.51 | 1406.04 | 354.47 | 0.8 | 3.23
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 2443.26 | 1
CORRIDORFLR2 PTAC HEAT COIL | Coil:Heating:Electric | 1904.86 | 1
CORRIDORFLR3 PTAC HEAT COIL | Coil:Heating:Electric | 2321.99 | 1
CORRIDORFLR4 PTAC HEAT COIL | Coil:Heating:Electric | 4251.94 | 1
EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 4354.82 | 1
EXERCISECENTERFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 5443.53 | 1
FRONTLOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 20958.78 | 1
FRONTOFFICEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 6773.41 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1673.21 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1524.21 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1557.63 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1789.25 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 26.04 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 170.95 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1352.46 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1375.78 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1628.32 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1607.36 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1369.44 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 2378.39 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 4883.58 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 3817.51 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 4772.23 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1472.03 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1437.88 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 4523.15 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 955.46 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 4648.58 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1389.84 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 2435.79 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 5001.84 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 4024.81 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 4965.8 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1512.73 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1486.35 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 4917.71 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1261.06 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 4889.71 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1441.13 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2879.91 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 6770.36 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 5470.37 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 6743.63 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1952.59 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1949.43 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 6729.9 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1832.42 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 6681.16 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1907.32 | 1
LAUNDRYROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 7076.59 | 1
MECHANICALROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1075.32 | 1
MEETINGROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 21243.29 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1542.93 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1362.22 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1391.04 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1616.82 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1022.5 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 972.83 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 988.87 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1005.11 | 1
RESTROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 794.21 | 1
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDORFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.64 | 406.39 | 1 | PTAC Fan
CORRIDORFLR2 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.38 | 240.56 | 1 | PTAC Fan
CORRIDORFLR3 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.35 | 222.01 | 1 | PTAC Fan
CORRIDORFLR4 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 274.72 | 1 | PTAC Fan
EMPLOYEELOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.4 | 251.64 | 1 | PTAC Fan
EXERCISECENTERFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.01 | 1 | PTAC Fan
FRONTLOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.05 | 669.4 | 1 | PTAC Fan
FRONTOFFICEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 326.41 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.3 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.74 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.87 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.74 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.1 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.64 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 89.72 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 92.8 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.86 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.68 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 87.34 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.24 | 153.91 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.67 | 425.08 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 348.76 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.65 | 415.92 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 112.27 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.25 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.64 | 408.6 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.2 | 124.57 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 380.22 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.45 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.24 | 151.87 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.67 | 424.93 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 353.05 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.67 | 424.06 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 113.31 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.1 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 393.49 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.96 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 387.59 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.15 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.25 | 160.93 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.68 | 434.75 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 357 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.68 | 433.51 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 116.12 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 119.65 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.69 | 438.33 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 114.01 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.68 | 434.42 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 117.64 | 1 | PTAC Fan
LAUNDRYROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.96 | 1248.84 | 1 | PTAC Fan
MECHANICALROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.07 | 42.51 | 1 | PTAC Fan
MEETINGROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 371.76 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.81 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.13 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.24 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.09 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.85 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.67 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.73 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.79 | 1 | Unit Heater Fans
RESTROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 67.7 | 1 | PTAC Fan
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 58476.7617 | 99.328 | 250.5685 | 0 | 0.001 | 260531.9346 | 24775.3588
February | 51080.8917 | 86.6421 | 218.2099 | 0 | 0.0009 | 226885.8591 | 21629.7835
March | 55095.6713 | 93.443 | 235.3124 | 0 | 0.0009 | 244668.2833 | 23328.9383
April | 54733.8081 | 93.0767 | 235.1061 | 0 | 0.0009 | 244455.4426 | 23199.9858
May | 61262.9183 | 104.6448 | 265.6688 | 0 | 0.001 | 276236.6302 | 26013.0951
June | 63910.8661 | 109.5757 | 279.3598 | 0 | 0.0011 | 290474.9305 | 27177.4669
July | 70574.0481 | 121.3174 | 310.2039 | 0 | 0.0012 | 322548.4353 | 30042.0696
August | 69082.4315 | 118.7294 | 303.5182 | 0 | 0.0012 | 315596.4705 | 29404.7701
September | 63424.4823 | 108.8056 | 277.579 | 0 | 0.0011 | 288623.7499 | 26976.8942
October | 58704.0954 | 100.271 | 254.5563 | 0 | 0.001 | 264682.1209 | 24926.2925
November | 54227.5502 | 92.2981 | 233.3772 | 0 | 0.0009 | 242658.3545 | 22993.4761
December | 59050.1091 | 100.4664 | 253.9153 | 0 | 0.001 | 264012.9824 | 25034.405
Annual Sum or Average | 719623.6339 | 1228.5983 | 3117.3756 | 0 | 0.0122 | 3241380 | 305502.5358
Minimum of Months | 51080.8917 | 86.6421 | 218.2099 | 0 | 0.0009 | 226885.8591 | 21629.7835
Maximum of Months | 70574.0481 | 121.3174 | 310.2039 | 0 | 0.0012 | 322548.4353 | 30042.0696
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 206553000000 | 141187.558 | 04-JAN-07:15 | 37896.934 | 51279.599 | 1464.302 | 39811.944 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 179878000000 | 121597.091 | 14-FEB-20:15 | 57185.041 | 38824.77 | 1942.855 | 0 | 12909.646 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 193976000000 | 126194.33 | 20-MAR-19:15 | 57185.041 | 38824.77 | 2534.151 | 0 | 16915.589 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 193807000000 | 135968.485 | 22-APR-19:15 | 57040.442 | 38772.136 | 3815.71 | 0 | 25605.419 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 219004000000 | 143596.43 | 30-MAY-19:15 | 57185.041 | 38824.77 | 4617.01 | 0 | 32234.83 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 230292000000 | 151814.499 | 28-JUN-19:30 | 57185.041 | 38824.77 | 5516.672 | 0 | 39553.238 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 255720000000 | 161405.089 | 30-JUL-19:15 | 57112.741 | 38807.225 | 6393.153 | 0 | 48357.191 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 250209000000 | 158169.368 | 01-AUG-19:15 | 57185.041 | 38824.77 | 6044.038 | 0 | 45380.74 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 228824000000 | 146102.824 | 02-SEP-19:15 | 57040.442 | 38772.136 | 4924.42 | 0 | 34631.048 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 209843000000 | 137312.068 | 01-OCT-19:15 | 57112.741 | 38807.225 | 3990.569 | 0 | 26666.754 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 192382000000 | 125222.515 | 09-NOV-20:00 | 57185.041 | 38824.77 | 2371.743 | 0 | 16106.183 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 209313000000 | 138990.325 | 29-DEC-07:15 | 37896.934 | 51279.599 | 1429.625 | 37649.389 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2569800000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 179878000000 | 121597.091 |  | 37896.934 | 38772.136 | 1429.625 | 0 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 255720000000 | 161405.089 |  | 57185.041 | 51279.599 | 6393.153 | 39811.944 | 48357.191 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 26552.87 | 5578.38 | 0 | 32131.25
Cost per Total Building Area ($/m2) | 5.2 | 1.09 | 0 | 6.29
Cost per Net Conditioned Building Area ($/m2) | 6.72 | 1.41 | 0 | 8.13

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3176.57 | 622.1 | 803.51
Net Site Energy | 3176.57 | 622.1 | 803.51
Total Source Energy | 5005.25 | 980.23 | 1266.07
Net Source Energy | 5005.25 | 980.23 | 1266.07
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 87.26 | 0 | 0 | 0 | 0 | 0
Cooling | 272.97 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.1 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 41.19 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 623.36 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2363.74 | 812.83 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.994 | 1.167 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.483 | 0.547 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.483 | 0.547 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.483 | 0.547 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.483 | 0.547 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.54 | 0.384 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.54 | 0.384 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.54 | 0.384 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 72.38 | 5.83 | 0.54 | 0.384
Non-North Total or Average |  |  | 111.83 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8777.57 | 7010.25 | 1767.32 | 0.8 | 3.02
CORRIDORFLR2 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5428.34 | 4335.37 | 1092.97 | 0.8 | 3.02
CORRIDORFLR3 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5038.47 | 4024 | 1014.47 | 0.8 | 3.02
CORRIDORFLR4 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6002.02 | 4793.54 | 1208.47 | 0.8 | 3.02
EMPLOYEELOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5327.98 | 4255.22 | 1072.76 | 0.8 | 3.02
EXERCISECENTERFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2480.5 | 1872.79 | 607.71 | 0.76 | 3.18
FRONTLOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18699.82 | 14649.51 | 4050.31 | 0.78 | 3.01
FRONTOFFICEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6639.97 | 5303.04 | 1336.92 | 0.8 | 3.02
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2432.1 | 1942.41 | 489.69 | 0.8 | 3.23
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2515.87 | 2009.31 | 506.56 | 0.8 | 3.23
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2582.08 | 2062.19 | 519.89 | 0.8 | 3.23
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1695.28 | 1353.94 | 341.33 | 0.8 | 3.23
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1773.7 | 1416.57 | 357.13 | 0.8 | 3.23
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3715.36 | 2967.3 | 748.07 | 0.8 | 3.02
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11365.95 | 9077.47 | 2288.47 | 0.8 | 3.02
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9496.91 | 7584.76 | 1912.15 | 0.8 | 3.02
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11113.45 | 8875.82 | 2237.64 | 0.8 | 3.02
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3015.22 | 2408.12 | 607.1 | 0.8 | 3.02
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2190.66 | 1749.58 | 441.08 | 0.8 | 3.23
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8560.44 | 6836.84 | 1723.6 | 0.8 | 3.02
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2636.62 | 2105.75 | 530.87 | 0.8 | 3.23
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7941.93 | 6342.87 | 1599.07 | 0.8 | 3.02
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2152.01 | 1718.71 | 433.3 | 0.8 | 3.23
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3667.2 | 2928.83 | 738.37 | 0.8 | 3.02
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11368.74 | 9079.7 | 2289.04 | 0.8 | 3.02
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9656.93 | 7712.56 | 1944.37 | 0.8 | 3.02
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11349.6 | 9064.42 | 2285.18 | 0.8 | 3.02
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3055.04 | 2439.93 | 615.12 | 0.8 | 3.02
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2237.7 | 1787.15 | 450.55 | 0.8 | 3.23
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8254.97 | 6592.87 | 1662.09 | 0.8 | 3.02
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2182.62 | 1743.16 | 439.46 | 0.8 | 3.23
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8132.51 | 6495.07 | 1637.44 | 0.8 | 3.02
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2178.37 | 1739.77 | 438.6 | 0.8 | 3.23
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3681.73 | 2940.44 | 741.3 | 0.8 | 3.02
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11449.6 | 9144.28 | 2305.32 | 0.8 | 3.02
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9684.3 | 7734.42 | 1949.88 | 0.8 | 3.02
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11446.63 | 9141.91 | 2304.72 | 0.8 | 3.02
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3077.14 | 2457.58 | 619.57 | 0.8 | 3.02
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2514.11 | 2007.91 | 506.2 | 0.8 | 3.23
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9183.88 | 7334.75 | 1849.13 | 0.8 | 3.02
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2381.94 | 1902.35 | 479.59 | 0.8 | 3.23
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9102.86 | 7270.04 | 1832.81 | 0.8 | 3.02
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2453.86 | 1959.79 | 494.07 | 0.8 | 3.23
LAUNDRYROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26981.56 | 21548.97 | 5432.6 | 0.8 | 3.02
MECHANICALROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1176.59 | 939.69 | 236.9 | 0.8 | 3.23
MEETINGROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11118.47 | 8234.66 | 2883.81 | 0.74 | 2.97
RESTROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1726.9 | 1379.2 | 347.7 | 0.8 | 3.23
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 2026.65 | 1
CORRIDORFLR2 PTAC HEAT COIL | Coil:Heating:Electric | 1693.69 | 1
CORRIDORFLR3 PTAC HEAT COIL | Coil:Heating:Electric | 2099.78 | 1
CORRIDORFLR4 PTAC HEAT COIL | Coil:Heating:Electric | 3677.48 | 1
EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 4739.88 | 1
EXERCISECENTERFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 5924.85 | 1
FRONTLOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 22811.96 | 1
FRONTOFFICEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 6321.69 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1423.51 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1317.34 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1354.29 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1541.35 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 101.08 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1233.41 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1255.65 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1493.81 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1473.92 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1249.94 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 2181.65 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 4560.93 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 3551.74 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 4465.94 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1380.98 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1346.32 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 4208.15 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 867.64 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 4338.32 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1295.57 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 2234.01 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 4676.54 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 3753.99 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 4647.57 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1419.85 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1393.64 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 4604.24 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1167.42 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 4580.18 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1351.65 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2595.03 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 6114.59 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 4932.01 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 6093.81 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1777.44 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1771.48 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 6087.14 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1645.22 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 6042.48 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1738.57 | 1
LAUNDRYROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 7702.31 | 1
MECHANICALROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 961.71 | 1
MEETINGROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 23121.63 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1305.94 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1170.27 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1197.23 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1375.57 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 803.58 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 798.45 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 815.12 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 830.33 | 1
RESTROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 671.64 | 1
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDORFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 337.53 | 1 | PTAC Fan
CORRIDORFLR2 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.33 | 208.74 | 1 | PTAC Fan
CORRIDORFLR3 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.3 | 193.75 | 1 | PTAC Fan
CORRIDORFLR4 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.36 | 230.8 | 1 | PTAC Fan
EMPLOYEELOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.32 | 204.88 | 1 | PTAC Fan
EXERCISECENTERFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.06 | 1 | PTAC Fan
FRONTLOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.08 | 689.24 | 1 | PTAC Fan
FRONTOFFICEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.4 | 255.33 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.48 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 4.14 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.26 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.85 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.32 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 93.52 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.74 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 99.29 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 65.19 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 68.2 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.22 | 142.87 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.69 | 437.06 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 365.19 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.67 | 427.35 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 115.94 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.24 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 329.18 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 101.39 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 305.39 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.75 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.22 | 141.02 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.69 | 437.17 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 371.34 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.69 | 436.43 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 117.48 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 86.05 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 317.43 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 83.93 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 312.72 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 83.77 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.22 | 141.57 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.69 | 440.27 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 372.39 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.69 | 440.16 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 118.33 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.68 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 353.15 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.59 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 350.03 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.36 | 1 | PTAC Fan
LAUNDRYROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.63 | 1037.53 | 1 | PTAC Fan
MECHANICALROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.07 | 45.24 | 1 | PTAC Fan
MEETINGROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 360.06 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 4.11 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.68 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.76 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.32 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.53 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.51 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.56 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.61 | 1 | Unit Heater Fans
RESTROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 66.41 | 1 | PTAC Fan
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 13465.6055 | 18.9642 | 43.0977 | 0 | 0.0002 | 569425.2203 | 5382.4523
February | 11726.8952 | 16.4118 | 36.8712 | 0 | 0.0002 | 487143.8282 | 4676.359
March | 13018.543 | 18.252 | 41.1397 | 0 | 0.0002 | 543543.2267 | 5194.9096
April | 12338.9154 | 17.3133 | 39.0827 | 0 | 0.0002 | 516367.5486 | 4925.2322
May | 13056.3028 | 18.4713 | 42.321 | 0 | 0.0002 | 559174.3323 | 5227.792
June | 12871.0412 | 18.3384 | 42.5457 | 0 | 0.0002 | 562159.9293 | 5167.4541
July | 13797.7628 | 19.8135 | 46.5967 | 0 | 0.0002 | 615707.1875 | 5556.0822
August | 13933.6404 | 20.0489 | 47.3131 | 0 | 0.0002 | 625177.555 | 5615.1159
September | 13045.998 | 18.6735 | 43.6723 | 0 | 0.0002 | 577056.8657 | 5246.8923
October | 12769.8903 | 18.0846 | 41.5111 | 0 | 0.0002 | 548475.292 | 5115.0982
November | 12384.5935 | 17.4567 | 39.7334 | 0 | 0.0002 | 524976.1013 | 4951.9539
December | 13540.8529 | 19.1468 | 43.8283 | 0 | 0.0002 | 579087.3991 | 5420.7439
Annual Sum or Average | 155950.041 | 220.9751 | 507.7128 | 0 | 0.0021 | 6708290 | 62480.0856
Minimum of Months | 11726.8952 | 16.4118 | 36.8712 | 0 | 0.0002 | 487143.8282 | 4676.359
Maximum of Months | 13933.6404 | 20.0489 | 47.3131 | 0 | 0.0002 | 625177.555 | 5615.1159
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 200643000000 | 120319.164 | 02-JAN-07:00 | 37896.934 | 51279.599 | 551.261 | 19856.591 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 171650000000 | 119590.29 | 21-FEB-20:45 | 57185.041 | 38824.77 | 1606.778 | 0 | 11238.923 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 191523000000 | 128556.54 | 29-MAR-19:00 | 57185.041 | 38824.77 | 2683.343 | 0 | 19128.607 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 181948000000 | 129437.158 | 29-APR-19:15 | 57040.442 | 38772.136 | 2780.694 | 0 | 20109.107 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 197031000000 | 135100.668 | 04-MAY-19:30 | 57185.041 | 38824.77 | 3471.735 | 0 | 24884.344 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 198083000000 | 137019.892 | 17-JUN-20:15 | 56764.46 | 36822.846 | 3960.137 | 0 | 28737.671 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 216951000000 | 144282.305 | 24-JUL-19:00 | 57185.041 | 38824.77 | 4541.979 | 0 | 32995.737 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 220288000000 | 144612.671 | 06-AUG-19:45 | 57112.741 | 38807.225 | 4561.895 | 0 | 33396.031 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 203332000000 | 149822.995 | 02-SEP-19:15 | 57040.442 | 38772.136 | 5099.427 | 0 | 38176.212 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 193261000000 | 130224.651 | 09-OCT-19:15 | 57112.741 | 38807.225 | 2859.794 | 0 | 20710.112 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 184981000000 | 126615.452 | 29-NOV-07:15 | 37896.934 | 51279.599 | 830.652 | 25873.488 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 204048000000 | 123943.38 | 11-DEC-07:15 | 37896.934 | 51279.599 | 736.456 | 23295.612 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2363740000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 171650000000 | 119590.29 |  | 37896.934 | 36822.846 | 551.261 | 0 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 220288000000 | 149822.995 |  | 57185.041 | 51279.599 | 5099.427 | 25873.488 | 38176.212 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 47070.8 | 6721.48 | 0 | 53792.28
Cost per Total Building Area ($/m2) | 9.22 | 1.32 | 0 | 10.53
Cost per Net Conditioned Building Area ($/m2) | 11.91 | 1.7 | 0 | 13.61

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3450.73 | 675.79 | 872.85
Net Site Energy | 3450.73 | 675.79 | 872.85
Total Source Energy | 10189.84 | 1995.58 | 2577.5
Net Source Energy | 10189.84 | 1995.58 | 2577.5
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 235.2 | 0 | 0 | 0 | 0 | 0
Cooling | 367.09 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.14 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 52.14 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 644.44 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2616.81 | 833.92 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.886 | 1.021 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.4 | 0.443 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.4 | 0.443 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.4 | 0.443 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.4 | 0.443 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 72.38 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 111.83 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9384.71 | 7495.15 | 1889.56 | 0.8 | 3.02
CORRIDORFLR2 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5340.6 | 4265.3 | 1075.3 | 0.8 | 3.02
CORRIDORFLR3 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4967.12 | 3967.02 | 1000.1 | 0.8 | 3.02
CORRIDORFLR4 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5930.87 | 4736.72 | 1194.15 | 0.8 | 3.02
EMPLOYEELOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6904.35 | 5018.43 | 1885.91 | 0.73 | 2.95
EXERCISECENTERFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3584.81 | 2423.63 | 1161.18 | 0.68 | 2.91
FRONTLOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 22254.71 | 15046.04 | 7208.67 | 0.68 | 2.91
FRONTOFFICEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9820.66 | 6979.42 | 2841.25 | 0.71 | 2.94
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2334.93 | 1760.42 | 574.51 | 0.75 | 3.18
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2389.55 | 1808.71 | 580.84 | 0.76 | 3.19
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2500.11 | 1906.72 | 593.39 | 0.76 | 3.19
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2261.84 | 1698.84 | 563 | 0.75 | 3.18
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2257.64 | 1695.15 | 562.49 | 0.75 | 3.18
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3610.69 | 2818.46 | 792.22 | 0.78 | 3.01
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10176.15 | 7837.59 | 2338.56 | 0.77 | 2.99
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8138.31 | 6302.33 | 1835.97 | 0.77 | 3
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10013.85 | 7692.57 | 2321.28 | 0.77 | 2.99
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2732.14 | 2127.42 | 604.73 | 0.78 | 3
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2443.06 | 1932.38 | 510.69 | 0.79 | 3.23
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9770.2 | 7499.37 | 2270.83 | 0.77 | 2.99
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2864.77 | 2246.55 | 618.22 | 0.78 | 3.01
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9275.85 | 7059.22 | 2216.63 | 0.76 | 2.99
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2401.05 | 1893.92 | 507.13 | 0.79 | 3.22
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3572.42 | 2790.24 | 782.18 | 0.78 | 3.01
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10201.36 | 7860.09 | 2341.28 | 0.77 | 3
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8242.78 | 6395.69 | 1847.09 | 0.78 | 3
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10187.65 | 7847.51 | 2340.14 | 0.77 | 3
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2761.43 | 2153.65 | 607.79 | 0.78 | 3
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2483.59 | 1969.46 | 514.13 | 0.79 | 3.23
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9520.56 | 7276.88 | 2243.68 | 0.76 | 2.99
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2365.62 | 1861.56 | 504.06 | 0.79 | 3.22
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9417.41 | 7185.07 | 2232.34 | 0.76 | 2.99
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2424.96 | 1915.78 | 509.19 | 0.79 | 3.22
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3669.49 | 2890.81 | 778.69 | 0.79 | 3.01
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10336.21 | 8029.63 | 2306.58 | 0.78 | 3
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8364.41 | 6534.12 | 1830.29 | 0.78 | 3.01
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10351.24 | 8030.8 | 2320.45 | 0.78 | 3
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2794.74 | 2196.8 | 597.94 | 0.79 | 3.01
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2720.03 | 2172.37 | 547.66 | 0.8 | 3.02
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9754.42 | 7712.64 | 2041.78 | 0.79 | 3.02
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2515.82 | 1998.85 | 516.97 | 0.79 | 3.23
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9688.04 | 7651.96 | 2036.08 | 0.79 | 3.01
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2646.4 | 2113.56 | 532.84 | 0.8 | 3.02
LAUNDRYROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28069.85 | 22382.08 | 5687.77 | 0.8 | 3.02
MECHANICALROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1283.72 | 960.23 | 323.5 | 0.75 | 3.18
MEETINGROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12437.3 | 8408.65 | 4028.65 | 0.68 | 2.91
RESTROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1659.35 | 1325.25 | 334.1 | 0.8 | 3.23
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 3913.97 | 1
CORRIDORFLR2 PTAC HEAT COIL | Coil:Heating:Electric | 3005.43 | 1
CORRIDORFLR3 PTAC HEAT COIL | Coil:Heating:Electric | 3436.55 | 1
CORRIDORFLR4 PTAC HEAT COIL | Coil:Heating:Electric | 5508.1 | 1
EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 6402.75 | 1
EXERCISECENTERFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 8003.43 | 1
FRONTLOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 30814.96 | 1
FRONTOFFICEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 9815.11 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 2976.74 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 2611.22 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 2647.38 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2914.11 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 55.93 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 109.16 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 128.3 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 291.72 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1890.71 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1914.29 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 2184.11 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 2174.37 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1920.24 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 3385.1 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 6937.8 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 5400.62 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 6816.43 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 2001.01 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1971.47 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 6598 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1502.89 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 6721.97 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1913.29 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 3453.69 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 7073.11 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 5620.88 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 7030.34 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 2046.64 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 2023.88 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 6997.89 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1820.46 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 6965.9 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1967.15 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 3940.47 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 8985.91 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 7184.6 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 8952.63 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2523.49 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2526.02 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 8952.41 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2433.43 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 8898.77 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2470.07 | 1
LAUNDRYROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 10404.46 | 1
MECHANICALROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1502.41 | 1
MEETINGROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 31233.26 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 2824.87 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 2439.34 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 2472.14 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2728.97 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1756.66 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1601.5 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1619.87 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1638.24 | 1
RESTROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1063.82 | 1
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDORFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 360.87 | 1 | PTAC Fan
CORRIDORFLR2 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.32 | 205.36 | 1 | PTAC Fan
CORRIDORFLR3 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.3 | 191 | 1 | PTAC Fan
CORRIDORFLR4 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.36 | 228.06 | 1 | PTAC Fan
EMPLOYEELOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.34 | 213.64 | 1 | PTAC Fan
EXERCISECENTERFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.89 | 1 | PTAC Fan
FRONTLOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.9 | 570.46 | 1 | PTAC Fan
FRONTOFFICEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 287.28 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.43 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.27 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.39 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.23 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.18 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.35 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.41 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.92 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.87 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.46 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 86.72 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75.72 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75.53 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.21 | 132.02 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 361.01 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 292.3 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 353.16 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 99.35 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.98 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 343.94 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 105.83 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 320.19 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 89.85 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.21 | 130.79 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 362.23 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 297.36 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 361.53 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.77 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.03 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 331.92 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.06 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 326.97 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.06 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.22 | 136.94 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 373.88 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 306.35 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 373.33 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.78 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.59 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 366.95 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 95.65 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 363.6 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 101.76 | 1 | PTAC Fan
LAUNDRYROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.69 | 1075.61 | 1 | PTAC Fan
MECHANICALROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.07 | 42.56 | 1 | PTAC Fan
MEETINGROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 318.81 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 8.95 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.73 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.83 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.65 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.57 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 5.08 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.13 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.19 | 1 | Unit Heater Fans
RESTROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 63.81 | 1 | PTAC Fan
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 92126.8148 | 163.9795 | 482.0928 | 0 | 0.0015 | 110978.3241 | 39568.086
February | 74751.751 | 132.6564 | 388.7924 | 0 | 0.0012 | 89499.9217 | 32067.6411
March | 72171.5167 | 127.6476 | 372.7955 | 0 | 0.0011 | 85816.8466 | 30919.6522
April | 65863.5277 | 116.4489 | 339.9606 | 0 | 0.001 | 78258.2616 | 28213.1781
May | 74191.4883 | 131.7257 | 386.2598 | 0 | 0.0012 | 88917.006 | 31833.3778
June | 80551.5953 | 143.6383 | 423.0907 | 0 | 0.0013 | 97396.3195 | 34621.6193
July | 88689.4125 | 158.5255 | 468.0881 | 0 | 0.0014 | 107755.3234 | 38155.2605
August | 86292.4913 | 154.2187 | 455.3023 | 0 | 0.0014 | 104811.9587 | 37121.9186
September | 77451.1663 | 138.1528 | 407.0646 | 0 | 0.0012 | 93707.1485 | 33293.16
October | 71745.2605 | 127.494 | 374.1928 | 0 | 0.0011 | 86139.3428 | 30794.4391
November | 68433.8637 | 121.3418 | 355.3166 | 0 | 0.0011 | 81793.6661 | 29347.52
December | 85341.4291 | 151.7927 | 445.9305 | 0 | 0.0014 | 102653.5741 | 36643.3463
Annual Sum or Average | 937610.3172 | 1667.6219 | 4898.8865 | 0 | 0.0148 | 1127730 | 402579.1989
Minimum of Months | 65863.5277 | 116.4489 | 339.9606 | 0 | 0.001 | 78258.2616 | 28213.1781
Maximum of Months | 92126.8148 | 163.9795 | 482.0928 | 0 | 0.0015 | 110978.3241 | 39568.086
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 257517000000 | 213841.862 | 07-JAN-06:15 | 29080.703 | 25635.382 | 4908.666 | 143482.333 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 207678000000 | 157629.462 | 09-FEB-06:15 | 30863.644 | 37264.076 | 2268.815 | 76498.148 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 199132000000 | 125373.121 | 14-MAR-19:00 | 57185.041 | 38824.77 | 2071.512 | 0 | 16557.02 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 181592000000 | 126270.051 | 28-APR-19:30 | 57185.041 | 38824.77 | 2316.916 | 0 | 17208.545 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 206325000000 | 141546.671 | 30-MAY-19:15 | 57185.041 | 38824.77 | 3881.879 | 0 | 30920.202 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 226001000000 | 152319.484 | 16-JUN-19:30 | 57185.041 | 38824.77 | 4885.542 | 0 | 40689.352 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 250038000000 | 161847.727 | 13-JUL-19:30 | 57185.041 | 38824.77 | 5710.792 | 0 | 49392.345 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 243208000000 | 166862.481 | 04-AUG-19:15 | 57185.041 | 38824.77 | 6066.735 | 0 | 54051.157 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 217440000000 | 145692.54 | 06-SEP-19:15 | 57185.041 | 38824.77 | 4241.105 | 0 | 34706.846 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 199880000000 | 135527.184 | 30-OCT-19:30 | 57185.041 | 38824.77 | 3196.918 | 0 | 25585.677 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 189796000000 | 134945.534 | 02-NOV-19:30 | 57185.041 | 38824.77 | 3160.796 | 0 | 25040.148 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 238200000000 | 192233.111 | 31-DEC-07:15 | 30422.587 | 41100.106 | 3184.323 | 106791.317 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2616810000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 181592000000 | 125373.121 |  | 29080.703 | 25635.382 | 2071.512 | 0 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 257517000000 | 213841.862 |  | 57185.041 | 41100.106 | 6066.735 | 143482.333 | 54051.157 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 70032.57 | 7535.92 | 0 | 77568.49
Cost per Total Building Area ($/m2) | 13.72 | 1.48 | 0 | 15.19
Cost per Net Conditioned Building Area ($/m2) | 17.71 | 1.91 | 0 | 19.62

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3334.56 | 653.04 | 843.47
Net Site Energy | 3334.56 | 653.04 | 843.47
Total Source Energy | 9213.8 | 1804.43 | 2330.61
Net Source Energy | 9213.8 | 1804.43 | 2330.61
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 145.42 | 0 | 0 | 0 | 0 | 0
Cooling | 341.92 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.17 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 53.6 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 641.74 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2503.35 | 831.22 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.914 | 1.059 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.422 | 0.47 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.422 | 0.47 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.422 | 0.47 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.422 | 0.47 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 72.38 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 111.83 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9860.96 | 7875.51 | 1985.45 | 0.8 | 3.02
CORRIDORFLR2 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5675.77 | 4532.99 | 1142.79 | 0.8 | 3.02
CORRIDORFLR3 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5203.66 | 4155.93 | 1047.73 | 0.8 | 3.02
CORRIDORFLR4 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6088.94 | 4862.97 | 1225.98 | 0.8 | 3.02
EMPLOYEELOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6339.99 | 5063.46 | 1276.52 | 0.8 | 3.02
EXERCISECENTERFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2892.6 | 2189.82 | 702.78 | 0.76 | 2.98
FRONTLOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16973.61 | 13127.27 | 3846.34 | 0.77 | 3
FRONTOFFICEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7721.21 | 6166.59 | 1554.63 | 0.8 | 3.02
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2135.38 | 1705.43 | 429.95 | 0.8 | 3.23
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2203.01 | 1759.44 | 443.56 | 0.8 | 3.23
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2216.39 | 1770.13 | 446.26 | 0.8 | 3.23
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1901.12 | 1518.34 | 382.78 | 0.8 | 3.23
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2062.2 | 1646.99 | 415.21 | 0.8 | 3.23
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3650.84 | 2915.76 | 735.08 | 0.8 | 3.02
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10298.55 | 8224.99 | 2073.56 | 0.8 | 3.02
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8335.31 | 6657.04 | 1678.27 | 0.8 | 3.02
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10082.44 | 8052.4 | 2030.05 | 0.8 | 3.02
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2680.7 | 2140.95 | 539.74 | 0.8 | 3.02
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2442.04 | 1950.35 | 491.69 | 0.8 | 3.23
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9909.96 | 7914.64 | 1995.32 | 0.8 | 3.02
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3063.7 | 2446.84 | 616.86 | 0.8 | 3.02
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9158.66 | 7314.61 | 1844.05 | 0.8 | 3.02
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2447.92 | 1955.04 | 492.87 | 0.8 | 3.23
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3605.07 | 2879.21 | 725.86 | 0.8 | 3.02
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10350.76 | 8266.69 | 2084.07 | 0.8 | 3.02
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8478.72 | 6771.57 | 1707.15 | 0.8 | 3.02
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10328 | 8248.51 | 2079.49 | 0.8 | 3.02
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2716.21 | 2169.31 | 546.89 | 0.8 | 3.02
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2489.44 | 1988.2 | 501.24 | 0.8 | 3.23
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9501.58 | 7588.48 | 1913.09 | 0.8 | 3.02
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2504.86 | 2000.52 | 504.34 | 0.8 | 3.23
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9351.93 | 7468.97 | 1882.96 | 0.8 | 3.02
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2464.36 | 1968.18 | 496.19 | 0.8 | 3.23
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3737.16 | 2984.71 | 752.46 | 0.8 | 3.02
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10474.05 | 8365.16 | 2108.9 | 0.8 | 3.02
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8569.46 | 6844.04 | 1725.42 | 0.8 | 3.02
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10447.19 | 8343.7 | 2103.49 | 0.8 | 3.02
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2758.18 | 2202.83 | 555.34 | 0.8 | 3.02
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2749.45 | 2195.86 | 553.59 | 0.8 | 3.02
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10282.93 | 8212.52 | 2070.41 | 0.8 | 3.02
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2656.22 | 2121.4 | 534.82 | 0.8 | 3.02
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10184.65 | 8134.02 | 2050.62 | 0.8 | 3.02
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2719.4 | 2171.86 | 547.54 | 0.8 | 3.02
LAUNDRYROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 32221.82 | 25734.12 | 6487.69 | 0.8 | 3.02
MECHANICALROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1048.24 | 837.18 | 211.06 | 0.8 | 3.23
MEETINGROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11387.45 | 8260.51 | 3126.95 | 0.73 | 2.95
RESTROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1695.81 | 1354.37 | 341.44 | 0.8 | 3.23
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 3206.13 | 1
CORRIDORFLR2 PTAC HEAT COIL | Coil:Heating:Electric | 2472.04 | 1
CORRIDORFLR3 PTAC HEAT COIL | Coil:Heating:Electric | 2898.56 | 1
CORRIDORFLR4 PTAC HEAT COIL | Coil:Heating:Electric | 5021.44 | 1
EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 5198.41 | 1
EXERCISECENTERFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 6498.01 | 1
FRONTLOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 25018.76 | 1
FRONTOFFICEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 8361.29 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 2441.43 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 2159.82 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 2194.37 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2464.68 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 73.23 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 91.9 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 258.81 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1633.66 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1656.8 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1924.71 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1918.23 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1665.9 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 2924.96 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 5903.91 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 4585.43 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 5785.77 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1740.53 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1714.17 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 5575.74 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1235.69 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 5698.72 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1657.94 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 2989.84 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 6032.52 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 4798.39 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 5990.94 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1783.93 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1764.05 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 5968.68 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1548.4 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 5938.03 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1709.48 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 3486.07 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 7990.12 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 6397.75 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 7957.93 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2271.65 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2277.36 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 7967.96 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2174.87 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 7915.73 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2223.96 | 1
LAUNDRYROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 8447.41 | 1
MECHANICALROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1318.48 | 1
MEETINGROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 25358.38 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 2287.73 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1986.38 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 2018.28 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2279.55 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1476.45 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1359.54 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1376.91 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1394.58 | 1
RESTROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 960.28 | 1
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDORFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 379.19 | 1 | PTAC Fan
CORRIDORFLR2 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.34 | 218.25 | 1 | PTAC Fan
CORRIDORFLR3 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.31 | 200.1 | 1 | PTAC Fan
CORRIDORFLR4 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.37 | 234.14 | 1 | PTAC Fan
EMPLOYEELOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.38 | 243.79 | 1 | PTAC Fan
EXERCISECENTERFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 98.64 | 1 | PTAC Fan
FRONTLOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.95 | 607.84 | 1 | PTAC Fan
FRONTOFFICEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 296.91 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.21 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.15 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.28 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.3 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.28 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.35 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.98 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.11 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.71 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 85.23 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 73.1 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 79.3 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.22 | 140.39 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 396.01 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 320.52 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 387.7 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.08 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 93.9 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 381.07 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 117.81 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 352.18 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.13 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.22 | 138.63 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 398.02 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 326.03 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 397.15 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.45 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 95.73 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 365.37 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.32 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 359.61 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.76 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.23 | 143.71 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 402.76 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 329.52 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 401.73 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.06 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 105.73 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 395.41 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 102.14 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 391.63 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.57 | 1 | PTAC Fan
LAUNDRYROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.95 | 1239.03 | 1 | PTAC Fan
MECHANICALROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.06 | 40.31 | 1 | PTAC Fan
MEETINGROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 350.64 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.63 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.5 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.62 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.6 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.57 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.13 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.2 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.26 | 1 | Unit Heater Fans
RESTROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 65.21 | 1 | PTAC Fan
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 62953.2792 | 107.0074 | 270.1589 | 0 | 0.0011 | 280901.8271 | 26679.3736
February | 53799.9834 | 91.2407 | 229.7526 | 0 | 0.0009 | 238887.3188 | 22779.8388
March | 56226.5015 | 95.2095 | 239.3226 | 0 | 0.0009 | 248836.8149 | 23792.9072
April | 53270.8847 | 90.2723 | 227.1083 | 0 | 0.0009 | 236137.4379 | 22548.8366
May | 56753.9314 | 96.4651 | 243.5299 | 0 | 0.001 | 253213.8664 | 24051.6588
June | 58651.5732 | 100.0769 | 253.7635 | 0 | 0.001 | 263857.0598 | 24893.7503
July | 66617.851 | 114.0989 | 290.5538 | 0 | 0.0011 | 302113.5206 | 28317.0147
August | 64833.663 | 111.0143 | 282.6161 | 0 | 0.0011 | 293859.8449 | 27555.79
September | 58477.453 | 99.8996 | 253.6589 | 0 | 0.001 | 263749.0513 | 24831.604
October | 56585.4917 | 96.349 | 243.7279 | 0 | 0.001 | 253420.9346 | 23996.9637
November | 54176.6216 | 92.0321 | 232.1874 | 0 | 0.0009 | 241419.986 | 22954.2904
December | 62844.3506 | 106.9539 | 270.4042 | 0 | 0.0011 | 281157.8211 | 26646.1281
Annual Sum or Average | 705191.5845 | 1200.6197 | 3036.7839 | 0 | 0.0119 | 3157560 | 299048.1563
Minimum of Months | 53270.8847 | 90.2723 | 227.1083 | 0 | 0.0009 | 236137.4379 | 22548.8366
Maximum of Months | 66617.851 | 114.0989 | 290.5538 | 0 | 0.0011 | 302113.5206 | 28317.0147
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 222702000000 | 185705.235 | 06-JAN-06:15 | 30863.644 | 37264.076 | 3888.422 | 102954.314 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 189393000000 | 162504.639 | 16-FEB-06:15 | 30863.644 | 37264.076 | 3076.669 | 80565.471 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 197281000000 | 127588.068 | 26-MAR-19:15 | 57112.741 | 38807.225 | 2737.665 | 0 | 18195.658 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 187213000000 | 133197.174 | 25-APR-19:30 | 57185.041 | 38824.77 | 3364.883 | 0 | 23087.702 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 200751000000 | 140455.625 | 23-MAY-19:15 | 57185.041 | 38824.77 | 4262.893 | 0 | 29448.143 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 209189000000 | 143836.955 | 27-JUN-19:30 | 57185.041 | 38824.77 | 4641.245 | 0 | 32451.12 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 239519000000 | 151334.999 | 17-JUL-19:30 | 57185.041 | 38824.77 | 5371.469 | 0 | 39218.94 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 232976000000 | 147975.229 | 29-AUG-19:15 | 57185.041 | 38824.77 | 5055.027 | 0 | 36175.613 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 209103000000 | 141095.421 | 01-SEP-19:15 | 57185.041 | 38824.77 | 4334.577 | 0 | 30016.255 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 200915000000 | 135284.073 | 01-OCT-19:15 | 57112.741 | 38807.225 | 3658.104 | 0 | 24971.224 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 191401000000 | 123609.442 | 18-NOV-20:00 | 57040.442 | 38772.136 | 349.73 | 16451.111 | 261.246 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 222905000000 | 173221.787 | 12-DEC-07:15 | 37896.934 | 51279.599 | 2409.92 | 70900.555 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2503350000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 187213000000 | 123609.442 |  | 30863.644 | 37264.076 | 349.73 | 0 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 239519000000 | 185705.235 |  | 57185.041 | 51279.599 | 5371.469 | 102954.314 | 39218.94 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 25871.21 | 6020.89 | 0 | 31892.11
Cost per Total Building Area ($/m2) | 5.07 | 1.18 | 0 | 6.25
Cost per Net Conditioned Building Area ($/m2) | 6.54 | 1.52 | 0 | 8.07

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3638.86 | 712.63 | 920.44
Net Site Energy | 3638.86 | 712.63 | 920.44
Total Source Energy | 10446.32 | 2045.81 | 2642.37
Net Source Energy | 10446.32 | 2045.81 | 2642.37
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 396.6 | 0 | 0 | 0 | 0 | 0
Cooling | 346.43 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.28 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 54.67 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 689.17 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2760.21 | 878.65 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.334 | 0.364 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.334 | 0.364 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.334 | 0.364 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.334 | 0.364 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 72.38 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 111.83 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9397.28 | 7505.19 | 1892.09 | 0.8 | 3.02
CORRIDORFLR2 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5290.45 | 4225.25 | 1065.21 | 0.8 | 3.02
CORRIDORFLR3 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4908.15 | 3919.92 | 988.23 | 0.8 | 3.02
CORRIDORFLR4 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5497.57 | 4390.66 | 1106.91 | 0.8 | 3.02
EMPLOYEELOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7260.74 | 5174.89 | 2085.85 | 0.71 | 2.94
EXERCISECENTERFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3621.52 | 2448.45 | 1173.07 | 0.68 | 2.91
FRONTLOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 22399.34 | 15143.82 | 7255.52 | 0.68 | 2.91
FRONTOFFICEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9355.55 | 6743.45 | 2612.1 | 0.72 | 2.95
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2281.12 | 1744.52 | 536.59 | 0.76 | 3.2
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2336.29 | 1793.73 | 542.56 | 0.77 | 3.2
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2438.51 | 1884.87 | 553.64 | 0.77 | 3.2
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2165.6 | 1644.55 | 521.05 | 0.76 | 3.19
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2171.56 | 1649.83 | 521.73 | 0.76 | 3.19
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3401.02 | 2685.7 | 715.33 | 0.79 | 3.01
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10002.61 | 7814.43 | 2188.18 | 0.78 | 3.01
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8031.39 | 6309.79 | 1721.59 | 0.79 | 3.01
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9840.87 | 7669.05 | 2171.82 | 0.78 | 3
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2676.89 | 2112.19 | 564.71 | 0.79 | 3.01
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2465.3 | 1930.46 | 534.83 | 0.78 | 3.22
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9473.66 | 7361.96 | 2111.7 | 0.78 | 3
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2778.31 | 2207.27 | 571.04 | 0.79 | 3.02
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8981.37 | 6920.29 | 2061.08 | 0.77 | 3
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2305.66 | 1841.43 | 464.23 | 0.8 | 3.23
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3371.17 | 2658.79 | 712.38 | 0.79 | 3.01
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10027.46 | 7836.8 | 2190.66 | 0.78 | 3.01
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8137.26 | 6405.2 | 1732.06 | 0.79 | 3.01
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10016.54 | 7826.14 | 2190.4 | 0.78 | 3.01
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2705.4 | 2137.92 | 567.48 | 0.79 | 3.01
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2502.13 | 1963.68 | 538.44 | 0.78 | 3.22
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9224.74 | 7138.44 | 2086.31 | 0.77 | 3
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2408.95 | 1876.91 | 532.04 | 0.78 | 3.21
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9122.31 | 7046.56 | 2075.74 | 0.77 | 3
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2335.17 | 1864.99 | 470.17 | 0.8 | 3.23
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3366.03 | 2677.39 | 688.64 | 0.8 | 3.02
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9881.46 | 7740.1 | 2141.36 | 0.78 | 3.01
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8012.1 | 6311.59 | 1700.51 | 0.79 | 3.01
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9875.34 | 7734.59 | 2140.75 | 0.78 | 3.01
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2665.83 | 2111.64 | 554.19 | 0.79 | 3.02
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2603.98 | 2079.68 | 524.3 | 0.8 | 3.23
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9190.07 | 7339.7 | 1850.37 | 0.8 | 3.02
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2382.64 | 1902.91 | 479.73 | 0.8 | 3.23
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9113.74 | 7274.83 | 1838.9 | 0.8 | 3.02
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2537.07 | 2026.24 | 510.83 | 0.8 | 3.23
LAUNDRYROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28093.37 | 22436.92 | 5656.45 | 0.8 | 3.02
MECHANICALROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1232.28 | 934.83 | 297.45 | 0.76 | 3.19
MEETINGROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12579.01 | 8504.45 | 4074.55 | 0.68 | 2.91
RESTROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1654.04 | 1321 | 333.03 | 0.8 | 3.23
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 4582.16 | 1
CORRIDORFLR2 PTAC HEAT COIL | Coil:Heating:Electric | 3409.65 | 1
CORRIDORFLR3 PTAC HEAT COIL | Coil:Heating:Electric | 3830.76 | 1
CORRIDORFLR4 PTAC HEAT COIL | Coil:Heating:Electric | 5818.83 | 1
EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 6919.49 | 1
EXERCISECENTERFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 8649.36 | 1
FRONTLOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 33301.91 | 1
FRONTOFFICEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 10939.32 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 3453.67 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 3000.16 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 3035.32 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 3296.41 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 104.9 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 145.93 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 164.07 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 323.07 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 2110.38 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 2134.88 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 2410.12 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 2396.06 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 2137.05 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 3743.58 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 7705.61 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 6011.54 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 7576.41 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 2196.68 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 2164.48 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 7350.25 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1698.22 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 7477.65 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 2102.88 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 3808.69 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 7820.82 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 6219.21 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 7775.68 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 2238.63 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 2213.94 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 7736.93 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 2018.62 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 7703.2 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 2153.11 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 4275.65 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 9652.44 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 7716.96 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 9617.21 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2695.8 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2696.45 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 9612.97 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2609.98 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 9557.25 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2635.91 | 1
LAUNDRYROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 11244.16 | 1
MECHANICALROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1669.64 | 1
MEETINGROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 33753.97 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 3300.18 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 2827.26 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 2859.11 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 3109.66 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 2033.4 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1826.8 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1844.29 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1860.06 | 1
RESTROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1183.29 | 1
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDORFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 361.36 | 1 | PTAC Fan
CORRIDORFLR2 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.32 | 203.44 | 1 | PTAC Fan
CORRIDORFLR3 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.3 | 188.73 | 1 | PTAC Fan
CORRIDORFLR4 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.33 | 211.4 | 1 | PTAC Fan
EMPLOYEELOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.34 | 213.94 | 1 | PTAC Fan
EXERCISECENTERFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 92.83 | 1 | PTAC Fan
FRONTLOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.9 | 574.17 | 1 | PTAC Fan
FRONTOFFICEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 283.57 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.12 | 11.03 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.58 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.69 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.11 | 10.53 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.34 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.47 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.52 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.03 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 79.63 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.29 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 87.22 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 74.38 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 74.67 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.2 | 127.59 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 366.41 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 297.9 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 358.5 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.24 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.78 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 342.93 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 105.62 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 318.93 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.66 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.2 | 126.12 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 367.63 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 303.11 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 367.01 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 101.65 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 92.59 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 330.78 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 87.72 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 325.78 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 89.79 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.2 | 128.29 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 364.1 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 298.96 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 363.8 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.69 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.13 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 353.39 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.62 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 350.05 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 97.56 | 1 | PTAC Fan
LAUNDRYROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.7 | 1080.28 | 1 | PTAC Fan
MECHANICALROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.07 | 42.23 | 1 | PTAC Fan
MEETINGROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 322.44 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.11 | 10.54 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.03 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.13 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.11 | 9.93 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.49 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.83 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.89 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.94 | 1 | Unit Heater Fans
RESTROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 63.6 | 1 | PTAC Fan
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 74398.0226 | 131.7769 | 209.5365 | 0 | 0.0015 | 137723.1255 | 31890.2892
February | 57116.546 | 100.5544 | 158.8691 | 0 | 0.0012 | 104418.3349 | 24424.1075
March | 50265.3365 | 87.7058 | 137.25 | 0 | 0.001 | 90205.8041 | 21419.1754
April | 44333.9303 | 77.1787 | 120.4757 | 0 | 0.0009 | 79180.3819 | 18874.6878
May | 50151.0431 | 87.9133 | 138.2628 | 0 | 0.001 | 90873.1021 | 21409.3653
June | 52783.2287 | 93.0788 | 147.3151 | 0 | 0.0011 | 96824.9735 | 22585.7511
July | 56818.9566 | 100.5354 | 159.6853 | 0 | 0.0012 | 104956.8023 | 24345.1121
August | 56278.0562 | 99.6305 | 158.3351 | 0 | 0.0012 | 104069.5513 | 24118.3424
September | 49021.6709 | 86.44 | 136.7985 | 0 | 0.001 | 89912.7563 | 20975.6567
October | 46186.7064 | 80.9931 | 127.4284 | 0 | 0.0009 | 83752.3412 | 19719.7885
November | 48172.1414 | 84.4829 | 132.9329 | 0 | 0.001 | 87370.2137 | 20568.2706
December | 65289.6818 | 115.3535 | 182.9381 | 0 | 0.0013 | 120239.53 | 27958.2972
Annual Sum or Average | 650815.3205 | 1145.6433 | 1809.8276 | 0 | 0.0133 | 1189530 | 278288.8437
Minimum of Months | 44333.9303 | 77.1787 | 120.4757 | 0 | 0.0009 | 79180.3819 | 18874.6878
Maximum of Months | 74398.0226 | 131.7769 | 209.5365 | 0 | 0.0015 | 137723.1255 | 31890.2892
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 319576000000 | 239434.036 | 06-JAN-06:15 | 30863.644 | 37264.076 | 4743.672 | 155827.866 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 242295000000 | 220481.151 | 04-FEB-06:15 | 29080.703 | 25635.382 | 4691.786 | 150338.502 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 209316000000 | 145296.141 | 05-MAR-21:00 | 56692.16 | 36787.756 | 687.432 | 40394.014 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 183732000000 | 134638.403 | 02-APR-19:00 | 57112.741 | 38807.225 | 3212.62 | 0 | 24771.038 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 210864000000 | 157209.823 | 27-MAY-19:45 | 57040.442 | 38772.136 | 5405.118 | 0 | 45257.349 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 224675000000 | 156647.588 | 29-JUN-19:00 | 57185.041 | 38824.77 | 5403.395 | 0 | 44499.604 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 243544000000 | 162540.224 | 15-JUL-19:00 | 57040.442 | 38772.136 | 5905.428 | 0 | 50087.44 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 241486000000 | 161875.43 | 25-AUG-19:15 | 57185.041 | 38824.77 | 5747.094 | 0 | 49383.746 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 208636000000 | 141700.186 | 14-SEP-19:15 | 57185.041 | 38824.77 | 3975.9 | 0 | 30979.696 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 194341000000 | 137162.359 | 08-OCT-19:15 | 57112.741 | 38807.225 | 3538.714 | 0 | 26968.899 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 202736000000 | 141545.508 | 30-NOV-07:15 | 37896.934 | 51279.599 | 902.199 | 40731.997 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 279007000000 | 249389.355 | 31-DEC-06:15 | 29080.703 | 25635.382 | 5589.625 | 178348.867 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2760210000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 183732000000 | 134638.403 |  | 29080.703 | 25635.382 | 687.432 | 0 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 319576000000 | 249389.355 |  | 57185.041 | 51279.599 | 5905.428 | 178348.867 | 50087.44 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 43235.47 | 7038.83 | 0 | 50274.3
Cost per Total Building Area ($/m2) | 8.47 | 1.38 | 0 | 9.85
Cost per Net Conditioned Building Area ($/m2) | 10.94 | 1.78 | 0 | 12.72

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3429.5 | 671.63 | 867.48
Net Site Energy | 3429.5 | 671.63 | 867.48
Total Source Energy | 9806.83 | 1920.57 | 2480.62
Net Source Energy | 9806.83 | 1920.57 | 2480.62
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 262.14 | 0 | 0 | 0 | 0 | 0
Cooling | 271.56 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.08 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 46.7 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 697.31 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2542.71 | 886.79 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.823 | 0.939 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.334 | 0.364 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.334 | 0.364 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.334 | 0.364 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.334 | 0.364 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 72.38 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 111.83 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9401.03 | 7508.18 | 1892.85 | 0.8 | 3.02
CORRIDORFLR2 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5443.72 | 4347.65 | 1096.06 | 0.8 | 3.02
CORRIDORFLR3 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5013.1 | 4003.73 | 1009.36 | 0.8 | 3.02
CORRIDORFLR4 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5477.51 | 4374.65 | 1102.87 | 0.8 | 3.02
EMPLOYEELOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6005.33 | 4796.19 | 1209.14 | 0.8 | 3.02
EXERCISECENTERFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2453.15 | 1959.22 | 493.93 | 0.8 | 3.23
FRONTLOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15660.39 | 12507.25 | 3153.14 | 0.8 | 3.02
FRONTOFFICEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7332.65 | 5856.26 | 1476.39 | 0.8 | 3.02
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2140.97 | 1709.9 | 431.07 | 0.8 | 3.23
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2211.12 | 1765.92 | 445.2 | 0.8 | 3.23
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2236.66 | 1786.32 | 450.34 | 0.8 | 3.23
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1817.54 | 1451.58 | 365.95 | 0.8 | 3.23
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1956.05 | 1562.21 | 393.84 | 0.8 | 3.23
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3454.96 | 2759.32 | 695.64 | 0.8 | 3.02
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10316.15 | 8239.05 | 2077.1 | 0.8 | 3.02
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8408.24 | 6715.29 | 1692.95 | 0.8 | 3.02
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10102.02 | 8068.03 | 2033.99 | 0.8 | 3.02
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2702.33 | 2158.23 | 544.1 | 0.8 | 3.02
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2355.07 | 1880.89 | 474.18 | 0.8 | 3.23
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9476.35 | 7568.34 | 1908.01 | 0.8 | 3.02
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2926.93 | 2337.61 | 589.32 | 0.8 | 3.02
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8763.05 | 6998.65 | 1764.39 | 0.8 | 3.02
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2338.15 | 1867.38 | 470.77 | 0.8 | 3.23
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3416.6 | 2728.68 | 687.91 | 0.8 | 3.02
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10384.23 | 8293.42 | 2090.81 | 0.8 | 3.02
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8571.57 | 6845.73 | 1725.84 | 0.8 | 3.02
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10365.6 | 8278.54 | 2087.06 | 0.8 | 3.02
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2747.87 | 2194.6 | 553.27 | 0.8 | 3.02
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2404.15 | 1920.09 | 484.06 | 0.8 | 3.23
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9111.45 | 7276.91 | 1834.54 | 0.8 | 3.02
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2404.02 | 1919.98 | 484.04 | 0.8 | 3.23
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8968.55 | 7162.78 | 1805.77 | 0.8 | 3.02
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2358.12 | 1883.33 | 474.8 | 0.8 | 3.23
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3408.93 | 2722.56 | 686.37 | 0.8 | 3.02
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9987.29 | 7976.4 | 2010.89 | 0.8 | 3.02
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8203.52 | 6551.78 | 1651.73 | 0.8 | 3.02
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9978.25 | 7969.18 | 2009.07 | 0.8 | 3.02
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2658.56 | 2123.27 | 535.29 | 0.8 | 3.02
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2558.7 | 2043.52 | 515.18 | 0.8 | 3.23
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9489.06 | 7578.49 | 1910.57 | 0.8 | 3.02
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2442.96 | 1951.08 | 491.88 | 0.8 | 3.23
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9396.32 | 7504.42 | 1891.9 | 0.8 | 3.02
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2523.03 | 2015.03 | 508 | 0.8 | 3.23
LAUNDRYROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30491.84 | 24352.47 | 6139.37 | 0.8 | 3.02
MECHANICALROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1062.91 | 848.9 | 214.01 | 0.8 | 3.23
MEETINGROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9874.52 | 7550.38 | 2324.14 | 0.76 | 2.99
RESTROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1676.67 | 1339.08 | 337.59 | 0.8 | 3.23
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 4367.48 | 1
CORRIDORFLR2 PTAC HEAT COIL | Coil:Heating:Electric | 3212.75 | 1
CORRIDORFLR3 PTAC HEAT COIL | Coil:Heating:Electric | 3633.19 | 1
CORRIDORFLR4 PTAC HEAT COIL | Coil:Heating:Electric | 5734.7 | 1
EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 6305.33 | 1
EXERCISECENTERFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 7881.66 | 1
FRONTLOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 30759.63 | 1
FRONTOFFICEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 10377.47 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 3276.07 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 2848.05 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 2882.23 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 3158.28 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 101.21 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 137.75 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 155.7 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 325.03 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 2020.44 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 2045.06 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 2322.63 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 2308.35 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 2047.26 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 3579.89 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 7313.68 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 5704.46 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 7182.75 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 2100.09 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 2066.46 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 6950.93 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1595.01 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 7077.07 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 2003.64 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 3643.31 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 7426.59 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 5910.31 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 7380.89 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 2141.42 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 2114.32 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 7331.68 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1913.9 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 7297.85 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 2052.24 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 4135.87 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 9365 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 7494.2 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 9329.42 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2625.13 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2623.97 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 9311.87 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2535.75 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 9256 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2562.08 | 1
LAUNDRYROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 10246.16 | 1
MECHANICALROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1610.71 | 1
MEETINGROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 30758.05 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 3124.34 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 2676.05 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 2707.38 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2972.86 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1961.37 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1761.65 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1778.01 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1792.94 | 1
RESTROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1161.76 | 1
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDORFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 361.5 | 1 | PTAC Fan
CORRIDORFLR2 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.33 | 209.33 | 1 | PTAC Fan
CORRIDORFLR3 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.3 | 192.77 | 1 | PTAC Fan
CORRIDORFLR4 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.33 | 210.63 | 1 | PTAC Fan
EMPLOYEELOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.36 | 230.92 | 1 | PTAC Fan
EXERCISECENTERFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.33 | 1 | PTAC Fan
FRONTLOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.95 | 602.19 | 1 | PTAC Fan
FRONTOFFICEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 281.96 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.13 | 11.71 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.11 | 10.18 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.11 | 10.3 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.12 | 11.28 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.36 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.49 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.56 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.16 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.33 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 85.02 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 86.01 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 69.89 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75.22 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.21 | 132.85 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 396.69 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 323.32 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 388.46 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.91 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.56 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 364.4 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 112.55 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 336.97 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 89.91 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.21 | 131.38 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 399.31 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 329.6 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 398.59 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 105.66 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 92.45 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 350.37 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 92.44 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 344.87 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.68 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.21 | 131.08 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 384.04 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 315.45 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 383.7 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 102.23 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 98.39 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 364.89 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 93.94 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 361.32 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 97.02 | 1 | PTAC Fan
LAUNDRYROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.84 | 1172.51 | 1 | PTAC Fan
MECHANICALROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.06 | 40.87 | 1 | PTAC Fan
MEETINGROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 344.57 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.12 | 11.16 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.56 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.67 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.11 | 10.62 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.01 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.3 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.35 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.41 | 1 | Unit Heater Fans
RESTROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 64.47 | 1 | PTAC Fan
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 66957.841 | 115.1364 | 196.8918 | 0 | 0.0014 | 4670410 | 28428.6966
February | 54445.119 | 93.2281 | 158.6792 | 0 | 0.0011 | 3763920 | 23078.1796
March | 52209.9171 | 88.9276 | 150.4537 | 0 | 0.0011 | 3568740 | 22084.9883
April | 46662.9205 | 79.3264 | 133.9152 | 0 | 0.0009 | 3176420 | 19723.789
May | 49628.5298 | 84.6583 | 143.4763 | 0 | 0.001 | 3403250 | 21005.3838
June | 51532.5852 | 88.3365 | 150.5364 | 0 | 0.0011 | 3570780 | 21852.8556
July | 57024.1434 | 98.1332 | 167.964 | 0 | 0.0012 | 3984230 | 24218.638
August | 55931.2517 | 96.2582 | 164.7658 | 0 | 0.0011 | 3908370 | 23755.0374
September | 50927.0526 | 87.4394 | 149.2771 | 0 | 0.001 | 3540930 | 21609.6944
October | 49267.4002 | 84.2658 | 143.2405 | 0 | 0.001 | 3397690 | 20874.1381
November | 48794.6935 | 83.3483 | 141.4718 | 0 | 0.001 | 3355720 | 20663.3177
December | 63154.148 | 108.537 | 185.4941 | 0 | 0.0013 | 4400040 | 26808.0514
Annual Sum or Average | 646535.602 | 1107.595 | 1886.1659 | 0 | 0.0132 | 44740500 | 274102.7699
Minimum of Months | 46662.9205 | 79.3264 | 133.9152 | 0 | 0.0009 | 3176420 | 19723.789
Maximum of Months | 66957.841 | 115.1364 | 196.8918 | 0 | 0.0014 | 4670410 | 28428.6966
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 265430000000 | 217784.705 | 07-JAN-06:15 | 29080.703 | 25635.382 | 5068.478 | 147265.364 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 213913000000 | 203287.714 | 26-FEB-06:15 | 29080.703 | 25635.382 | 4513.833 | 133323.018 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 202820000000 | 151956.853 | 04-MAR-06:15 | 29080.703 | 25635.382 | 2680.159 | 83825.831 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 180524000000 | 125790.744 | 30-APR-19:30 | 57112.741 | 38807.225 | 2483.256 | 0 | 16652.743 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 193415000000 | 132972.432 | 25-MAY-19:00 | 57185.041 | 38824.77 | 3331.332 | 0 | 22896.511 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 202936000000 | 145623.896 | 25-JUN-20:30 | 56692.16 | 36787.756 | 5073.448 | 0 | 36335.753 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 226433000000 | 141138.538 | 30-JUL-19:00 | 57112.741 | 38807.225 | 4354.498 | 0 | 30129.294 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 222122000000 | 145139.941 | 11-AUG-19:45 | 57185.041 | 38824.77 | 4691.781 | 0 | 33703.57 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 201240000000 | 141782.117 | 02-SEP-19:15 | 57040.442 | 38772.136 | 4381.604 | 0 | 30853.157 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 193099000000 | 129103.944 | 06-OCT-19:15 | 57185.041 | 38824.77 | 2857.802 | 0 | 19501.553 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 190714000000 | 128159.854 | 30-NOV-07:15 | 37896.934 | 51279.599 | 594.984 | 27653.558 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 250065000000 | 225562.822 | 11-DEC-06:15 | 30863.644 | 37264.076 | 4664.452 | 142035.871 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2542710000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 180524000000 | 125790.744 |  | 29080.703 | 25635.382 | 594.984 | 0 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 265430000000 | 225562.822 |  | 57185.041 | 51279.599 | 5073.448 | 147265.364 | 36335.753 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 51598.38 | 7899.04 | 0 | 59497.42
Cost per Total Building Area ($/m2) | 10.11 | 1.55 | 0 | 11.65
Cost per Net Conditioned Building Area ($/m2) | 13.05 | 2 | 0 | 15.05

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3704.97 | 725.58 | 937.16
Net Site Energy | 3704.97 | 725.58 | 937.16
Total Source Energy | 10500.42 | 2056.4 | 2656.06
Net Source Energy | 10500.42 | 2056.4 | 2656.06
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 521.45 | 0 | 0 | 0 | 0 | 0
Cooling | 225.03 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.03 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 43.75 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 762.99 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2752.49 | 952.47 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.772 | 0.873 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.341 | 0.371 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.341 | 0.371 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.341 | 0.371 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.341 | 0.371 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 72.38 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 111.83 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8424.92 | 6728.61 | 1696.31 | 0.8 | 3.02
CORRIDORFLR2 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4965.02 | 3965.34 | 999.68 | 0.8 | 3.02
CORRIDORFLR3 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4602.6 | 3675.89 | 926.71 | 0.8 | 3.02
CORRIDORFLR4 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5067.56 | 4047.24 | 1020.33 | 0.8 | 3.02
EMPLOYEELOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6125.27 | 4630.91 | 1494.37 | 0.76 | 2.98
EXERCISECENTERFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3172.12 | 2179.71 | 992.41 | 0.69 | 2.92
FRONTLOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19652.58 | 13584.42 | 6068.16 | 0.69 | 2.92
FRONTOFFICEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7343.32 | 5543.22 | 1800.1 | 0.75 | 2.98
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1884.35 | 1504.94 | 379.42 | 0.8 | 3.23
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1949.88 | 1557.28 | 392.6 | 0.8 | 3.23
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1979.37 | 1580.84 | 398.54 | 0.8 | 3.23
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1666.63 | 1308.55 | 358.08 | 0.79 | 3.22
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1758.21 | 1392.24 | 365.97 | 0.79 | 3.23
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3075.17 | 2456 | 619.17 | 0.8 | 3.02
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9326.01 | 7448.27 | 1877.74 | 0.8 | 3.02
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7602.22 | 6071.56 | 1530.67 | 0.8 | 3.02
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9127.23 | 7289.51 | 1837.72 | 0.8 | 3.02
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2459.08 | 1963.96 | 495.12 | 0.8 | 3.23
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2152.55 | 1719.14 | 433.4 | 0.8 | 3.23
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8592.56 | 6862.5 | 1730.07 | 0.8 | 3.02
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2658.48 | 2123.21 | 535.27 | 0.8 | 3.02
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7942.91 | 6343.65 | 1599.26 | 0.8 | 3.02
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2142.09 | 1710.79 | 431.3 | 0.8 | 3.23
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3045.86 | 2432.59 | 613.27 | 0.8 | 3.02
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9400.44 | 7507.71 | 1892.73 | 0.8 | 3.02
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7764.21 | 6200.92 | 1563.28 | 0.8 | 3.02
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9384.55 | 7495.02 | 1889.53 | 0.8 | 3.02
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2507.33 | 2002.49 | 504.84 | 0.8 | 3.23
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2209.98 | 1765.01 | 444.97 | 0.8 | 3.23
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8288.57 | 6619.71 | 1668.86 | 0.8 | 3.02
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2188.92 | 1748.19 | 440.73 | 0.8 | 3.23
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8158.41 | 6515.75 | 1642.65 | 0.8 | 3.02
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2175.27 | 1737.29 | 437.98 | 0.8 | 3.23
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3069.56 | 2451.52 | 618.04 | 0.8 | 3.02
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9131.64 | 7293.03 | 1838.61 | 0.8 | 3.02
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7501.09 | 5990.79 | 1510.31 | 0.8 | 3.02
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9124.48 | 7287.31 | 1837.17 | 0.8 | 3.02
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2440.93 | 1949.46 | 491.47 | 0.8 | 3.23
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2379.24 | 1900.2 | 479.05 | 0.8 | 3.23
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8762.33 | 6998.08 | 1764.25 | 0.8 | 3.02
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2257.5 | 1802.96 | 454.54 | 0.8 | 3.23
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8677.38 | 6930.23 | 1747.14 | 0.8 | 3.02
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2345.01 | 1872.85 | 472.15 | 0.8 | 3.23
LAUNDRYROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27859.3 | 22249.97 | 5609.32 | 0.8 | 3.02
MECHANICALROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 965.61 | 762.11 | 203.5 | 0.79 | 3.22
MEETINGROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12002 | 8114.35 | 3887.65 | 0.68 | 2.91
RESTROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1464.44 | 1169.58 | 294.86 | 0.8 | 3.23
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 4879.67 | 1
CORRIDORFLR2 PTAC HEAT COIL | Coil:Heating:Electric | 3572.59 | 1
CORRIDORFLR3 PTAC HEAT COIL | Coil:Heating:Electric | 4002.32 | 1
CORRIDORFLR4 PTAC HEAT COIL | Coil:Heating:Electric | 6139.18 | 1
EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 7082.62 | 1
EXERCISECENTERFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 8853.28 | 1
FRONTLOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 34310.59 | 1
FRONTOFFICEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 11401.58 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 3648.98 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 3155.06 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 3191.38 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 3475.38 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 125.05 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 159.16 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 177.8 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 350.26 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 2200.66 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 2225.67 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 2501.78 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 2487.42 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 2227.89 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 3878.35 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 8014.18 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 6262.85 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 7881.93 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 2273.78 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 2242.08 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 7659.11 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1778.2 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 7787.66 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 2180.18 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 3945.02 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 8136.32 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 6478.55 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 8090.86 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 2317.7 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 2293.93 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 8055.34 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 2104.1 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 8020.84 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 2232.48 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 4449.78 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 10110.33 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 8091.94 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 10074.99 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2810.41 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2814 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 10075.15 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2736.52 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 10018.32 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2752.55 | 1
LAUNDRYROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 11509.26 | 1
MECHANICALROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1735.31 | 1
MEETINGROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 34549.76 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 3493.46 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 2981.53 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 3014.57 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 3287.09 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 2137.96 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1908.95 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1926.47 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1944.65 | 1
RESTROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1231.01 | 1
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDORFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 323.97 | 1 | PTAC Fan
CORRIDORFLR2 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.3 | 190.92 | 1 | PTAC Fan
CORRIDORFLR3 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.28 | 176.99 | 1 | PTAC Fan
CORRIDORFLR4 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.31 | 194.86 | 1 | PTAC Fan
EMPLOYEELOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.33 | 208.23 | 1 | PTAC Fan
EXERCISECENTERFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.98 | 1 | PTAC Fan
FRONTLOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.84 | 534.89 | 1 | PTAC Fan
FRONTOFFICEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.39 | 248.74 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.13 | 11.9 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.11 | 10.29 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.11 | 10.41 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.12 | 11.33 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.41 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.52 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.58 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.14 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 72.46 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 74.98 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.11 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 61.73 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 66.36 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 118.25 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 358.62 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 292.33 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 350.97 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.56 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.77 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 330.41 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 102.23 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 305.43 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.37 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 117.12 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 361.48 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 298.56 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 360.87 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.42 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.98 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 318.72 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.17 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 313.72 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 83.65 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 118.03 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 351.14 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 288.44 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 350.87 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 93.86 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.49 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 336.94 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 86.81 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 333.67 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.17 | 1 | PTAC Fan
LAUNDRYROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.68 | 1071.28 | 1 | PTAC Fan
MECHANICALROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.06 | 36.18 | 1 | PTAC Fan
MEETINGROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 307.65 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.12 | 11.39 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.72 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.11 | 9.83 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.12 | 10.72 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 6.97 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.23 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.28 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.34 | 1 | Unit Heater Fans
RESTROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 56.31 | 1 | PTAC Fan
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 75938.5581 | 134.4151 | 213.5807 | 0 | 0.0016 | 140380.9497 | 32541.9839
February | 64163.708 | 113.2537 | 179.4238 | 0 | 0.0013 | 117929.2467 | 27465.5833
March | 56070.8414 | 98.0862 | 153.9182 | 0 | 0.0011 | 101161.8068 | 23916.9915
April | 44223.2577 | 76.7124 | 119.2841 | 0 | 0.0009 | 78396.1614 | 18801.4207
May | 45473.8848 | 79.0387 | 123.1682 | 0 | 0.0009 | 80949.5049 | 19348.1152
June | 47651.5495 | 83.3331 | 130.725 | 0 | 0.001 | 85918.1188 | 20323.3488
July | 53131.5313 | 93.3813 | 147.2722 | 0 | 0.0011 | 96795.4892 | 22704.9903
August | 51283.2775 | 90.0948 | 142.0251 | 0 | 0.001 | 93346.7009 | 21911.5269
September | 45820.3126 | 80.2269 | 126.015 | 0 | 0.0009 | 82822.8868 | 19551.5372
October | 45680.4463 | 79.7456 | 124.8603 | 0 | 0.0009 | 82063.0126 | 19469.2511
November | 52907.1798 | 92.8736 | 146.2809 | 0 | 0.0011 | 96143.5502 | 22598.2742
December | 70625.862 | 124.8879 | 198.2364 | 0 | 0.0015 | 130295.0853 | 30253.5291
Annual Sum or Average | 652970.409 | 1146.0494 | 1804.79 | 0 | 0.0133 | 1186200 | 278886.552
Minimum of Months | 44223.2577 | 76.7124 | 119.2841 | 0 | 0.0009 | 78396.1614 | 18801.4207
Maximum of Months | 75938.5581 | 134.4151 | 213.5807 | 0 | 0.0016 | 140380.9497 | 32541.9839
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 325743000000 | 250043.817 | 09-JAN-07:15 | 37896.934 | 51279.599 | 3901.008 | 146231.498 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 273646000000 | 249203.41 | 02-FEB-07:15 | 37896.934 | 51279.599 | 3888.133 | 145403.965 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 234738000000 | 203818.342 | 09-MAR-06:15 | 30863.644 | 37264.076 | 3277.036 | 121678.807 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 181912000000 | 120792.431 | 15-APR-19:15 | 57040.442 | 38772.136 | 1789.074 | 0 | 12456.001 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 187837000000 | 130814.151 | 31-MAY-19:00 | 57185.041 | 38824.77 | 3024.529 | 0 | 21045.033 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 199367000000 | 146066.542 | 14-JUN-19:00 | 57185.041 | 38824.77 | 4547.834 | 0 | 34774.119 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 224607000000 | 152229.042 | 06-JUL-19:00 | 57185.041 | 38824.77 | 5188.277 | 0 | 40296.176 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 216604000000 | 153407.356 | 13-AUG-19:30 | 57112.741 | 38807.225 | 5269.213 | 0 | 41483.397 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 192184000000 | 138064.053 | 08-SEP-19:15 | 57185.041 | 38824.77 | 3642.486 | 0 | 27676.977 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 190421000000 | 131637.313 | 07-OCT-19:15 | 57040.442 | 38772.136 | 3071.383 | 0 | 22018.574 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 223094000000 | 187359.535 | 25-NOV-07:15 | 30350.287 | 41065.016 | 2670.365 | 102539.089 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 302340000000 | 243986.061 | 31-DEC-06:15 | 29080.703 | 25635.382 | 4980.288 | 173554.91 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2752490000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 181912000000 | 120792.431 |  | 29080.703 | 25635.382 | 1789.074 | 0 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 325743000000 | 250043.817 |  | 57185.041 | 51279.599 | 5269.213 | 173554.91 | 41483.397 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 43501.69 | 7635.76 | 0 | 51137.45
Cost per Total Building Area ($/m2) | 8.52 | 1.5 | 0 | 10.01
Cost per Net Conditioned Building Area ($/m2) | 11 | 1.93 | 0 | 12.94

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4433.29 | 868.22 | 1121.39
Net Site Energy | 4433.29 | 868.22 | 1121.39
Total Source Energy | 13252.05 | 2595.28 | 3352.08
Net Source Energy | 13252.05 | 2595.28 | 3352.08
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 1209.75 | 0 | 0 | 0 | 0 | 0
Cooling | 170.16 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 166.03 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 50.32 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 852.32 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3391.49 | 1041.8 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.71 | 0.794 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.334 | 0.364 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.334 | 0.364 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.334 | 0.364 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.334 | 0.364 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.525 | 0.407 | 0.316 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 3.525 | 0.407 | 0.316 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.525 | 0.407 | 0.316 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.525 | 0.407 | 0.316 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 72.38 | 3.52 | 0.407 | 0.316
Non-North Total or Average |  |  | 111.83 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7204.8 | 5754.15 | 1450.65 | 0.8 | 3.02
CORRIDORFLR2 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4627.04 | 3695.41 | 931.63 | 0.8 | 3.02
CORRIDORFLR3 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4321.39 | 3451.3 | 870.09 | 0.8 | 3.02
CORRIDORFLR4 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4612.89 | 3684.11 | 928.78 | 0.8 | 3.02
EMPLOYEELOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5022.44 | 4011.2 | 1011.24 | 0.8 | 3.02
EXERCISECENTERFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1963.5 | 1568.16 | 395.34 | 0.8 | 3.23
FRONTLOUNGEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14559.68 | 11628.17 | 2931.52 | 0.8 | 3.02
FRONTOFFICEFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5399.92 | 4312.68 | 1087.25 | 0.8 | 3.02
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1927.31 | 1539.25 | 388.05 | 0.8 | 3.23
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1999.75 | 1597.11 | 402.64 | 0.8 | 3.23
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1990.19 | 1589.48 | 400.72 | 0.8 | 3.23
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1508.37 | 1204.66 | 303.7 | 0.8 | 3.23
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1467.92 | 1172.36 | 295.56 | 0.8 | 3.23
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2897.1 | 2313.79 | 583.32 | 0.8 | 3.02
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10056.76 | 8031.88 | 2024.88 | 0.8 | 3.02
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8334.67 | 6656.53 | 1678.14 | 0.8 | 3.02
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9831.29 | 7851.81 | 1979.48 | 0.8 | 3.02
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2615.46 | 2088.85 | 526.61 | 0.8 | 3.23
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1962.75 | 1567.56 | 395.19 | 0.8 | 3.23
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8020.92 | 6405.95 | 1614.97 | 0.8 | 3.02
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2520.65 | 2013.13 | 507.52 | 0.8 | 3.23
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7390.59 | 5902.53 | 1488.06 | 0.8 | 3.02
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1977.2 | 1579.1 | 398.1 | 0.8 | 3.23
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2888 | 2306.52 | 581.48 | 0.8 | 3.02
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10181.14 | 8131.22 | 2049.92 | 0.8 | 3.02
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8571.22 | 6845.45 | 1725.77 | 0.8 | 3.02
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10164.01 | 8117.54 | 2046.47 | 0.8 | 3.02
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2687.38 | 2146.29 | 541.09 | 0.8 | 3.02
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2036.61 | 1626.55 | 410.06 | 0.8 | 3.23
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7774.33 | 6209.01 | 1565.32 | 0.8 | 3.02
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2048.01 | 1635.65 | 412.36 | 0.8 | 3.23
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7648.46 | 6108.48 | 1539.98 | 0.8 | 3.02
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2024.13 | 1616.59 | 407.55 | 0.8 | 3.23
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3333.52 | 2662.34 | 671.19 | 0.8 | 3.02
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10054.15 | 8029.8 | 2024.35 | 0.8 | 3.02
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8489.11 | 6779.87 | 1709.24 | 0.8 | 3.02
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10054.18 | 8029.83 | 2024.36 | 0.8 | 3.02
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2659.3 | 2123.87 | 535.44 | 0.8 | 3.02
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2159.02 | 1724.31 | 434.71 | 0.8 | 3.23
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8170.68 | 6525.55 | 1645.12 | 0.8 | 3.02
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2090.83 | 1669.85 | 420.98 | 0.8 | 3.23
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8090.33 | 6461.38 | 1628.94 | 0.8 | 3.02
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2153.89 | 1720.21 | 433.67 | 0.8 | 3.23
LAUNDRYROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26266.92 | 20978.22 | 5288.71 | 0.8 | 3.02
MECHANICALROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1181.57 | 943.67 | 237.9 | 0.8 | 3.23
MEETINGROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8099.75 | 6468.9 | 1630.84 | 0.8 | 3.02
RESTROOMFLR1 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1391.86 | 1111.62 | 280.24 | 0.8 | 3.23
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
CORRIDORFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 6943.39 | 1
CORRIDORFLR2 PTAC HEAT COIL | Coil:Heating:Electric | 4785.77 | 1
CORRIDORFLR3 PTAC HEAT COIL | Coil:Heating:Electric | 5242.97 | 1
CORRIDORFLR4 PTAC HEAT COIL | Coil:Heating:Electric | 8000.66 | 1
EMPLOYEELOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 8770.72 | 1
EXERCISECENTERFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 10963.4 | 1
FRONTLOUNGEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 44939.44 | 1
FRONTOFFICEFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 14877.79 | 1
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 5159.24 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 4380.14 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 4416.72 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 4793.75 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 281.81 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 270.77 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 289.66 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 520.81 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 2871.99 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 2898.78 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 3191.92 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 3177.93 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 2905.54 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 4985.07 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 10302.09 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 8068.12 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 10151.34 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 2856.87 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 2825.56 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 9969.26 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 2396.36 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 10060.26 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 2752.92 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 5054.68 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 10431.01 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 8296.68 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 10379.1 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 2903.39 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 2878.63 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 10345.31 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 2726.83 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 10300.31 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 2806.31 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 5709.63 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 12997.31 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 10389.68 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 12956.84 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 3542 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 3550.88 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 12952.06 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 3524.61 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 12888.4 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 3479.11 | 1
LAUNDRYROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 14915.32 | 1
MECHANICALROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 2263.98 | 1
MEETINGROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 42784.47 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 4998.52 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 4200.19 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 4233.99 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 4597.57 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 2996.92 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 2601.81 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 2616.01 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2638.45 | 1
RESTROOMFLR1 PTAC HEAT COIL | Coil:Heating:Electric | 1613.11 | 1
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
CORRIDORFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 277.05 | 1 | PTAC Fan
CORRIDORFLR2 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.28 | 177.92 | 1 | PTAC Fan
CORRIDORFLR3 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.26 | 166.17 | 1 | PTAC Fan
CORRIDORFLR4 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.28 | 177.38 | 1 | PTAC Fan
EMPLOYEELOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.3 | 193.13 | 1 | PTAC Fan
EXERCISECENTERFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75.5 | 1 | PTAC Fan
FRONTLOUNGEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.88 | 559.87 | 1 | PTAC Fan
FRONTOFFICEFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.33 | 207.64 | 1 | PTAC Fan
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.17 | 16.24 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.15 | 13.79 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.15 | 13.91 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.16 | 15.09 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.89 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.85 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.91 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.64 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 74.11 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.9 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.53 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 58 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 56.45 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 111.4 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 386.72 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 320.5 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 378.05 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.57 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75.47 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 308.43 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.93 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 284.19 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.03 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 111.05 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 391.5 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 329.59 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 390.84 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.34 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.31 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 298.95 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.75 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 294.11 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 77.83 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.2 | 128.18 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 386.62 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 326.43 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 386.62 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 102.26 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 83.02 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 314.19 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 80.4 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 311.1 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.82 | 1 | PTAC Fan
LAUNDRYROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 1.59 | 1010.05 | 1 | PTAC Fan
MECHANICALROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.07 | 45.44 | 1 | PTAC Fan
MEETINGROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 311.46 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.17 | 15.74 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.14 | 13.22 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.14 | 13.33 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.16 | 14.48 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.44 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.19 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.24 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.31 | 1 | Unit Heater Fans
RESTROOMFLR1 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.08 | 53.52 | 1 | PTAC Fan
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.8 | 0.34 | 0.67
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 101048.4659 | 124.9634 | 695.6146 | 0 | 0.0024 | 139609.9836 | 40087.4429
February | 82959.0601 | 102.4584 | 568.275 | 0 | 0.0019 | 114052.4843 | 32890.4155
March | 64706.0872 | 79.432 | 433.1348 | 0 | 0.0015 | 86928.3862 | 25579.4026
April | 44790.9793 | 54.5361 | 290.4425 | 0 | 0.001 | 58289.183 | 17637.6095
May | 40795.8976 | 49.4774 | 260.4689 | 0 | 0.0009 | 52273.1116 | 16034.521
June | 42144.1158 | 51.2393 | 271.73 | 0 | 0.0009 | 54533.5012 | 16583.943
July | 45153.2098 | 55.0162 | 293.608 | 0 | 0.001 | 58924.602 | 17786.2541
August | 43138.7048 | 52.5289 | 279.8242 | 0 | 0.001 | 56158.2089 | 16987.6878
September | 39786.3653 | 48.387 | 256.8274 | 0 | 0.0009 | 51542.7458 | 15658.3568
October | 50084.1107 | 61.2143 | 329.6497 | 0 | 0.0011 | 66158.4792 | 19757.8445
November | 73708.6562 | 90.8118 | 500.2659 | 0 | 0.0017 | 100402.4018 | 29188.7951
December | 90015.9351 | 111.1449 | 616.0063 | 0 | 0.0021 | 123632.0379 | 35683.7461
Annual Sum or Average | 718331.5878 | 881.2098 | 4795.8474 | 0 | 0.0163 | 962505.1254 | 283876.019
Minimum of Months | 39786.3653 | 48.387 | 256.8274 | 0 | 0.0009 | 51542.7458 | 15658.3568
Maximum of Months | 101048.4659 | 124.9634 | 695.6146 | 0 | 0.0024 | 139609.9836 | 40087.4429
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 491931000000 | 353949.354 | 13-JAN-06:15 | 30863.644 | 37264.076 | 6028.155 | 269058.7 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 401876000000 | 338608.621 | 05-FEB-06:15 | 29080.703 | 25635.382 | 6093.508 | 267064.25 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 306302000000 | 252714.169 | 14-MAR-06:00 | 37896.934 | 51279.599 | 3088.275 | 149714.582 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 205388000000 | 152325.647 | 09-APR-05:15 | 29080.703 | 25635.382 | 1798.393 | 85076.391 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 184190000000 | 120776.175 | 29-MAY-19:00 | 57112.741 | 38807.225 | 3197.428 | 0 | 21574.002 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 192155000000 | 129608.932 | 23-JUN-19:00 | 57185.041 | 38824.77 | 4101.917 | 0 | 29412.426 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 207627000000 | 135611.367 | 29-JUL-19:30 | 57040.442 | 38772.136 | 4686.826 | 0 | 35027.185 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 197880000000 | 128942.022 | 19-AUG-20:00 | 56764.46 | 36822.846 | 3039.396 | 0 | 21580.542 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 181616000000 | 123468.142 | 09-SEP-19:45 | 57040.442 | 38772.136 | 2126.482 | 0 | 14794.304 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 233117000000 | 168704.443 | 22-OCT-07:15 | 41071.521 | 57998.833 | 1057.492 | 57827.889 | 13.93 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 353779000000 | 232089.203 | 23-NOV-06:15 | 29080.703 | 25635.382 | 3707.548 | 162930.791 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 435631000000 | 295243.381 | 29-DEC-06:15 | 30863.644 | 37264.076 | 4731.706 | 211649.176 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 3391490000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 181616000000 | 120776.175 |  | 29080.703 | 25635.382 | 1057.492 | 0 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 491931000000 | 353949.354 |  | 57185.041 | 57998.833 | 6093.508 | 269058.7 | 35027.185 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 87914.01 | 4407.74 | 0 | 92321.75
Cost per Total Building Area ($/m2) | 17.22 | 0.86 | 0 | 18.08
Cost per Net Conditioned Building Area ($/m2) | 22.24 | 1.11 | 0 | 23.35

## Picture
DOE Commercial Building Benchmark - Small Hotel
First Floor
Upper Floors

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | 8.55 | 58.7 | 3060.79
|  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 7.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | 8.1
GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | 9.51 | 58.28 | 3038.89
|  |  | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | 10.73
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Ltg_Sch | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5 | 19.7 | 118.2 | 6163.29
|  |  | Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5 | 19.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15.72 | 78.6 | 4098.43
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Ltg_Sch | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.4 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.4 | 0.15 | 0.15 | 0.05 | 0.05 | 12.6 | 71.2 | 3712.57
|  |  | Sat, Sun, Hol | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.3 | 0.15 | 0.15 | 0.05 | 0.05 | 8.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | 12.05 | 60.25 | 3141.61
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Storage_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MechanicalRoom_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Ltg_Sch_Base | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 16 | 112 | 5840
LaundryRoom_Ltg_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 63 | 3285
Corridor_Ltg_Sch | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Exterior_Ltg_Sch | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 12 | 84 | 4380
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | 10.9 | 75.25 | 3923.75
|  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 10.25
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | 10.5
GuestRoom_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11 | 8.19 | 49.33 | 2572.21
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11 | 8.38
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Eqp_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21 | 9.02 | 45.1 | 2351.64
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Eqp_Sch | Fraction | Through 12/31 | WD | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | 14.27 | 83.07 | 4331.51
|  |  | Sat, Sun, Hol | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | 11.72
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08 | 66.48 | 3466.46
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Elec_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Gas_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.66 | 25.62 | 1335.9
ExerciseRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | 10.5 | 73.5 | 3832.5
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95 | 23.8 | 1241
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 2.72 | 19.04 | 992.8
BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 13.9 | 96.4 | 5026.57
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 13.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 13
GuestRoom_Occ_Sch | Fraction | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.43 | 0.43 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.31 | 0.54 | 0.54 | 0.54 | 0.77 | 0.77 | 0.89 | 1 | 1 | 15.19 | 90.86 | 4737.7
|  |  | Sat, Sun, Hol | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77 | 14.91
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Occ_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 6.6 | 38.6 | 2012.71
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Occ_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 12.1 | 68.2 | 3556.14
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 7.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 3.1 | 16.85 | 878.61
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 1.35
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2 | 19.2 | 1001.14
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 7.02 | 366.04
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Occ_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 14.5 | 101.5 | 5292.5
INFIL_SCH | fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_HALF_ON_SCH | fraction | Through 12/31 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
INFIL_QUARTER_ON_SCH | fraction | Through 12/31 | All | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 9 | 63.3 | 3300.64
|  |  | Sat, WinterDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 9.3
|  |  | Sun, Hol, Other | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 9
GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | 8 | 40 | 2085.71
|  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
LaundryRoom_SWH_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 2920
Hours_of_operation | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
HTGSETP_SCH_KEYCARD | Temperature | Through 12/31 | SummerDesign, WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 0 | 0
|  |  | Other | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 486
CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
CLGSETP_SCH_KEYCARD | Temperature | Through 12/31 | SummerDesign, WinterDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 0 | 0
|  |  | Other | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 594
SemiHeated_HtgSP_Sch | Temperature | Through 12/31 | All | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 172.8 | 1209.6 | 63072
Base_OccGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
Base_OccGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
VacGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | All | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 453.6 | 3175.2 | 165564
VacGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | All | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 559.2 | 3914.4 | 204108
CommonArea_HtgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
CommonArea_ClgSP_Sch | Temperature | Through 12/31 | All | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 573.6 | 4015.2 | 209364
Off During Unoccupied Period | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 70 | 3650
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHWSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720