## BuildingSummary
Building Summary Small Hotel post-1980 construction
|  | Value | Data Source
Program
| Building Name | Small Hotel
| Available Fuel Types | gas, electricity
| Principal Building Activity | Lodging
Form
| Total Floor Area (m2) | 4013.63 | PNNL - 17875 Technical Support Document: The Development of the Advanced Energy Design Guide for Highway Lodging Buildings
| Building Shape | Rectangle
| Aspect Ratio | 3
| Number of Floors | 4
Window Fraction (Window to Wall Ratio)
| South | 0.1524
| East | 0.0313
| North | 0.1139
| West | 0.0395
| Total | 0.1087
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | core zone with four perimeter zones on each floor plus attic
| Floor to Ceiling Height (m) | 3.35 1st floor, 2.74 upper floors
| Floor to Floor Height (m) | 3.35 1st floor, 2.74 upper floors
| Roof type | Attic | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel frame | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1694.66
| Net Dimensions - Total Area (m2) | 1510.43
| Wall to Skin Ratio | 0.6
Roof
| Construction Type | Attic | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1003.3894
| Net Dimensions - Total Area (m2) | 1003.3894
| Roof to Skin Ratio | 0.4
Window Dimensions (m2)
| South | 96.83
| East | 6.62
| North | 72.38
| West | 8.38
| Total Area (m2) | 184.21
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab w/carpet
| Dimensions - Total Area (m2) | 1661
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Dimensions - Total Area (m2)
Internal Mass
| Construction | 15 cm wood
Dimensions - Total Area (m2)
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.95 | See Benchmark Technical Report
HVAC
| System Type | MZ-CAV common areas, PTACs guest rooms | 2003 CBECS
| Heating Type | Gas furnace, unit heater, PTAC electric heat | 2003 CBECS
| Cooling Type | DX | 2003 CBECS
| Fan Control | Constant | 2003 CBECS
Service Water Heating
| SWH Type | gas water heater
| Fuel | gas
| Thermal Efficiency (%) | 78 | Standard 90.1-1989
| Temperature Setpoint (ºC ) | 60
| Water Consumption (m3 ) | 3470.09

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
REARSTAIRSFLR1 | Yes | 1 | 20.07 | 67.3 | 3.3533 | 35.77 | 0 |  | 0 | 9.9549 | 0 |  |  |  |  | 0 |  | 2.1693
CORRIDORFLR1 | Yes | 1 | 150.51 | 504.62 | 3.3527 | 32.7 | 9.82 |  | 0 | 9.5035 | 0 |  |  |  | 0.25 | 37.6275 |  | 0.26448
REARSTORAGEFLR1 | No | 1 | 20.07 | 67.3 | 3.3533 | 35.77 | 0 |  | 0 | 4.9774 | 0 |  |  |  |  | 0 |  | 2.1693
FRONTLOUNGEFLR1 | Yes | 1 | 163.06 | 546.7 | 3.3528 | 94.0201 | 14.83 | 3.0937 | 52.7076 | 14.1516 | 15.4389 |  |  | 8 |  | 421.6604 |  | 0.7019
RESTROOMFLR1 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 0 | 32.61 | 1 | 11.8232 | 10.767 |  |  |  |  | 0 | 188.7788 | 0.49608
MEETINGROOMFLR1 | Yes | 1 | 80.27 | 269.14 | 3.3529 | 32.7 | 4.94 | 1.8581 | 43.2009 | 22.9155 | 12.9047 |  |  | 10 |  | 432.0091 |  | 0.49588
MECHANICALROOMFLR1 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 0 |  | 0 | 10.3453 | 0 |  |  |  | 0.25 | 8.1525 |  | 0.49608
GUESTROOM101 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.64 | 21.74 | 1.5 | 20.6905 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49608
GUESTROOM102 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.64 | 21.74 | 1.5 | 20.6905 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49608
GUESTROOM103 | Yes | 1 | 32.61 | 109.34 | 3.353 | 13.29 | 1.65 | 21.74 | 1.5 | 20.6905 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49608
GUESTROOM104 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.65 | 21.74 | 1.5 | 20.6895 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49613
GUESTROOM105 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.64 | 21.74 | 1.5 | 20.6895 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49613
EMPLOYEELOUNGEFLR1 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.64 | 3.0937 | 10.5409 | 17.7339 | 77.1847 |  |  | 8 |  | 84.3269 |  | 0.49613
LAUNDRYROOMFLR1 | Yes | 1 | 97.83 | 327.99 | 3.3527 | 39.86 | 4.94 | 9.2903 | 10.5303 | 11.1826 | 21.8747 | 184.3145 | 255.5145 | 13 |  | 136.8942 |  | 0.496
ELEVATORCOREFLR1 | No | 1 | 15.05 | 50.46 | 3.3528 | 6.13 | 0 |  | 0 | 0 | 128.4161 |  |  |  | 5 | 75.25 |  | 0.49582
EXERCISECENTERFLR1 | Yes | 1 | 32.61 | 109.33 | 3.3527 | 13.29 | 1.65 | 3.0937 | 10.5409 | 14.7782 | 11.5041 |  |  | 10 |  | 105.4086 |  | 0.49613
FRONTOFFICEFLR1 | Yes | 1 | 130.44 | 437.33 | 3.3527 | 53.14 | 6.58 | 13.0064 | 10.0289 | 21.6803 | 12.9047 |  |  | 10 |  | 100.2888 |  | 0.49593
FRONTSTAIRSFLR1 | Yes | 1 | 20.07 | 67.28 | 3.3523 | 35.77 | 0 |  | 0 | 9.9528 | 0 |  |  |  |  | 0 |  | 2.1699
FRONTSTORAGEFLR1 | No | 1 | 12.54 | 42.05 | 3.3533 | 5.11 | 0 |  | 0 | 5.7543 | 0 |  |  |  |  | 0 |  | 0.49598
REARSTAIRSFLR2 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 8.7747 | 0 |  |  |  |  | 0 |  | 2.1697
CORRIDORFLR2 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 9.2219 | 0 |  |  |  | 0.25 | 31.355 |  | 0.21816
REARSTORAGEFLR2 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 4.3878 | 0 |  |  |  |  | 0 |  | 2.1693
GUESTROOM201 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.5261
GUESTROOM202_205 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591
GUESTROOM206_208 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 18.7728 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 0.49594
GUESTROOM209_212 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591
GUESTROOM213 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49591
GUESTROOM214 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597
GUESTROOM215_218 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596
ELEVATORCOREFLR2 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 0.49621
GUESTROOM219 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597
GUESTROOM220_223 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596
GUESTROOM224 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597
FRONTSTORAGEFLR2 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 4.8911 | 0 |  |  |  |  | 0 |  | 0.49579
FRONTSTAIRSFLR2 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 8.7739 | 0 |  |  |  |  | 0 |  | 2.1693
REARSTAIRSFLR3 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 8.7747 | 0 |  |  |  |  | 0 |  | 2.1697
CORRIDORFLR3 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 9.2219 | 0 |  |  |  | 0.25 | 31.355 |  | 0.21816
REARSTORAGEFLR3 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 4.3878 | 0 |  |  |  |  | 0 |  | 2.1693
GUESTROOM301 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.5261
GUESTROOM302_305 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591
GUESTROOM306_308 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 18.7728 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 0.49594
GUESTROOM309_312 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49591
GUESTROOM313 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49591
GUESTROOM314 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597
GUESTROOM315_318 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596
ELEVATORCOREFLR3 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 0.49621
GUESTROOM319 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597
GUESTROOM320_323 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 0.49596
GUESTROOM324 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 0.49597
FRONTSTORAGEFLR3 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 4.8911 | 0 |  |  |  |  | 0 |  | 0.49579
FRONTSTAIRSFLR3 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 8.7739 | 0 |  |  |  |  | 0 |  | 2.1693
REARSTAIRSFLR4 | Yes | 1 | 20.07 | 55.06 | 2.7434 | 29.27 | 0 |  | 0 | 4.3874 | 0 |  |  |  |  | 0 |  | 3.6574
CORRIDORFLR4 | Yes | 1 | 125.42 | 344.05 | 2.7432 | 18.39 | 2.62 |  | 0 | 9.2219 | 0 |  |  |  | 0.25 | 31.355 |  | 1.706
REARSTORAGEFLR4 | No | 1 | 20.07 | 55.07 | 2.7439 | 29.27 | 0 |  | 0 | 4.3878 | 0 |  |  |  |  | 0 |  | 3.6567
GUESTROOM401 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 33.45 | 1.64 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 3.0138
GUESTROOM402_405 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838
GUESTROOM406_408 | Yes | 1 | 105.36 | 289.02 | 2.7432 | 35.12 | 6.7 | 23.41 | 4.5006 | 18.7728 | 14.3052 |  | 19.8734 |  |  | 42.4752 |  | 1.9838
GUESTROOM409_412 | Yes | 1 | 130.45 | 357.84 | 2.7431 | 43.48 | 6.58 | 21.74 | 6.0005 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838
GUESTROOM413 | Yes | 1 | 32.61 | 89.46 | 2.7433 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7728 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9837
GUESTROOM414 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9839
GUESTROOM415_418 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838
ELEVATORCOREFLR4 | No | 1 | 15.05 | 41.29 | 2.7435 | 5.02 | 0 |  | 0 | 0 | 0 |  |  |  |  | 0 |  | 1.9838
GUESTROOM419 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.65 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9839
GUESTROOM420_423 | Yes | 1 | 130.44 | 357.81 | 2.7431 | 43.48 | 6.58 | 21.74 | 6 | 18.7728 | 14.3052 |  | 26.4978 |  |  | 56.6336 |  | 1.9838
GUESTROOM424 | Yes | 1 | 32.61 | 89.45 | 2.743 | 10.87 | 1.64 | 21.74 | 1.5 | 18.7719 | 14.3052 |  | 6.6245 |  |  | 14.1584 |  | 1.9839
FRONTSTORAGEFLR4 | No | 1 | 12.54 | 34.41 | 2.744 | 4.18 | 0 |  | 0 | 4.8911 | 0 |  |  |  |  | 0 |  | 1.9832
FRONTSTAIRSFLR4 | Yes | 1 | 20.07 | 55.05 | 2.7429 | 29.26 | 0 |  | 0 | 8.7739 | 0 |  |  |  |  | 0 |  | 3.6573
ATTIC | No | 1 | 1092.62 | 1582.44 | 1.4483 | 0 | 0 | [8 empty] | 0 |  | 1
Total Conditioned Zones |  |  | 4013.63 | 11621.75 |  | 1694.6616 | 184.2302 |  | 254.0541
Data Source | [7 empty] | 1 |  | 2 | 4 |  | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] PNNL - 17875 Technical Support Document: The Development of the Advanced Energy Design Guide for Highway Lodging Buildings

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame | Steel frame
| R-value (m2·K / W) | 0.32 | 1.1737 | 0.73368 | 1.355 | 0.80064 | 1.1013 | 1.355 | 1.9802 | 1.7606 | 1.9157 | 2.1459 | 2.1459 | 2.71 | 2.445 | 3.0395 | 3.9062
Roof
| Construction Type | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic | Attic
| R-value attic floor (m2·K / W) | 2.381 | 2.6667 | 3.8314 | 2.445 | 1.7606 | 3.663 | 2 | 3.0395 | 2.9851 | 2.7548 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet | 4 in slab w/carpet
| R-value (m2·K / W) | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706 | 0.53706
HVAC
HVAC Sizing
Air Conditioning (kW)
| GUESTROOM101 PTAC DXCOIL | 2.6266 | 2.3883 | 2.4778 | 2.2375 | 2.2079 | 2.0902 | 1.9507 | 2.1576 | 1.9808 | 1.9396 | 2.1495 | 1.9295 | 2.0286 | 1.8548 | 1.7287 | 1.766
| GUESTROOM102 PTAC DXCOIL | 2.6866 | 2.442 | 2.5417 | 2.2893 | 2.277 | 2.1472 | 2.0172 | 2.2077 | 2.0465 | 2.009 | 2.2001 | 1.9928 | 2.0785 | 1.9188 | 1.7781 | 1.847
| GUESTROOM103 PTAC DXCOIL | 3.0204 | 2.57 | 2.7875 | 2.3998 | 2.3815 | 2.2962 | 1.9916 | 2.2765 | 2.0442 | 2.0124 | 2.2556 | 1.9528 | 2.1062 | 1.8786 | 1.7336 | 1.7174
| GUESTROOM104 PTAC DXCOIL | 2.941 | 2.3786 | 2.4342 | 2.2891 | 1.784 | 2.1086 | 1.3619 | 2.1766 | 1.8977 | 1.5513 | 2.1466 | 1.7859 | 2.0273 | 1.6924 | 1.5773 | 1.2539
| GUESTROOM105 PTAC DXCOIL | 2.7811 | 2.3535 | 2.292 | 2.2689 | 1.8494 | 2.0602 | 1.5223 | 2.1986 | 2.0554 | 1.6679 | 2.1881 | 1.9893 | 2.0865 | 1.8761 | 1.7181 | 1.4811
| GUESTROOM201 PTAC DXCOIL | 6.0355 | 3.6705 | 4.5295 | 3.3509 | 3.5687 | 3.8363 | 2.9484 | 3.0498 | 3.152 | 2.7701 | 3.0161 | 2.9062 | 2.7558 | 2.7087 | 2.413 | 2.6002
| GUESTROOM202_205 PTAC DXCOIL | 10.5139 | 10.2199 | 11.0608 | 9.7393 | 9.7198 | 10.0599 | 9.7314 | 9.5154 | 9.8114 | 9.5889 | 9.6027 | 9.6956 | 9.2047 | 9.4216 | 8.8344 | 9.9292
| GUESTROOM206_208 PTAC DXCOIL | 8.3396 | 8.1599 | 8.8512 | 7.777 | 7.9729 | 8.1731 | 8.056 | 7.6208 | 7.9475 | 7.9421 | 7.6779 | 7.851 | 7.4543 | 7.6781 | 7.2715 | 8.409
| GUESTROOM209_212 PTAC DXCOIL | 10.346 | 10.0642 | 10.8788 | 9.5875 | 9.5219 | 9.849 | 9.5204 | 9.3853 | 9.5999 | 9.3722 | 9.4436 | 9.4793 | 9.0451 | 9.209 | 8.6185 | 9.6494
| GUESTROOM213 PTAC DXCOIL | 3.0004 | 2.7535 | 3.1092 | 2.6183 | 2.6169 | 2.802 | 2.5031 | 2.5214 | 2.5504 | 2.5009 | 2.5247 | 2.4762 | 2.4008 | 2.4082 | 2.2477 | 2.4652
| GUESTROOM214 PTAC DXCOIL | 3.0741 | 2.6126 | 2.8911 | 2.4334 | 2.1206 | 2.7014 | 1.9116 | 2.4684 | 2.4608 | 2.0716 | 2.4622 | 2.3553 | 2.3566 | 2.2598 | 2.0917 | 1.9888
| GUESTROOM215_218 PTAC DXCOIL | 11.1199 | 9.8777 | 10.1899 | 9.7141 | 8.2698 | 9.8721 | 7.8618 | 9.5514 | 9.9227 | 8.2638 | 9.5769 | 9.7382 | 9.2612 | 9.2872 | 8.5104 | 8.1821
| GUESTROOM219 PTAC DXCOIL | 3.1849 | 2.8609 | 3.0733 | 2.8456 | 2.5535 | 3.0057 | 2.4419 | 2.8004 | 3.0751 | 2.5619 | 2.8155 | 3.0255 | 2.7314 | 2.8823 | 2.6427 | 2.5617
| GUESTROOM220_223 PTAC DXCOIL | 10.6712 | 9.4034 | 9.636 | 8.7849 | 7.6726 | 9.2133 | 7.24 | 9.0544 | 9.1716 | 7.6378 | 9.0765 | 8.9831 | 8.7627 | 8.571 | 7.8565 | 7.5447
| GUESTROOM224 PTAC DXCOIL | 2.9986 | 2.5661 | 2.7687 | 2.3967 | 2.0899 | 2.6147 | 1.9198 | 2.4297 | 2.4581 | 2.058 | 2.4292 | 2.3755 | 2.34 | 2.273 | 2.0967 | 1.9798
| GUESTROOM301 PTAC DXCOIL | 6.0088 | 3.6563 | 4.5241 | 3.34 | 3.5145 | 3.8234 | 2.9149 | 3.038 | 3.1318 | 2.7514 | 3.0029 | 2.8845 | 2.7419 | 2.69 | 2.4071 | 2.6057
| GUESTROOM302_305 PTAC DXCOIL | 10.4763 | 10.1256 | 11.1262 | 9.7855 | 9.6736 | 10.1731 | 9.7952 | 9.5872 | 9.9013 | 9.6633 | 9.6513 | 9.7886 | 9.2574 | 9.5268 | 8.9408 | 10.0723
| GUESTROOM306_308 PTAC DXCOIL | 8.3636 | 8.1555 | 8.9982 | 7.8893 | 8.0395 | 8.37 | 8.2314 | 7.7361 | 8.1183 | 8.1265 | 7.798 | 8.0271 | 7.5861 | 7.8689 | 7.4705 | 8.7028
| GUESTROOM309_312 PTAC DXCOIL | 10.4106 | 10.1112 | 11.1061 | 9.773 | 9.6578 | 10.1532 | 9.7795 | 9.5746 | 9.8817 | 9.6481 | 9.6386 | 9.768 | 9.2461 | 9.5094 | 8.9235 | 10.0476
| GUESTROOM313 PTAC DXCOIL | 2.971 | 2.7489 | 3.1547 | 2.6524 | 2.6261 | 2.8674 | 2.5537 | 2.5646 | 2.6037 | 2.5582 | 2.5701 | 2.5296 | 2.4492 | 2.4694 | 2.3138 | 2.5583
| GUESTROOM314 PTAC DXCOIL | 3.0784 | 2.6451 | 2.9543 | 2.4726 | 2.148 | 2.7748 | 1.9644 | 2.5088 | 2.5187 | 2.128 | 2.5055 | 2.4109 | 2.4073 | 2.3202 | 2.1596 | 2.0722
| GUESTROOM315_318 PTAC DXCOIL | 10.8421 | 9.6165 | 9.9013 | 9.011 | 7.9239 | 9.5898 | 7.5697 | 9.2967 | 9.5351 | 7.9682 | 9.3281 | 9.3535 | 9.0175 | 8.9391 | 8.2248 | 7.9457
| GUESTROOM319 PTAC DXCOIL | 2.8556 | 2.5131 | 2.6322 | 2.3553 | 2.0961 | 2.5506 | 1.9951 | 2.4188 | 2.5174 | 2.105 | 2.432 | 2.4661 | 2.3509 | 2.3569 | 2.1702 | 2.0855
| GUESTROOM320_323 PTAC DXCOIL | 10.739 | 9.5146 | 9.7933 | 8.911 | 7.8043 | 9.4491 | 7.4498 | 9.1935 | 9.3841 | 7.8442 | 9.2248 | 9.2035 | 8.9151 | 8.7962 | 8.0944 | 7.817
| GUESTROOM324 PTAC DXCOIL | 3.0018 | 2.5828 | 2.8185 | 2.4191 | 2.0971 | 2.6684 | 1.9472 | 2.4515 | 2.4823 | 2.0893 | 2.4532 | 2.3965 | 2.3647 | 2.2997 | 2.1335 | 2.0305
| GUESTROOM401 PTAC DXCOIL | 6.1044 | 3.8079 | 4.5626 | 3.5047 | 3.6484 | 3.8724 | 2.9895 | 3.1194 | 3.2333 | 2.8157 | 3.0597 | 2.8936 | 2.7379 | 2.6801 | 2.3356 | 2.6089
| GUESTROOM402_405 PTAC DXCOIL | 11.2054 | 10.4403 | 10.6827 | 10.0598 | 9.6678 | 9.9877 | 9.9539 | 9.6311 | 10.0631 | 9.5869 | 9.6014 | 9.6235 | 9.0918 | 9.3186 | 8.5858 | 10.1665
| GUESTROOM406_408 PTAC DXCOIL | 8.9707 | 8.4539 | 8.6585 | 8.1218 | 7.9468 | 8.187 | 8.3343 | 7.7866 | 8.2295 | 8.034 | 7.7829 | 7.8816 | 7.4277 | 7.6454 | 7.1534 | 8.83
| GUESTROOM409_412 PTAC DXCOIL | 11.1638 | 10.4433 | 10.6985 | 10.067 | 9.658 | 9.9643 | 9.9513 | 9.6243 | 10.043 | 9.587 | 9.5976 | 9.6105 | 9.0911 | 9.3125 | 8.5853 | 10.1619
| GUESTROOM413 PTAC DXCOIL | 3.1554 | 2.8347 | 3.037 | 2.7234 | 2.6109 | 2.8323 | 2.6006 | 2.5776 | 2.6569 | 2.5442 | 2.5613 | 2.5019 | 2.4126 | 2.4397 | 2.2285 | 2.5802
| GUESTROOM414 PTAC DXCOIL | 3.2308 | 2.8673 | 3.1112 | 2.7878 | 2.4802 | 2.9469 | 2.1858 | 2.5486 | 2.7303 | 2.2932 | 2.5126 | 2.5153 | 2.3976 | 2.4114 | 2.2275 | 2.1007
| GUESTROOM415_418 PTAC DXCOIL | 11.4525 | 10.3799 | 10.3707 | 9.8518 | 9.0872 | 10.1288 | 8.2899 | 9.4614 | 10.1405 | 8.4839 | 9.2393 | 9.5323 | 8.7215 | 9.0598 | 8.3175 | 7.9799
| GUESTROOM419 PTAC DXCOIL | 2.9857 | 2.6764 | 2.7106 | 2.5544 | 2.3648 | 2.628 | 2.1356 | 2.3982 | 2.6073 | 2.184 | 2.364 | 2.4339 | 2.2243 | 2.3149 | 2.1177 | 2.0136
| GUESTROOM420_423 PTAC DXCOIL | 11.381 | 10.3105 | 10.2739 | 9.7843 | 9.0057 | 10.0319 | 8.2135 | 9.3951 | 10.0407 | 8.4041 | 9.1732 | 9.4354 | 8.6563 | 8.9668 | 8.2319 | 7.8963
| GUESTROOM424 PTAC DXCOIL | 3.1891 | 2.7929 | 2.9905 | 2.7174 | 2.43 | 2.8408 | 2.169 | 2.4916 | 2.6813 | 2.2539 | 2.4534 | 2.4771 | 2.3254 | 2.367 | 2.1783 | 2.0486
| PSZ-HEATCOOL:1_COOLC DXCOIL | 10.763 | 9.8774 | 9.8786 | 9.6399 | 8.9932 | 9.2474 | 7.2305 | 9.1455 | 9.8684 | 8.2472 | 9.1132 | 9.6739 | 9.1093 | 9.2354 | 8.4335 | 7.4212
| PSZ-HEATCOOL:10_COOLC DXCOIL | 6.9554 | 5.8805 | 6.1724 | 5.5148 | 5.1482 | 5.7819 | 4.611 | 5.4071 | 5.5787 | 4.8185 | 5.4316 | 5.3839 | 5.2022 | 5.1369 | 4.8124 | 4.7188
| PSZ-HEATCOOL:11_COOLC DXCOIL | 6.6235 | 5.5389 | 5.9084 | 5.1918 | 4.7256 | 5.4455 | 4.2575 | 5.0969 | 5.1311 | 4.4585 | 5.1205 | 4.9343 | 4.881 | 4.7253 | 4.4592 | 4.4148
| PSZ-HEATCOOL:12_COOLC DXCOIL | 7.4442 | 6.3591 | 6.3064 | 6.1068 | 5.8948 | 5.8904 | 5.0223 | 5.6221 | 5.6865 | 5.0047 | 5.4471 | 5.1039 | 5.0294 | 4.8725 | 4.4422 | 4.2695
| PSZ-HEATCOOL:2_COOLC DXCOIL | 25.3124 | 21.6159 | 24.7459 | 21.4871 | 21.2788 | 22.9802 | 16.1749 | 20.1971 | 17.3087 | 17.503 | 20.3617 | 17.0376 | 19.9103 | 15.383 | 19.6578 | 14.5919
| PSZ-HEATCOOL:3_COOLC DXCOIL | 1.9653 | 1.6314 | 1.8066 | 1.5757 | 1.7031 | 1.6123 | 1.4145 | 1.4896 | 1.5368 | 1.4107 | 1.4713 | 1.4913 | 1.3941 | 1.4271 | 1.2333 | 1.1331
| PSZ-HEATCOOL:4_COOLC DXCOIL | 13.0365 | 12.0794 | 13.1863 | 12.2229 | 12.9237 | 12.7896 | 9.6002 | 11.5883 | 11.7909 | 10.8534 | 11.711 | 11.7831 | 11.5701 | 9.9608 | 11.3598 | 7.8815
| PSZ-HEATCOOL:5_COOLC DXCOIL | 1.7399 | 1.3909 | 1.4345 | 1.2751 | 1.1854 | 1.087 | 0.88633 | 1.2116 | 0.89076 | 0.86544 | 1.1898 | 0.845 | 1.0862 | 0.81391 | 0.87781 | 0.92252
| PSZ-HEATCOOL:6_COOLC DXCOIL | 8.7943 | 8.2143 | 7.5243 | 8.0685 | 6.2874 | 6.5971 | 5.1283 | 8.044 | 6.3302 | 5.5612 | 8.0391 | 6.2739 | 7.7466 | 5.9322 | 6.6729 | 5.0714
| PSZ-HEATCOOL:7_COOLC DXCOIL | 32.8512 | 32.235 | 31.3271 | 31.554 | 27.5678 | 29.2261 | 26.0902 | 30.8322 | 32.4137 | 26.9348 | 30.8814 | 32.298 | 30.648 | 30.5699 | 28.4233 | 26.5278
| PSZ-HEATCOOL:8_COOLC DXCOIL | 4.2903 | 3.6854 | 3.8664 | 3.7167 | 3.3727 | 3.7281 | 2.1802 | 3.4626 | 3.1359 | 2.6439 | 3.4688 | 3.1029 | 3.4601 | 2.561 | 3.2489 | 2.0021
| PSZ-HEATCOOL:9_COOLC DXCOIL | 13.0871 | 11.0847 | 10.2994 | 10.5763 | 8.0028 | 8.607 | 5.7354 | 10.3447 | 7.7242 | 6.5732 | 10.2527 | 7.4554 | 9.7603 | 7.0489 | 7.9133 | 5.4002
Heating (kW)
| FRONTSTAIRSFLR1 UNIT HEATER COIL | 0.5353 | 1.1063 | 0.83823 | 1.4794 | 0.40439 | 1.0758 | 0.55862 | 1.6954 | 1.3115 | 1.1146 | 2.5088 | 1.9658 | 2.8769 | 2.745 | 3.0431 | 4.3701
| FRONTSTAIRSFLR2 UNIT HEATER COIL | 0.70528 | 1.0715 | 0.81854 | 1.3579 | 0.47604 | 0.98608 | 0.58419 | 1.5135 | 1.1816 | 1.0334 | 2.1831 | 1.7263 | 2.4691 | 2.3626 | 2.5954 | 3.6559
| FRONTSTAIRSFLR3 UNIT HEATER COIL | 0.74114 | 1.1102 | 0.8431 | 1.3956 | 0.50892 | 1.0123 | 0.6232 | 1.5512 | 1.2172 | 1.071 | 2.2158 | 1.7616 | 2.5005 | 2.3956 | 2.625 | 3.6836
| FRONTSTAIRSFLR4 UNIT HEATER COIL | 0.7983 | 1.2582 | 0.91872 | 1.581 | 0.63229 | 1.1173 | 0.76921 | 1.7304 | 1.3917 | 1.2289 | 2.4234 | 1.9584 | 2.7058 | 2.6325 | 2.8227 | 3.8917
| FRONTSTORAGEFLR1 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09929
| FRONTSTORAGEFLR2 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02949 | 0.03068 | 0.11404
| FRONTSTORAGEFLR3 UNIT HEATER COIL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03357 | 0 | 0.04604 | 0.05103 | 0.05174 | 0.13117
| FRONTSTORAGEFLR4 UNIT HEATER COIL | 0 | 0.02984 | 0 | 0.08334 | 0 | 0 | 0 | 0.07194 | 0.04549 | 0 | 0.15961 | 0.11426 | 0.17154 | 0.19308 | 0.17295 | 0.25707
| GUESTROOM101 PTAC HEAT COIL | 0.73266 | 1.0454 | 0.95801 | 1.2137 | 0.71749 | 1.0923 | 0.77661 | 1.3088 | 1.1486 | 1.0538 | 1.6863 | 1.4293 | 1.8404 | 1.7715 | 1.9179 | 2.5163
| GUESTROOM102 PTAC HEAT COIL | 0.75106 | 1.0671 | 0.97794 | 1.2354 | 0.73646 | 1.1134 | 0.79566 | 1.3301 | 1.1704 | 1.0746 | 1.7093 | 1.4519 | 1.8635 | 1.7948 | 1.9413 | 2.541
| GUESTROOM103 PTAC HEAT COIL | 0.98368 | 1.2912 | 1.2111 | 1.4662 | 0.95044 | 1.3428 | 1.0034 | 1.5514 | 1.3941 | 1.2859 | 1.941 | 1.6818 | 2.0912 | 2.0297 | 2.1668 | 2.7678
| GUESTROOM104 PTAC HEAT COIL | 0.96279 | 1.273 | 1.1971 | 1.4525 | 0.93761 | 1.3278 | 0.99548 | 1.5431 | 1.3804 | 1.2753 | 1.9303 | 1.6724 | 2.0804 | 2.0185 | 2.1557 | 2.757
| GUESTROOM105 PTAC HEAT COIL | 0.73957 | 1.0601 | 0.9771 | 1.235 | 0.73061 | 1.1127 | 0.79377 | 1.3338 | 1.1695 | 1.0731 | 1.7145 | 1.4578 | 1.8688 | 1.8003 | 1.9467 | 2.5485
| GUESTROOM201 PTAC HEAT COIL | 1.7828 | 1.9015 | 1.6992 | 2.135 | 1.3306 | 1.8141 | 1.3533 | 2.2158 | 1.9076 | 1.7722 | 2.8463 | 2.3873 | 3.0623 | 2.9577 | 3.1636 | 4.0861
| GUESTROOM202_205 PTAC HEAT COIL | 3.2142 | 4.0256 | 3.4043 | 4.5156 | 2.6876 | 3.8181 | 2.8601 | 4.8029 | 4.1083 | 3.8782 | 6.1837 | 5.1541 | 6.6988 | 6.391 | 6.9571 | 8.9901
| GUESTROOM206_208 PTAC HEAT COIL | 2.412 | 3.1183 | 2.609 | 3.4975 | 2.0326 | 2.9631 | 2.1677 | 3.7192 | 3.19 | 2.9959 | 4.8279 | 4.0154 | 5.232 | 4.989 | 5.445 | 7.0578
| GUESTROOM209_212 PTAC HEAT COIL | 3.119 | 3.9441 | 3.3229 | 4.4323 | 2.6229 | 3.7364 | 2.8059 | 4.7306 | 4.0307 | 3.8139 | 6.0957 | 5.0697 | 6.614 | 6.3005 | 6.8716 | 8.8969
| GUESTROOM213 PTAC HEAT COIL | 1.0492 | 1.238 | 1.0884 | 1.3648 | 0.89517 | 1.187 | 0.93209 | 1.4286 | 1.2553 | 1.1883 | 1.7808 | 1.5216 | 1.9057 | 1.8343 | 1.9678 | 2.4747
| GUESTROOM214 PTAC HEAT COIL | 1.0159 | 1.1995 | 1.0565 | 1.3294 | 0.85977 | 1.1538 | 0.89778 | 1.393 | 1.2179 | 1.1524 | 1.7461 | 1.4882 | 1.8693 | 1.7983 | 1.9315 | 2.4388
| GUESTROOM215_218 PTAC HEAT COIL | 2.8444 | 3.6614 | 3.0692 | 4.1702 | 2.3372 | 3.4866 | 2.5582 | 4.471 | 3.7585 | 3.5387 | 5.8587 | 4.8281 | 6.3771 | 6.0606 | 6.6387 | 8.6752
| GUESTROOM219 PTAC HEAT COIL | 0.55632 | 0.73442 | 0.61963 | 0.85313 | 0.5786 | 0.67631 | 0.63954 | 0.92793 | 0.7403 | 0.76269 | 1.2904 | 1.0194 | 1.4248 | 1.3439 | 1.4918 | 2.0247
| GUESTROOM220_223 PTAC HEAT COIL | 2.9689 | 3.7996 | 3.2036 | 4.3057 | 2.4822 | 3.6229 | 2.6685 | 4.6082 | 3.8986 | 3.6786 | 5.9912 | 4.9636 | 6.5099 | 6.1934 | 6.7718 | 8.8158
| GUESTROOM224 PTAC HEAT COIL | 0.94459 | 1.1429 | 0.99576 | 1.2803 | 0.78953 | 1.1001 | 0.83116 | 1.3492 | 1.1669 | 1.0967 | 1.717 | 1.451 | 1.8448 | 1.7685 | 1.9092 | 2.4184
| GUESTROOM301 PTAC HEAT COIL | 1.8479 | 1.9495 | 1.7324 | 2.1859 | 1.3762 | 1.8445 | 1.3979 | 2.2608 | 1.9475 | 1.8129 | 2.8948 | 2.4308 | 3.1056 | 3.0049 | 3.2035 | 4.1182
| GUESTROOM302_305 PTAC HEAT COIL | 3.3329 | 4.1385 | 3.442 | 4.6357 | 2.8007 | 3.8597 | 2.9824 | 4.9152 | 4.2006 | 3.9852 | 6.2986 | 5.2536 | 6.8025 | 6.5013 | 7.0514 | 9.056
| GUESTROOM306_308 PTAC HEAT COIL | 2.6226 | 3.3211 | 2.7413 | 3.7015 | 2.2297 | 3.0996 | 2.3693 | 3.9123 | 3.3702 | 3.1872 | 5.026 | 4.2006 | 5.4184 | 5.1816 | 5.6246 | 7.2169
| GUESTROOM309_312 PTAC HEAT COIL | 3.2934 | 4.1161 | 3.4154 | 4.6121 | 2.7821 | 3.8368 | 2.9705 | 4.8978 | 4.1817 | 3.972 | 6.2761 | 5.2325 | 6.7826 | 6.4781 | 7.0324 | 9.0366
| GUESTROOM313 PTAC HEAT COIL | 1.0881 | 1.2758 | 1.1077 | 1.4039 | 0.93056 | 1.2077 | 0.96924 | 1.4654 | 1.2877 | 1.2234 | 1.8196 | 1.5563 | 1.9418 | 1.8719 | 2.002 | 2.5031
| GUESTROOM314 PTAC HEAT COIL | 1.0625 | 1.2452 | 1.0823 | 1.3774 | 0.90216 | 1.1807 | 0.94216 | 1.4369 | 1.2578 | 1.1947 | 1.7928 | 1.5304 | 1.9133 | 1.8439 | 1.9734 | 2.4741
| GUESTROOM315_318 PTAC HEAT COIL | 3.2506 | 4.0629 | 3.3827 | 4.5728 | 2.7345 | 3.8022 | 2.9236 | 4.8559 | 4.1331 | 3.9241 | 6.2389 | 5.1997 | 6.7425 | 6.4333 | 6.9942 | 8.9996
| GUESTROOM319 PTAC HEAT COIL | 0.82684 | 1.0142 | 0.84095 | 1.1526 | 0.66409 | 0.94537 | 0.7046 | 1.22 | 1.0303 | 0.96829 | 1.5919 | 1.3157 | 1.723 | 1.6471 | 1.7881 | 2.3226
| GUESTROOM320_323 PTAC HEAT COIL | 3.2247 | 4.0427 | 3.3619 | 4.5518 | 2.7181 | 3.782 | 2.9115 | 4.8376 | 4.1141 | 3.9081 | 6.2164 | 5.1787 | 6.7208 | 6.4104 | 6.9722 | 8.9754
| GUESTROOM324 PTAC HEAT COIL | 1.0044 | 1.2001 | 1.03 | 1.338 | 0.84293 | 1.1357 | 0.88898 | 1.4037 | 1.2167 | 1.1516 | 1.7663 | 1.5011 | 1.8912 | 1.8158 | 1.9533 | 2.454
| GUESTROOM401 PTAC HEAT COIL | 1.9872 | 2.2227 | 1.8765 | 2.53 | 1.6365 | 2.0338 | 1.6864 | 2.5867 | 2.2597 | 2.1006 | 3.2694 | 2.7826 | 3.4713 | 3.4229 | 3.5541 | 4.4764
| GUESTROOM402_405 PTAC HEAT COIL | 3.9831 | 5.2286 | 4.0535 | 5.9868 | 3.8619 | 4.6235 | 4.1202 | 6.1816 | 5.4206 | 5.1054 | 7.749 | 6.6195 | 8.2127 | 8.1204 | 8.4003 | 10.4329
| GUESTROOM406_408 PTAC HEAT COIL | 3.164 | 4.2178 | 3.2489 | 4.8096 | 3.1033 | 3.7309 | 3.3051 | 4.9522 | 4.3721 | 4.1086 | 6.2153 | 5.3209 | 6.5747 | 6.5069 | 6.7314 | 8.3462
| GUESTROOM409_412 PTAC HEAT COIL | 3.9518 | 5.2136 | 4.0339 | 5.9704 | 3.8498 | 4.6078 | 4.1135 | 6.1706 | 5.4087 | 5.0982 | 7.7338 | 6.6055 | 8.1999 | 8.1047 | 8.3886 | 10.4213
| GUESTROOM413 PTAC HEAT COIL | 1.2474 | 1.5471 | 1.2591 | 1.7404 | 1.1941 | 1.398 | 1.2532 | 1.7816 | 1.5921 | 1.5035 | 2.1813 | 1.8971 | 2.2939 | 2.2757 | 2.339 | 2.847
| GUESTROOM414 PTAC HEAT COIL | 1.2305 | 1.5342 | 1.2442 | 1.735 | 1.1811 | 1.3842 | 1.2435 | 1.7743 | 1.5829 | 1.493 | 2.1777 | 1.8938 | 2.2895 | 2.2729 | 2.3342 | 2.8421
| GUESTROOM415_418 PTAC HEAT COIL | 3.9414 | 5.1979 | 4.0353 | 5.9708 | 3.8422 | 4.6064 | 4.1111 | 6.1679 | 5.3993 | 5.0924 | 7.7329 | 6.61 | 8.1978 | 8.0962 | 8.3881 | 10.4181
| GUESTROOM419 PTAC HEAT COIL | 1.0738 | 1.3949 | 1.0827 | 1.6082 | 1.0346 | 1.2319 | 1.1013 | 1.6525 | 1.4499 | 1.3593 | 2.0762 | 1.7771 | 2.1971 | 2.1809 | 2.2449 | 2.7868
| GUESTROOM420_423 PTAC HEAT COIL | 3.8988 | 5.1568 | 3.9946 | 5.9281 | 3.8048 | 4.5656 | 4.0755 | 6.1271 | 5.3583 | 5.0544 | 7.6875 | 6.5661 | 8.1527 | 8.0498 | 8.3428 | 10.3697
| GUESTROOM424 PTAC HEAT COIL | 1.1894 | 1.5087 | 1.207 | 1.7073 | 1.1471 | 1.3569 | 1.2169 | 1.7539 | 1.5604 | 1.4777 | 2.1513 | 1.8686 | 2.2666 | 2.2452 | 2.3128 | 2.8203
| REARSTAIRSFLR1 UNIT HEATER COIL | 0.47648 | 1.0006 | 0.74322 | 1.3584 | 0.32307 | 0.96429 | 0.46574 | 1.5681 | 1.1918 | 1.0042 | 2.3633 | 1.8313 | 2.7239 | 2.5948 | 2.8863 | 4.213
| REARSTAIRSFLR2 UNIT HEATER COIL | 0.58276 | 0.94108 | 0.68918 | 1.2162 | 0.36343 | 0.8527 | 0.46628 | 1.3718 | 1.047 | 0.90353 | 2.0244 | 1.5766 | 2.3096 | 2.2006 | 2.4355 | 3.4963
| REARSTAIRSFLR3 UNIT HEATER COIL | 0.60597 | 0.96658 | 0.70406 | 1.242 | 0.38657 | 0.86914 | 0.49247 | 1.3993 | 1.0714 | 0.92924 | 2.0511 | 1.6021 | 2.3367 | 2.2282 | 2.4621 | 3.5207
| REARSTAIRSFLR4 UNIT HEATER COIL | 0.65528 | 1.096 | 0.76746 | 1.4138 | 0.49484 | 0.9575 | 0.62587 | 1.5623 | 1.2258 | 1.0711 | 2.2498 | 1.7861 | 2.5314 | 2.4561 | 2.6488 | 3.7168
| REARSTORAGEFLR1 UNIT HEATER COIL | 0.36576 | 0.56482 | 0.49225 | 0.77636 | 0.18171 | 0.58874 | 0.21825 | 0.83515 | 0.66603 | 0.50715 | 1.2882 | 1.0146 | 1.4489 | 1.4243 | 1.5232 | 2.207
| REARSTORAGEFLR2 UNIT HEATER COIL | 0.52868 | 0.61691 | 0.52094 | 0.77602 | 0.27682 | 0.58095 | 0.29916 | 0.80403 | 0.65152 | 0.53036 | 1.1817 | 0.94483 | 1.3023 | 1.2814 | 1.3559 | 1.8917
| REARSTORAGEFLR3 UNIT HEATER COIL | 0.5479 | 0.63569 | 0.53289 | 0.79407 | 0.29307 | 0.59285 | 0.31597 | 0.82196 | 0.66702 | 0.54713 | 1.199 | 0.9608 | 1.3191 | 1.2978 | 1.3721 | 1.9053
| REARSTORAGEFLR4 UNIT HEATER COIL | 0.53564 | 0.64767 | 0.52905 | 0.81268 | 0.30205 | 0.59846 | 0.33174 | 0.84256 | 0.685 | 0.56591 | 1.2216 | 0.98112 | 1.3424 | 1.3216 | 1.3952 | 1.927
| PSZ-HEATCOOL:1_HEATC | 30.3584 | 14.3597 | 13.9707 | 14.1392 | 25.8991 | 12.8206 | 20.9856 | 14.0097 | 12.3967 | 12.4353 | 14.2287 | 12.5113 | 14.3523 | 13.0289 | 13.29 | 12.9859
| PSZ-HEATCOOL:10_HEATC | 9.4763 | 8.1246 | 8.8423 | 7.9955 | 7.6681 | 8.2144 | 13.3542 | 8.0193 | 7.3088 | 7.5504 | 8.3395 | 7.3723 | 8.355 | 7.7749 | 8.1513 | 8.8185
| PSZ-HEATCOOL:11_HEATC | 8.9515 | 7.599 | 8.4108 | 7.4982 | 7.0834 | 7.7829 | 6.5853 | 7.5169 | 6.7976 | 7.0577 | 7.8379 | 6.8597 | 7.8584 | 7.2793 | 7.6854 | 8.4031
| PSZ-HEATCOOL:12_HEATC | 10.3213 | 8.9921 | 9.073 | 9.0673 | 8.7013 | 8.3537 | 7.647 | 8.4532 | 7.432 | 7.8054 | 8.4745 | 7.0531 | 8.1531 | 7.4566 | 7.663 | 8.2045
| PSZ-HEATCOOL:2_HEATC | 30.0935 | 31.8837 | 30.9174 | 33.1355 | 29.114 | 30.6621 | 29.3674 | 34.9078 | 29.6643 | 32.9531 | 39.2792 | 33.2309 | 41.2557 | 38.3649 | 41.6307 | 51.9573
| PSZ-HEATCOOL:3_HEATC | 2.7187 | 2.1769 | 2.4103 | 2.1082 | 2.3567 | 2.0688 | 1.9636 | 2.0136 | 1.7556 | 1.9314 | 1.9729 | 1.7005 | 1.8788 | 1.7187 | 1.6273 | 1.5485
| PSZ-HEATCOOL:4_HEATC | 18.8198 | 23.2496 | 20.7578 | 25.062 | 19.3734 | 21.8325 | 20.4435 | 27.2016 | 22.834 | 24.1672 | 31.73 | 26.7353 | 34.0801 | 31.7312 | 34.6621 | 43.1768
| PSZ-HEATCOOL:5_HEATC | 2.0928 | 1.6561 | 1.8341 | 1.6298 | 1.7495 | 1.5393 | 1.4059 | 1.579 | 1.261 | 1.4328 | 1.6253 | 1.2842 | 1.5786 | 1.3933 | 1.4299 | 1.877
| PSZ-HEATCOOL:6_HEATC | 9.7853 | 10.2176 | 9.6351 | 10.4846 | 8.9595 | 9.7239 | 8.8641 | 10.8797 | 9.8587 | 9.8331 | 11.7734 | 10.6157 | 12.2314 | 11.6033 | 12.1465 | 13.5828
| PSZ-HEATCOOL:7_HEATC | 81.2696 | 42.4882 | 41.1426 | 42.9411 | 78.1145 | 41.1301 | 75.6952 | 43.5402 | 41.2982 | 41.2252 | 44.9383 | 42.4559 | 45.6926 | 44.0637 | 45.1252 | 47.0643
| PSZ-HEATCOOL:8_HEATC | 5.7017 | 6.5019 | 5.7526 | 6.9435 | 5.0207 | 5.9801 | 5.0642 | 7.4244 | 6.2178 | 6.2198 | 8.5543 | 7.1912 | 9.1779 | 8.4318 | 9.1793 | 11.0513
| PSZ-HEATCOOL:9_HEATC | 15.2488 | 13.7135 | 13.3424 | 13.5773 | 11.3561 | 12.5609 | 10.0144 | 13.7538 | 11.8095 | 11.621 | 14.6291 | 12.435 | 14.9664 | 13.5562 | 14.0435 | 14.9392
HVAC Efficiency
Air Conditioning (COP)
| GUESTROOM101 PTAC DXCOIL | 2.75 | 2.78 | 2.78 | 2.82 | 2.87 | 2.89 | 2.9 | 2.83 | 2.9 | 2.9 | 2.83 | 2.9 | 2.86 | 2.9 | 2.89 | 2.9
| GUESTROOM102 PTAC DXCOIL | 2.74 | 2.77 | 2.77 | 2.81 | 2.85 | 2.88 | 2.9 | 2.82 | 2.9 | 2.9 | 2.82 | 2.9 | 2.86 | 2.9 | 2.89 | 2.9
| GUESTROOM103 PTAC DXCOIL | 2.68 | 2.75 | 2.73 | 2.8 | 2.83 | 2.85 | 2.9 | 2.81 | 2.9 | 2.9 | 2.82 | 2.9 | 2.85 | 2.9 | 2.89 | 2.9
| GUESTROOM104 PTAC DXCOIL | 2.71 | 2.8 | 2.81 | 2.82 | 2.9 | 2.89 | 2.9 | 2.83 | 2.9 | 2.9 | 2.83 | 2.9 | 2.86 | 2.9 | 2.88 | 2.9
| GUESTROOM105 PTAC DXCOIL | 2.73 | 2.8 | 2.84 | 2.82 | 2.9 | 2.9 | 2.9 | 2.82 | 2.9 | 2.9 | 2.83 | 2.9 | 2.85 | 2.9 | 2.89 | 2.9
| GUESTROOM201 PTAC DXCOIL | 2.44 | 2.56 | 2.44 | 2.63 | 2.6 | 2.55 | 2.72 | 2.68 | 2.68 | 2.76 | 2.68 | 2.73 | 2.74 | 2.77 | 2.82 | 2.79
| GUESTROOM202_205 PTAC DXCOIL | 2.41 | 2.41 | 2.43 | 2.42 | 2.44 | 2.44 | 2.44 | 2.42 | 2.44 | 2.44 | 2.42 | 2.44 | 2.43 | 2.44 | 2.44 | 2.44
| GUESTROOM206_208 PTAC DXCOIL | 2.42 | 2.41 | 2.43 | 2.42 | 2.44 | 2.44 | 2.44 | 2.42 | 2.44 | 2.44 | 2.42 | 2.44 | 2.43 | 2.44 | 2.44 | 2.44
| GUESTROOM209_212 PTAC DXCOIL | 2.41 | 2.41 | 2.43 | 2.42 | 2.44 | 2.44 | 2.44 | 2.41 | 2.44 | 2.44 | 2.42 | 2.44 | 2.42 | 2.44 | 2.44 | 2.44
| GUESTROOM213 PTAC DXCOIL | 2.69 | 2.73 | 2.68 | 2.77 | 2.79 | 2.75 | 2.81 | 2.78 | 2.8 | 2.81 | 2.78 | 2.82 | 2.82 | 2.83 | 2.86 | 2.82
| GUESTROOM214 PTAC DXCOIL | 2.69 | 2.77 | 2.73 | 2.82 | 2.89 | 2.77 | 2.9 | 2.79 | 2.82 | 2.9 | 2.79 | 2.84 | 2.82 | 2.86 | 2.89 | 2.9
| GUESTROOM215_218 PTAC DXCOIL | 2.43 | 2.42 | 2.44 | 2.42 | 2.44 | 2.44 | 2.44 | 2.42 | 2.44 | 2.44 | 2.42 | 2.44 | 2.42 | 2.44 | 2.44 | 2.44
| GUESTROOM219 PTAC DXCOIL | 2.67 | 2.73 | 2.7 | 2.73 | 2.8 | 2.71 | 2.82 | 2.74 | 2.7 | 2.8 | 2.73 | 2.71 | 2.76 | 2.74 | 2.78 | 2.8
| GUESTROOM220_223 PTAC DXCOIL | 2.42 | 2.42 | 2.44 | 2.43 | 2.44 | 2.44 | 2.44 | 2.41 | 2.44 | 2.44 | 2.41 | 2.44 | 2.42 | 2.44 | 2.44 | 2.44
| GUESTROOM224 PTAC DXCOIL | 2.7 | 2.77 | 2.76 | 2.83 | 2.89 | 2.79 | 2.9 | 2.79 | 2.82 | 2.9 | 2.8 | 2.84 | 2.82 | 2.86 | 2.89 | 2.9
| GUESTROOM301 PTAC DXCOIL | 2.44 | 2.56 | 2.44 | 2.63 | 2.61 | 2.55 | 2.73 | 2.68 | 2.69 | 2.76 | 2.69 | 2.73 | 2.74 | 2.77 | 2.82 | 2.79
| GUESTROOM302_305 PTAC DXCOIL | 2.41 | 2.41 | 2.43 | 2.42 | 2.44 | 2.44 | 2.44 | 2.42 | 2.44 | 2.44 | 2.42 | 2.44 | 2.43 | 2.44 | 2.44 | 2.44
| GUESTROOM306_308 PTAC DXCOIL | 2.42 | 2.41 | 2.43 | 2.43 | 2.44 | 2.44 | 2.44 | 2.42 | 2.44 | 2.44 | 2.42 | 2.44 | 2.43 | 2.44 | 2.44 | 2.44
| GUESTROOM309_312 PTAC DXCOIL | 2.41 | 2.41 | 2.43 | 2.42 | 2.44 | 2.44 | 2.44 | 2.42 | 2.44 | 2.44 | 2.42 | 2.44 | 2.43 | 2.44 | 2.44 | 2.44
| GUESTROOM313 PTAC DXCOIL | 2.7 | 2.73 | 2.67 | 2.76 | 2.79 | 2.74 | 2.8 | 2.77 | 2.79 | 2.8 | 2.78 | 2.8 | 2.81 | 2.82 | 2.85 | 2.8
| GUESTROOM314 PTAC DXCOIL | 2.69 | 2.76 | 2.72 | 2.81 | 2.88 | 2.76 | 2.9 | 2.78 | 2.81 | 2.88 | 2.79 | 2.83 | 2.81 | 2.85 | 2.88 | 2.9
| GUESTROOM315_318 PTAC DXCOIL | 2.42 | 2.42 | 2.44 | 2.43 | 2.44 | 2.44 | 2.44 | 2.41 | 2.44 | 2.44 | 2.42 | 2.44 | 2.42 | 2.44 | 2.44 | 2.44
| GUESTROOM319 PTAC DXCOIL | 2.72 | 2.78 | 2.78 | 2.83 | 2.89 | 2.8 | 2.9 | 2.8 | 2.81 | 2.89 | 2.8 | 2.82 | 2.82 | 2.84 | 2.88 | 2.89
| GUESTROOM320_323 PTAC DXCOIL | 2.42 | 2.42 | 2.44 | 2.43 | 2.44 | 2.44 | 2.44 | 2.41 | 2.44 | 2.44 | 2.42 | 2.44 | 2.42 | 2.44 | 2.44 | 2.44
| GUESTROOM324 PTAC DXCOIL | 2.7 | 2.77 | 2.75 | 2.82 | 2.89 | 2.78 | 2.9 | 2.79 | 2.81 | 2.89 | 2.79 | 2.83 | 2.82 | 2.85 | 2.88 | 2.9
| GUESTROOM401 PTAC DXCOIL | 2.44 | 2.54 | 2.44 | 2.61 | 2.59 | 2.54 | 2.71 | 2.67 | 2.67 | 2.75 | 2.68 | 2.73 | 2.75 | 2.78 | 2.84 | 2.79
| GUESTROOM402_405 PTAC DXCOIL | 2.42 | 2.42 | 2.43 | 2.43 | 2.44 | 2.44 | 2.44 | 2.42 | 2.44 | 2.44 | 2.42 | 2.44 | 2.43 | 2.44 | 2.44 | 2.44
| GUESTROOM406_408 PTAC DXCOIL | 2.42 | 2.42 | 2.43 | 2.44 | 2.44 | 2.44 | 2.44 | 2.43 | 2.44 | 2.44 | 2.43 | 2.44 | 2.43 | 2.44 | 2.44 | 2.44
| GUESTROOM409_412 PTAC DXCOIL | 2.42 | 2.42 | 2.43 | 2.43 | 2.44 | 2.44 | 2.44 | 2.42 | 2.44 | 2.44 | 2.42 | 2.44 | 2.43 | 2.44 | 2.44 | 2.44
| GUESTROOM413 PTAC DXCOIL | 2.67 | 2.72 | 2.7 | 2.76 | 2.79 | 2.75 | 2.79 | 2.78 | 2.78 | 2.8 | 2.78 | 2.81 | 2.82 | 2.82 | 2.86 | 2.79
| GUESTROOM414 PTAC DXCOIL | 2.66 | 2.73 | 2.69 | 2.75 | 2.81 | 2.72 | 2.87 | 2.8 | 2.77 | 2.85 | 2.81 | 2.81 | 2.83 | 2.83 | 2.86 | 2.89
| GUESTROOM415_418 PTAC DXCOIL | 2.43 | 2.42 | 2.44 | 2.44 | 2.44 | 2.44 | 2.44 | 2.43 | 2.44 | 2.44 | 2.43 | 2.44 | 2.44 | 2.44 | 2.44 | 2.44
| GUESTROOM419 PTAC DXCOIL | 2.7 | 2.76 | 2.77 | 2.8 | 2.84 | 2.79 | 2.88 | 2.82 | 2.79 | 2.87 | 2.83 | 2.82 | 2.86 | 2.85 | 2.89 | 2.9
| GUESTROOM420_423 PTAC DXCOIL | 2.43 | 2.42 | 2.44 | 2.44 | 2.44 | 2.44 | 2.44 | 2.43 | 2.44 | 2.44 | 2.43 | 2.44 | 2.44 | 2.44 | 2.44 | 2.44
| GUESTROOM424 PTAC DXCOIL | 2.67 | 2.74 | 2.71 | 2.77 | 2.82 | 2.74 | 2.88 | 2.81 | 2.77 | 2.86 | 2.82 | 2.82 | 2.85 | 2.84 | 2.87 | 2.9
| PSZ-HEATCOOL:1_COOLC DXCOIL | 4 | 4 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.03 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04
| PSZ-HEATCOOL:10_COOLC DXCOIL | 3.95 | 3.9 | 4.03 | 3.96 | 4.04 | 4.04 | 4.04 | 3.93 | 4.04 | 4.04 | 3.94 | 4.04 | 3.97 | 4.04 | 4.04 | 4.04
| PSZ-HEATCOOL:11_COOLC DXCOIL | 3.93 | 3.88 | 4.01 | 3.95 | 4.04 | 4.04 | 4.04 | 3.91 | 4.04 | 4.04 | 3.92 | 4.04 | 3.95 | 4.04 | 4.04 | 4.04
| PSZ-HEATCOOL:12_COOLC DXCOIL | 3.97 | 3.94 | 4.04 | 4.01 | 4.04 | 4.04 | 4.04 | 3.95 | 4.04 | 4.04 | 3.96 | 4.04 | 3.97 | 4.04 | 4.04 | 4.04
| PSZ-HEATCOOL:2_COOLC DXCOIL | 3.44 | 3.45 | 3.44 | 3.45 | 3.51 | 3.45 | 3.89 | 3.45 | 3.85 | 3.82 | 3.45 | 3.86 | 3.45 | 3.93 | 3.45 | 4.01
| PSZ-HEATCOOL:3_COOLC DXCOIL | 4.03 | 3.99 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04 | 4.01 | 4.04 | 4.04 | 4.02 | 4.04 | 4.04 | 4.04 | 4.04 | 4.04
| PSZ-HEATCOOL:4_COOLC DXCOIL | 3.65 | 3.65 | 3.65 | 3.65 | 3.65 | 3.65 | 3.84 | 3.65 | 3.73 | 3.74 | 3.65 | 3.72 | 3.65 | 3.83 | 3.65 | 4.03
| PSZ-HEATCOOL:5_COOLC DXCOIL | 3.81 | 3.73 | 3.87 | 3.79 | 4.01 | 3.98 | 4.04 | 3.75 | 4.04 | 4.04 | 3.75 | 4.04 | 3.76 | 4.04 | 3.83 | 4.04
| PSZ-HEATCOOL:6_COOLC DXCOIL | 3.68 | 3.67 | 3.77 | 3.69 | 3.86 | 3.89 | 4.01 | 3.66 | 4.04 | 3.96 | 3.67 | 4.04 | 3.69 | 4.04 | 3.8 | 4.04
| PSZ-HEATCOOL:7_COOLC DXCOIL | 3.62 | 3.63 | 3.68 | 3.67 | 3.76 | 3.73 | 3.77 | 3.66 | 3.73 | 3.77 | 3.67 | 3.73 | 3.68 | 3.73 | 3.75 | 3.77
| PSZ-HEATCOOL:8_COOLC DXCOIL | 3.65 | 3.65 | 3.65 | 3.65 | 3.65 | 3.65 | 3.9 | 3.65 | 3.82 | 3.79 | 3.65 | 3.81 | 3.65 | 3.94 | 3.65 | 4.04
| PSZ-HEATCOOL:9_COOLC DXCOIL | 3.74 | 3.7 | 3.82 | 3.72 | 3.87 | 3.92 | 4.02 | 3.68 | 4.04 | 3.98 | 3.68 | 4.04 | 3.71 | 4.04 | 3.79 | 4.04
Heating Efficiency (%)
| FRONTSTAIRSFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTAIRSFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| FRONTSTORAGEFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM101 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM102 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM103 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM104 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM105 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM201 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM202_205 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM206_208 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM209_212 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM213 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM214 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM215_218 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM219 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM220_223 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM224 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM301 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM302_305 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM306_308 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM309_312 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM313 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM314 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM315_318 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM319 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM320_323 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM324 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM401 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM402_405 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM406_408 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM409_412 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM413 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM414 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM415_418 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM419 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM420_423 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| GUESTROOM424 PTAC HEAT COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTAIRSFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR1 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR2 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR3 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| REARSTORAGEFLR4 UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| PSZ-HEATCOOL:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:10_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:11_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:12_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:2_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:3_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:4_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:5_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:6_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:7_HEATC | 0.78 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.78 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:8_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-HEATCOOL:9_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
HVAC Control - Economizer
| All GuestRoom & UnitHeater systems | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:1 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:10 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:11 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:12 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:2 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:3 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:4 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:5 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:6 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:7 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:8 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
| PSZ-HEATCOOL:9 | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer
Fan Max Flow Rate (m3/s )
| FRONTSTAIRSFLR1 UNIT HEATERFAN | 0.02 | 0.04 | 0.03 | 0.05 | 0.01 | 0.04 | 0.02 | 0.06 | 0.05 | 0.04 | 0.09 | 0.08 | 0.1 | 0.11 | 0.11 | 0.15
| FRONTSTAIRSFLR2 UNIT HEATERFAN | 0.02 | 0.04 | 0.03 | 0.05 | 0.02 | 0.04 | 0.02 | 0.05 | 0.05 | 0.03 | 0.07 | 0.07 | 0.08 | 0.09 | 0.09 | 0.12
| FRONTSTAIRSFLR3 UNIT HEATERFAN | 0.02 | 0.04 | 0.03 | 0.05 | 0.02 | 0.04 | 0.02 | 0.05 | 0.05 | 0.04 | 0.08 | 0.07 | 0.09 | 0.09 | 0.09 | 0.12
| FRONTSTAIRSFLR4 UNIT HEATERFAN | 0.03 | 0.04 | 0.03 | 0.05 | 0.02 | 0.04 | 0.03 | 0.06 | 0.06 | 0.04 | 0.08 | 0.08 | 0.09 | 0.1 | 0.1 | 0.13
| FRONTSTORAGEFLR1 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTORAGEFLR2 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTORAGEFLR3 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| FRONTSTORAGEFLR4 UNIT HEATERFAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0.01 | 0.01 | 0.01 | 0.01
| GUESTROOM101 PTACFAN | 0.14 | 0.12 | 0.13 | 0.12 | 0.13 | 0.12 | 0.12 | 0.11 | 0.12 | 0.12 | 0.11 | 0.12 | 0.11 | 0.11 | 0.1 | 0.11
| GUESTROOM102 PTACFAN | 0.14 | 0.12 | 0.14 | 0.12 | 0.14 | 0.13 | 0.12 | 0.11 | 0.12 | 0.12 | 0.11 | 0.12 | 0.11 | 0.12 | 0.11 | 0.11
| GUESTROOM103 PTACFAN | 0.17 | 0.13 | 0.16 | 0.13 | 0.14 | 0.14 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.11 | 0.11 | 0.1 | 0.1
| GUESTROOM104 PTACFAN | 0.17 | 0.13 | 0.14 | 0.12 | 0.11 | 0.13 | 0.08 | 0.11 | 0.11 | 0.09 | 0.11 | 0.11 | 0.11 | 0.1 | 0.09 | 0.08
| GUESTROOM105 PTACFAN | 0.15 | 0.12 | 0.13 | 0.12 | 0.11 | 0.12 | 0.09 | 0.11 | 0.12 | 0.1 | 0.11 | 0.12 | 0.11 | 0.11 | 0.1 | 0.09
| GUESTROOM201 PTACFAN | 0.36 | 0.2 | 0.27 | 0.19 | 0.22 | 0.23 | 0.18 | 0.17 | 0.19 | 0.17 | 0.17 | 0.18 | 0.15 | 0.16 | 0.14 | 0.16
| GUESTROOM202_205 PTACFAN | 0.56 | 0.53 | 0.63 | 0.54 | 0.59 | 0.61 | 0.59 | 0.52 | 0.59 | 0.58 | 0.53 | 0.59 | 0.52 | 0.57 | 0.53 | 0.6
| GUESTROOM206_208 PTACFAN | 0.45 | 0.43 | 0.51 | 0.44 | 0.48 | 0.49 | 0.49 | 0.42 | 0.48 | 0.48 | 0.43 | 0.47 | 0.42 | 0.46 | 0.44 | 0.51
| GUESTROOM209_212 PTACFAN | 0.55 | 0.52 | 0.62 | 0.53 | 0.58 | 0.59 | 0.58 | 0.51 | 0.58 | 0.57 | 0.52 | 0.57 | 0.51 | 0.56 | 0.52 | 0.58
| GUESTROOM213 PTACFAN | 0.17 | 0.15 | 0.18 | 0.15 | 0.16 | 0.17 | 0.15 | 0.14 | 0.15 | 0.15 | 0.14 | 0.15 | 0.14 | 0.15 | 0.14 | 0.15
| GUESTROOM214 PTACFAN | 0.18 | 0.15 | 0.17 | 0.15 | 0.13 | 0.16 | 0.12 | 0.14 | 0.15 | 0.13 | 0.14 | 0.14 | 0.13 | 0.14 | 0.13 | 0.12
| GUESTROOM215_218 PTACFAN | 0.63 | 0.54 | 0.61 | 0.54 | 0.5 | 0.6 | 0.47 | 0.52 | 0.6 | 0.5 | 0.53 | 0.59 | 0.52 | 0.56 | 0.51 | 0.49
| GUESTROOM219 PTACFAN | 0.19 | 0.17 | 0.19 | 0.17 | 0.15 | 0.18 | 0.15 | 0.16 | 0.19 | 0.15 | 0.16 | 0.18 | 0.16 | 0.17 | 0.16 | 0.15
| GUESTROOM220_223 PTACFAN | 0.6 | 0.51 | 0.57 | 0.51 | 0.46 | 0.56 | 0.44 | 0.48 | 0.55 | 0.46 | 0.49 | 0.54 | 0.48 | 0.52 | 0.47 | 0.46
| GUESTROOM224 PTACFAN | 0.17 | 0.14 | 0.17 | 0.14 | 0.13 | 0.16 | 0.12 | 0.13 | 0.15 | 0.12 | 0.13 | 0.14 | 0.13 | 0.14 | 0.13 | 0.12
| GUESTROOM301 PTACFAN | 0.36 | 0.2 | 0.27 | 0.19 | 0.21 | 0.23 | 0.18 | 0.17 | 0.19 | 0.17 | 0.17 | 0.17 | 0.15 | 0.16 | 0.14 | 0.16
| GUESTROOM302_305 PTACFAN | 0.56 | 0.53 | 0.63 | 0.55 | 0.58 | 0.61 | 0.59 | 0.52 | 0.6 | 0.58 | 0.53 | 0.59 | 0.53 | 0.58 | 0.54 | 0.61
| GUESTROOM306_308 PTACFAN | 0.46 | 0.43 | 0.52 | 0.45 | 0.49 | 0.51 | 0.5 | 0.43 | 0.49 | 0.49 | 0.44 | 0.48 | 0.43 | 0.48 | 0.45 | 0.53
| GUESTROOM309_312 PTACFAN | 0.56 | 0.53 | 0.63 | 0.54 | 0.58 | 0.61 | 0.59 | 0.52 | 0.6 | 0.58 | 0.53 | 0.59 | 0.52 | 0.57 | 0.54 | 0.61
| GUESTROOM313 PTACFAN | 0.17 | 0.15 | 0.19 | 0.15 | 0.16 | 0.17 | 0.15 | 0.14 | 0.16 | 0.15 | 0.14 | 0.15 | 0.14 | 0.15 | 0.14 | 0.15
| GUESTROOM314 PTACFAN | 0.18 | 0.15 | 0.18 | 0.15 | 0.13 | 0.17 | 0.12 | 0.14 | 0.15 | 0.13 | 0.14 | 0.15 | 0.14 | 0.14 | 0.13 | 0.13
| GUESTROOM315_318 PTACFAN | 0.61 | 0.52 | 0.6 | 0.52 | 0.48 | 0.58 | 0.46 | 0.5 | 0.58 | 0.48 | 0.51 | 0.57 | 0.5 | 0.54 | 0.5 | 0.48
| GUESTROOM319 PTACFAN | 0.16 | 0.14 | 0.16 | 0.14 | 0.13 | 0.15 | 0.12 | 0.13 | 0.15 | 0.13 | 0.13 | 0.15 | 0.13 | 0.14 | 0.13 | 0.13
| GUESTROOM320_323 PTACFAN | 0.6 | 0.52 | 0.59 | 0.52 | 0.47 | 0.57 | 0.45 | 0.49 | 0.57 | 0.47 | 0.5 | 0.56 | 0.5 | 0.53 | 0.49 | 0.47
| GUESTROOM324 PTACFAN | 0.17 | 0.14 | 0.17 | 0.14 | 0.13 | 0.16 | 0.12 | 0.13 | 0.15 | 0.13 | 0.14 | 0.14 | 0.13 | 0.14 | 0.13 | 0.12
| GUESTROOM401 PTACFAN | 0.37 | 0.21 | 0.28 | 0.21 | 0.22 | 0.23 | 0.18 | 0.18 | 0.2 | 0.17 | 0.17 | 0.17 | 0.16 | 0.16 | 0.14 | 0.16
| GUESTROOM402_405 PTACFAN | 0.62 | 0.57 | 0.62 | 0.59 | 0.58 | 0.6 | 0.6 | 0.54 | 0.61 | 0.58 | 0.54 | 0.58 | 0.53 | 0.56 | 0.52 | 0.61
| GUESTROOM406_408 PTACFAN | 0.5 | 0.47 | 0.5 | 0.48 | 0.48 | 0.49 | 0.5 | 0.44 | 0.5 | 0.49 | 0.44 | 0.48 | 0.43 | 0.46 | 0.43 | 0.53
| GUESTROOM409_412 PTACFAN | 0.62 | 0.57 | 0.62 | 0.59 | 0.58 | 0.6 | 0.6 | 0.54 | 0.61 | 0.58 | 0.54 | 0.58 | 0.53 | 0.56 | 0.52 | 0.61
| GUESTROOM413 PTACFAN | 0.18 | 0.16 | 0.18 | 0.16 | 0.16 | 0.17 | 0.16 | 0.15 | 0.16 | 0.15 | 0.15 | 0.15 | 0.14 | 0.15 | 0.13 | 0.16
| GUESTROOM414 PTACFAN | 0.19 | 0.17 | 0.19 | 0.17 | 0.15 | 0.18 | 0.13 | 0.15 | 0.16 | 0.14 | 0.15 | 0.15 | 0.14 | 0.15 | 0.13 | 0.13
| GUESTROOM415_418 PTACFAN | 0.66 | 0.58 | 0.63 | 0.59 | 0.55 | 0.61 | 0.5 | 0.54 | 0.61 | 0.51 | 0.54 | 0.58 | 0.52 | 0.55 | 0.5 | 0.48
| GUESTROOM419 PTACFAN | 0.17 | 0.15 | 0.16 | 0.15 | 0.14 | 0.16 | 0.13 | 0.14 | 0.16 | 0.13 | 0.14 | 0.15 | 0.13 | 0.14 | 0.13 | 0.12
| GUESTROOM420_423 PTACFAN | 0.65 | 0.58 | 0.62 | 0.59 | 0.54 | 0.61 | 0.5 | 0.53 | 0.61 | 0.51 | 0.53 | 0.57 | 0.51 | 0.54 | 0.5 | 0.48
| GUESTROOM424 PTACFAN | 0.19 | 0.16 | 0.18 | 0.16 | 0.15 | 0.17 | 0.13 | 0.15 | 0.16 | 0.14 | 0.15 | 0.15 | 0.14 | 0.14 | 0.13 | 0.12
| REARSTAIRSFLR1 UNIT HEATERFAN | 0.02 | 0.03 | 0.03 | 0.05 | 0.01 | 0.03 | 0.02 | 0.05 | 0.05 | 0.03 | 0.08 | 0.07 | 0.09 | 0.1 | 0.1 | 0.14
| REARSTAIRSFLR2 UNIT HEATERFAN | 0.02 | 0.03 | 0.02 | 0.04 | 0.01 | 0.03 | 0.02 | 0.05 | 0.04 | 0.03 | 0.07 | 0.06 | 0.08 | 0.08 | 0.09 | 0.12
| REARSTAIRSFLR3 UNIT HEATERFAN | 0.02 | 0.03 | 0.02 | 0.04 | 0.01 | 0.03 | 0.02 | 0.05 | 0.04 | 0.03 | 0.07 | 0.07 | 0.08 | 0.09 | 0.09 | 0.12
| REARSTAIRSFLR4 UNIT HEATERFAN | 0.02 | 0.04 | 0.03 | 0.05 | 0.02 | 0.03 | 0.02 | 0.05 | 0.05 | 0.04 | 0.08 | 0.07 | 0.09 | 0.09 | 0.09 | 0.13
| REARSTORAGEFLR1 UNIT HEATERFAN | 0.01 | 0.02 | 0.02 | 0.03 | 0.01 | 0.02 | 0.01 | 0.03 | 0.03 | 0.02 | 0.04 | 0.04 | 0.05 | 0.05 | 0.05 | 0.07
| REARSTORAGEFLR2 UNIT HEATERFAN | 0.02 | 0.02 | 0.02 | 0.03 | 0.01 | 0.02 | 0.01 | 0.03 | 0.03 | 0.02 | 0.04 | 0.04 | 0.04 | 0.05 | 0.05 | 0.06
| REARSTORAGEFLR3 UNIT HEATERFAN | 0.02 | 0.02 | 0.02 | 0.03 | 0.01 | 0.02 | 0.01 | 0.03 | 0.03 | 0.02 | 0.04 | 0.04 | 0.05 | 0.05 | 0.05 | 0.06
| REARSTORAGEFLR4 UNIT HEATERFAN | 0.02 | 0.02 | 0.02 | 0.03 | 0.01 | 0.02 | 0.01 | 0.03 | 0.03 | 0.02 | 0.04 | 0.04 | 0.05 | 0.05 | 0.05 | 0.07
| PSZ-HEATCOOL:1_FAN | 0.63 | 0.58 | 0.6 | 0.58 | 0.54 | 0.56 | 0.44 | 0.55 | 0.6 | 0.5 | 0.55 | 0.58 | 0.55 | 0.56 | 0.51 | 0.45
| PSZ-HEATCOOL:10_FAN | 0.39 | 0.32 | 0.37 | 0.31 | 0.31 | 0.35 | 0.28 | 0.3 | 0.34 | 0.29 | 0.3 | 0.33 | 0.3 | 0.31 | 0.29 | 0.29
| PSZ-HEATCOOL:11_FAN | 0.37 | 0.29 | 0.35 | 0.29 | 0.29 | 0.33 | 0.26 | 0.28 | 0.31 | 0.27 | 0.28 | 0.3 | 0.27 | 0.29 | 0.27 | 0.27
| PSZ-HEATCOOL:12_FAN | 0.43 | 0.35 | 0.38 | 0.36 | 0.36 | 0.36 | 0.3 | 0.32 | 0.34 | 0.3 | 0.31 | 0.31 | 0.29 | 0.29 | 0.27 | 0.26
| PSZ-HEATCOOL:2_FAN | 1.02 | 0.87 | 1 | 0.87 | 0.95 | 0.94 | 0.88 | 0.81 | 0.9 | 0.89 | 0.82 | 0.88 | 0.8 | 0.85 | 0.79 | 0.88
| PSZ-HEATCOOL:3_FAN | 0.12 | 0.1 | 0.11 | 0.1 | 0.1 | 0.1 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.09 | 0.08 | 0.09 | 0.07 | 0.07
| PSZ-HEATCOOL:4_FAN | 0.52 | 0.49 | 0.53 | 0.49 | 0.52 | 0.52 | 0.49 | 0.47 | 0.53 | 0.49 | 0.47 | 0.52 | 0.47 | 0.5 | 0.46 | 0.47
| PSZ-HEATCOOL:5_FAN | 0.09 | 0.06 | 0.08 | 0.06 | 0.07 | 0.06 | 0.05 | 0.06 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.06
| PSZ-HEATCOOL:6_FAN | 0.37 | 0.34 | 0.35 | 0.34 | 0.32 | 0.35 | 0.3 | 0.33 | 0.38 | 0.32 | 0.33 | 0.38 | 0.33 | 0.36 | 0.32 | 0.31
| PSZ-HEATCOOL:7_FAN | 1.71 | 1.68 | 1.73 | 1.73 | 1.64 | 1.77 | 1.58 | 1.66 | 1.96 | 1.63 | 1.69 | 1.95 | 1.69 | 1.85 | 1.69 | 1.6
| PSZ-HEATCOOL:8_FAN | 0.17 | 0.15 | 0.16 | 0.15 | 0.14 | 0.15 | 0.12 | 0.14 | 0.16 | 0.13 | 0.14 | 0.15 | 0.14 | 0.14 | 0.13 | 0.12
| PSZ-HEATCOOL:9_FAN | 0.59 | 0.48 | 0.51 | 0.46 | 0.42 | 0.47 | 0.34 | 0.43 | 0.47 | 0.38 | 0.43 | 0.45 | 0.42 | 0.43 | 0.38 | 0.33
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.078551 | 0.10838 | 0.085704 | 0.10029 | 0.1229 | 0.094786 | 0.14517 | 0.069114 | 0.037185 | 0.07184 | 0.09746 | 0.037192 | 0.054976 | 0.071172 | 0.054806 | 0.090949
| Total Cost ($/m2) | 15.18 | 18.45 | 14.85 | 15.6 | 18.09 | 15.03 | 19.67 | 10.33 | 5.46 | 9.63 | 14.36 | 5.3 | 8.24 | 10.01 | 7.94 | 14.55
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011456 | 0.0081752 | 0.0085359 | 0.01059 | 0.0084159 | 0.0080647 | 0.0084201 | 0.0099958 | 0.0071504 | 0.0083061 | 0.0087777 | 0.0071485 | 0.0079527 | 0.0086237 | 0.0079513 | 0.0041739
| Total Cost ($/m2) | 1.32 | 1.24 | 1.17 | 1.96 | 1.31 | 1.29 | 1.62 | 2.27 | 1.44 | 1.88 | 2.32 | 1.69 | 2.4 | 2.41 | 2.77 | 1.95
Total Utility Costs
| Cost Intensity ($/m2) | 16.5 | 19.69 | 16.02 | 17.57 | 19.41 | 16.32 | 21.3 | 12.6 | 6.9 | 11.51 | 16.68 | 6.99 | 10.65 | 12.42 | 10.71 | 16.5
Energy - End Uses
Electricity (kWh)
| Heating | 161.1111 | 3800 | 1408.3333 | 9361.1111 | 130.5556 | 2383.3333 | 777.7778 | 15822.2222 | 6738.8889 | 6197.2222 | 30519.4444 | 15619.4444 | 50711.1111 | 33425 | 62480.5556 | 154983.3333
| Cooling | 353622.2222 | 247052.7778 | 257750 | 169341.6667 | 137361.1111 | 187738.8889 | 86352.7778 | 137375 | 125266.6667 | 72636.1111 | 112758.3333 | 98066.6667 | 106275 | 74977.7778 | 72188.8889 | 57188.8889
| Interior Lighting | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667 | 272316.6667
| Exterior Lighting | 46566.6667 | 46483.3333 | 46472.2222 | 46547.2222 | 46541.6667 | 46494.4444 | 46444.4444 | 46491.6667 | 46483.3333 | 46416.6667 | 46427.7778 | 46436.1111 | 46466.6667 | 46411.1111 | 46397.2222 | 46119.4444
| Interior Equipment | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667 | 225616.6667
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 87763.8889 | 73452.7778 | 80522.2222 | 70469.4444 | 69072.2222 | 74205.5556 | 59786.1111 | 64675 | 72216.6667 | 60613.8889 | 63930.5556 | 69119.4444 | 63672.2222 | 64941.6667 | 60305.5556 | 59997.2222
| Pumps | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667 | 741.6667
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 986791.6667 | 869466.6667 | 884827.7778 | 794397.2222 | 751777.7778 | 809497.2222 | 692036.1111 | 763041.6667 | 749383.3333 | 684538.8889 | 752313.8889 | 727916.6667 | 765800 | 718430.5556 | 740047.2222 | 816963.8889
Gas (MJ)
| Heating | 9380 | 113310 | 87560 | 210470 | 75380 | 147510 | 197710 | 360990 | 242390 | 324920 | 499540 | 357820 | 644990 | 522560 | 806390 | 1325340
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480 | 189480
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 390440 | 470340 | 424460 | 547360 | 532400 | 479780 | 598240 | 607860 | 596380 | 639320 | 660940 | 658180 | 706830 | 715170 | 782550 | 874160
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 589300 | 773130 | 701500 | 947310 | 797250 | 816770 | 985430 | 1158330 | 1028240 | 1153720 | 1349960 | 1205480 | 1541300 | 1427210 | 1778420 | 2388970
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 4141750 | 3903210 | 3886880 | 3807150 | 3503660 | 3730960 | 3476760 | 3905270 | 3726020 | 3618070 | 4058290 | 3825990 | 4298180 | 4013560 | 4442590 | 5330050
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0.11359 | 2.6791 | 0.99291 | 6.5998 | 0.092045 | 1.6803 | 0.54835 | 11.155 | 4.7511 | 4.3692 | 21.5169 | 11.0121 | 35.7525 | 23.5654 | 44.0503 | 109.267
| Cooling (elec) | 249.3121 | 174.1781 | 181.7199 | 119.3899 | 96.8429 | 132.3604 | 60.8808 | 96.8527 | 88.316 | 51.2102 | 79.4973 | 69.1393 | 74.9264 | 52.8611 | 50.8949 | 40.3195
| Interior Lighting (elec) | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898 | 191.9898
| Exterior Lighting (elec) | 32.8306 | 32.7719 | 32.764 | 32.8169 | 32.813 | 32.7797 | 32.7444 | 32.7777 | 32.7719 | 32.7249 | 32.7327 | 32.7386 | 32.7601 | 32.7209 | 32.7111 | 32.5153
| Interior Equipment (elec) | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651 | 159.0651
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 61.8756 | 51.786 | 56.7701 | 49.6826 | 48.6976 | 52.3167 | 42.1506 | 45.5974 | 50.9145 | 42.7342 | 45.0726 | 48.7309 | 44.8904 | 45.7854 | 42.5169 | 42.2995
| Pumps (elec) | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289 | 0.52289
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 695.7117 | 612.9948 | 623.8247 | 560.069 | 530.0213 | 570.7149 | 487.902 | 537.9626 | 528.3331 | 482.6163 | 530.3993 | 513.1986 | 539.9073 | 506.5107 | 521.751 | 575.9791
Gas (MJ/m2)
| Heating (gas) | 1.837 | 22.1906 | 17.1477 | 41.2184 | 14.7624 | 28.8884 | 38.7195 | 70.6963 | 47.4696 | 63.6323 | 97.8299 | 70.0755 | 126.3148 | 102.3381 | 157.9234 | 259.5545
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078 | 37.1078
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 76.4638 | 92.1114 | 83.1262 | 107.195 | 104.2652 | 93.9601 | 117.1593 | 119.0433 | 116.795 | 125.2044 | 129.4385 | 128.8979 | 138.4256 | 140.0589 | 153.2546 | 171.1955
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 115.4085 | 151.4098 | 137.3817 | 185.5212 | 156.1334 | 159.9562 | 192.9866 | 226.8473 | 201.3705 | 225.9445 | 264.3761 | 236.0812 | 301.8481 | 279.5048 | 348.2857 | 467.8558
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 811.1202 | 764.4045 | 761.2065 | 745.5921 | 686.1567 | 730.6711 | 680.8886 | 764.8079 | 729.7036 | 708.5627 | 794.7754 | 749.2818 | 841.7554 | 786.0155 | 870.0367 | 1043.8368
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 162.8865 | 153.9943 | 139.6772 | 137.3592 | 136.7128 | 126.9929 | 129.1851 | 135.7411 | 127.9252 | 122.39 | 153.4806 | 139.5417 | 166.1426 | 167.3796 | 166.5261 | 223.9511
| Feb | 167.5819 | 148.4113 | 139.3694 | 139.0043 | 138.0186 | 132.6513 | 135.6101 | 124.7856 | 131.4715 | 128.915 | 128.4371 | 131.3831 | 151.8694 | 144.5077 | 168.2842 | 223.302
| Mar | 169.5645 | 160.1718 | 160.2143 | 145.6174 | 136.2882 | 137.5479 | 131.6645 | 142.5749 | 134.8798 | 136.668 | 136.2108 | 136.882 | 135.2243 | 133.9336 | 136.871 | 172.0012
| Apr | 176.1395 | 171.27 | 160.9753 | 156.4656 | 143.4217 | 157.0759 | 137.689 | 144.0511 | 145.7743 | 137.6997 | 135.3217 | 142.6048 | 145.4787 | 134.1647 | 130.4085 | 126.8102
| May | 181.171 | 183.3993 | 186.2866 | 171.2883 | 147.4999 | 165.0721 | 139.4274 | 156.8543 | 153.0708 | 142.3287 | 151.8902 | 150.1397 | 170.1107 | 140.882 | 138.7504 | 129.6818
| Jun | 198.4029 | 180.3902 | 213.6264 | 174.1374 | 145.986 | 196.7166 | 140.3197 | 175.8262 | 160.1217 | 144.9623 | 164.9243 | 153.9427 | 167.7367 | 155.3715 | 157.2816 | 139.2958
| Jul | 190.4827 | 189.0325 | 209.6651 | 185.9466 | 149.0191 | 193.4921 | 159.6638 | 185.6502 | 170.14 | 152.522 | 174.372 | 162.1127 | 175.9863 | 150.5014 | 162.6485 | 145.9273
| Aug | 191.1195 | 195.4974 | 212.79 | 175.7916 | 150.8817 | 189.298 | 140.9581 | 185.0681 | 168.3466 | 153.5042 | 180.9649 | 158.3081 | 175.3081 | 155.6693 | 165.5748 | 138.6335
| Sep | 185.2119 | 181.8937 | 194.7528 | 167.152 | 150.7327 | 173.8937 | 151.6299 | 159.2901 | 155.8981 | 159.1452 | 156.8641 | 151.5692 | 152.3859 | 152.0657 | 148.9627 | 133.7308
| Oct | 182.5161 | 172.0405 | 165.7558 | 156.1586 | 145.1383 | 153.6135 | 139.837 | 154.0399 | 145.5546 | 138.7368 | 146.173 | 144.3626 | 147.0686 | 137.6253 | 141.7853 | 135.6164
| Nov | 172.3853 | 161.1248 | 144.2763 | 140.5077 | 139.9376 | 135.3492 | 133.1861 | 148.4212 | 134.8175 | 135.4474 | 145.8294 | 131.8781 | 133.2813 | 129.5265 | 135.7246 | 167.6646
| Dec | 162.6073 | 160.3386 | 139.9062 | 137.6401 | 136.7379 | 130.0327 | 128.7408 | 126.9666 | 126.4979 | 125.3726 | 143.4996 | 135.3989 | 165.5646 | 159.1475 | 160.2565 | 200.368
Time of Peak Electrical Demand
| Jan | 22-JAN-08:00 | 22-JAN-20:00 | 29-JAN-20:15 | 24-JAN-20:30 | 26-JAN-20:30 | 18-JAN-20:00 | 15-JAN-20:30 | 31-JAN-07:15 | 26-JAN-20:30 | 28-JAN-20:00 | 07-JAN-07:15 | 06-JAN-07:15 | 06-JAN-07:15 | 07-JAN-08:15 | 09-JAN-07:15 | 13-JAN-09:00
| Feb | 20-FEB-08:00 | 20-FEB-20:45 | 27-FEB-20:15 | 20-FEB-20:00 | 12-FEB-20:30 | 26-FEB-20:00 | 15-FEB-20:30 | 15-FEB-20:45 | 14-FEB-20:30 | 21-FEB-20:00 | 11-FEB-08:15 | 12-FEB-20:00 | 04-FEB-06:15 | 26-FEB-07:15 | 02-FEB-07:15 | 04-FEB-08:15
| Mar | 13-MAR-19:15 | 26-MAR-19:15 | 17-MAR-19:15 | 28-MAR-19:30 | 04-MAR-20:00 | 31-MAR-19:00 | 30-MAR-19:00 | 09-MAR-20:00 | 20-MAR-19:15 | 29-MAR-19:00 | 14-MAR-19:00 | 26-MAR-19:15 | 19-MAR-19:00 | 30-MAR-19:30 | 09-MAR-06:15 | 14-MAR-07:15
| Apr | 01-APR-19:15 | 30-APR-19:15 | 02-APR-19:15 | 15-APR-19:15 | 11-APR-19:15 | 21-APR-19:15 | 29-APR-19:15 | 04-APR-19:30 | 22-APR-19:15 | 29-APR-19:15 | 28-APR-19:00 | 25-APR-19:00 | 02-APR-19:00 | 30-APR-19:30 | 15-APR-19:15 | 23-APR-20:45
| May | 15-MAY-19:15 | 26-MAY-19:15 | 28-MAY-19:30 | 14-MAY-19:30 | 29-MAY-19:15 | 31-MAY-19:15 | 25-MAY-19:15 | 15-MAY-19:15 | 30-MAY-19:15 | 04-MAY-19:30 | 30-MAY-19:15 | 23-MAY-19:15 | 27-MAY-19:45 | 25-MAY-19:00 | 27-MAY-19:45 | 29-MAY-19:00
| Jun | 27-JUN-19:15 | 13-JUN-19:30 | 27-JUN-19:45 | 19-JUN-19:00 | 28-JUN-19:15 | 27-JUN-19:15 | 16-JUN-19:30 | 30-JUN-19:45 | 28-JUN-19:30 | 18-JUN-20:15 | 16-JUN-19:30 | 27-JUN-19:30 | 29-JUN-19:00 | 25-JUN-20:30 | 14-JUN-19:00 | 23-JUN-19:00
| Jul | 04-JUL-19:15 | 03-JUL-19:30 | 11-JUL-19:45 | 02-JUL-19:00 | 10-JUL-19:15 | 25-JUL-19:15 | 02-JUL-19:30 | 24-JUL-19:30 | 30-JUL-19:15 | 24-JUL-19:00 | 02-JUL-19:30 | 17-JUL-19:30 | 13-JUL-19:00 | 21-JUL-20:15 | 06-JUL-19:00 | 29-JUL-19:00
| Aug | 21-AUG-19:15 | 06-AUG-19:15 | 01-AUG-19:30 | 14-AUG-19:30 | 16-AUG-19:15 | 06-AUG-19:15 | 27-AUG-19:15 | 17-AUG-19:15 | 01-AUG-19:15 | 06-AUG-19:45 | 04-AUG-19:15 | 29-AUG-19:15 | 27-AUG-19:15 | 11-AUG-19:45 | 13-AUG-19:30 | 19-AUG-20:00
| Sep | 10-SEP-19:15 | 04-SEP-19:15 | 09-SEP-19:15 | 10-SEP-19:15 | 24-SEP-19:00 | 01-SEP-19:00 | 28-SEP-19:00 | 09-SEP-19:15 | 02-SEP-19:15 | 02-SEP-19:15 | 06-SEP-19:15 | 01-SEP-19:30 | 14-SEP-19:15 | 02-SEP-19:15 | 08-SEP-19:15 | 09-SEP-19:45
| Oct | 06-OCT-19:15 | 29-OCT-19:30 | 02-OCT-19:30 | 21-OCT-19:15 | 05-OCT-19:30 | 06-OCT-19:30 | 13-OCT-19:30 | 20-OCT-19:30 | 01-OCT-19:15 | 09-OCT-19:15 | 30-OCT-19:30 | 01-OCT-19:15 | 08-OCT-19:15 | 06-OCT-19:15 | 07-OCT-19:30 | 22-OCT-07:15
| Nov | 01-NOV-19:15 | 27-NOV-20:15 | 05-NOV-19:15 | 22-NOV-20:00 | 09-NOV-20:45 | 09-NOV-20:00 | 12-NOV-20:45 | 04-NOV-19:30 | 09-NOV-20:00 | 04-NOV-19:15 | 02-NOV-19:30 | 04-NOV-19:15 | 02-NOV-19:00 | 21-NOV-20:00 | 25-NOV-08:15 | 23-NOV-08:15
| Dec | 16-DEC-08:00 | 02-DEC-20:15 | 13-DEC-20:45 | 04-DEC-20:00 | 18-DEC-20:30 | 05-DEC-20:30 | 03-DEC-20:30 | 21-DEC-07:15 | 08-DEC-20:00 | 31-DEC-20:00 | 31-DEC-20:00 | 12-DEC-07:15 | 31-DEC-06:15 | 11-DEC-07:15 | 31-DEC-08:15 | 29-DEC-08:00
Source Energy
| Total Source Energy (GJ) | 12427 | 12212.7 | 10841.39 | 10654.94 | 9246.92 | 11315.98 | 8786.76 | 11087.98 | 10074.06 | 5552.75 | 11077.89 | 10011.22 | 11158.49 | 10548.67 | 11098.8 | 13114.27
| Total Source Energy (MJ/m2) | 2433.7 | 2391.74 | 2123.18 | 2086.67 | 1810.92 | 2216.12 | 1720.8 | 2171.47 | 1972.9 | 1087.45 | 2169.49 | 1960.6 | 2185.28 | 2065.85 | 2173.59 | 2568.3
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09
| Total Building | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09 | 3470.09
Emissions
| Carbon Equivalent (kg) | 281254.1195 | 303961.6232 | 279757.5539 | 261786.3722 | 102233.9148 | 287752.016 | 98645.3865 | 226798.6232 | 324663.0201 | 70662.5949 | 425438.6169 | 319091.0804 | 289921.6875 | 288277.9421 | 285383.0478 | 272963.1425
| CO2 (kg) | 657354.9406 | 768023.3348 | 664704.6659 | 604734.629 | 276101.0029 | 689213.0604 | 267264.6001 | 522110.8737 | 766863.1028 | 178545.288 | 995768.3263 | 755666.9097 | 684609.5973 | 684994.9145 | 676642.5244 | 700327.5256
| NOX (kg) | 1133.0414 | 993.1211 | 1094.8673 | 1117.2454 | 238.4441 | 1099.1079 | 231.3929 | 978.0383 | 1300.1337 | 244.8677 | 1748.9742 | 1272.6711 | 1175.6552 | 1151.4465 | 1149.7888 | 834.4435
| SO2 (kg) | 4224.0219 | 4147.5618 | 3558.2547 | 2788.5913 | 2187.8007 | 4453.1051 | 2014.008 | 2785.7167 | 3272.677 | 529.4038 | 5070.35 | 3178.9944 | 1807.8232 | 1918.6789 | 1747.1091 | 4159.3169
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0193 | 0.0117 | 0.0097 | 0.0103 | 0.0011 | 0.0084 | 0.001 | 0.0113 | 0.0129 | 0.0022 | 0.0154 | 0.0125 | 0.0133 | 0.0134 | 0.0129 | 0.0143
| Water for Electricity (m3) | 522.7609 | 1414.72 | 26283.3 | 4959.9 | 13199.6 | 22207.8 | 12150.6 | 173.2391 | 3402.79 | 6993.81 | 1167.17 | 3305.33 | 1188.09 | 45508.4 | 1148.14 | 834.6764

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4141.75 | 811.12 | 1047.65
Net Site Energy | 4141.75 | 811.12 | 1047.65
Total Source Energy | 12427 | 2433.7 | 3143.38
Net Source Energy | 12427 | 2433.7 | 3143.38
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.58 | 9.38 | 0 | 0 | 0 | 0
Cooling | 1273.04 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.64 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 315.95 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 390.44 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3552.45 | 589.3 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 3.125 | 5.873 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.42 | 0.468 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.42 | 0.468 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.42 | 0.468 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.42 | 0.468 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 72.38 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 111.83 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2626.62 | 1973.88 | 652.73 | 0.75 | 2.75
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2686.63 | 2026.9 | 659.73 | 0.75 | 2.74
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3020.38 | 2324.64 | 695.73 | 0.77 | 2.68
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2941.04 | 2282.6 | 658.44 | 0.78 | 2.71
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2781.08 | 2141.62 | 639.47 | 0.77 | 2.73
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6035.46 | 4820.25 | 1215.21 | 0.8 | 2.44
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10513.94 | 7966.34 | 2547.6 | 0.76 | 2.41
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8339.59 | 6348.02 | 1991.57 | 0.76 | 2.42
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10345.96 | 7817.57 | 2528.39 | 0.76 | 2.41
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3000.38 | 2326.91 | 673.47 | 0.78 | 2.69
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3074.07 | 2419.97 | 654.1 | 0.79 | 2.69
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11119.87 | 8628.38 | 2491.49 | 0.78 | 2.43
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3184.9 | 2523.01 | 661.9 | 0.79 | 2.67
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10671.19 | 8225.03 | 2446.16 | 0.77 | 2.42
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2998.61 | 2354.42 | 644.19 | 0.79 | 2.7
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6008.76 | 4798.92 | 1209.83 | 0.8 | 2.44
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10476.29 | 7942.45 | 2533.84 | 0.76 | 2.41
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8363.58 | 6376.76 | 1986.82 | 0.76 | 2.42
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10410.56 | 7884.15 | 2526.41 | 0.76 | 2.41
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2971.02 | 2298.9 | 672.12 | 0.77 | 2.7
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3078.44 | 2426.48 | 651.96 | 0.79 | 2.69
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10842.09 | 8378.45 | 2463.64 | 0.77 | 2.42
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2855.57 | 2225.22 | 630.35 | 0.78 | 2.72
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10739.01 | 8285.82 | 2453.18 | 0.77 | 2.42
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3001.81 | 2357.31 | 644.5 | 0.79 | 2.7
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6104.37 | 4875.29 | 1229.08 | 0.8 | 2.44
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11205.41 | 8626.54 | 2578.88 | 0.77 | 2.42
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8970.74 | 6937.61 | 2033.13 | 0.77 | 2.42
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11163.83 | 8579 | 2584.83 | 0.77 | 2.42
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3155.44 | 2471.07 | 684.37 | 0.78 | 2.67
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3230.84 | 2566.59 | 664.25 | 0.79 | 2.66
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11452.52 | 8934.71 | 2517.82 | 0.78 | 2.43
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2985.7 | 2344.54 | 641.17 | 0.79 | 2.7
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11380.99 | 8870.14 | 2510.85 | 0.78 | 2.43
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3189.07 | 2528.99 | 660.08 | 0.79 | 2.67
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10763 | 8502.43 | 2260.57 | 0.79 | 4
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6955.4 | 5376.07 | 1579.33 | 0.77 | 3.95
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6623.47 | 5094.07 | 1529.4 | 0.77 | 3.93
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7444.22 | 5810.47 | 1633.75 | 0.78 | 3.97
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 25312.38 | 17113.27 | 8199.1 | 0.68 | 3.44
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1965.34 | 1566.84 | 398.5 | 0.8 | 4.03
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13036.48 | 8813.75 | 4222.73 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1739.89 | 1270.01 | 469.88 | 0.73 | 3.81
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8794.28 | 6014.56 | 2779.73 | 0.68 | 3.68
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 32851.19 | 24553.14 | 8298.05 | 0.75 | 3.62
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4290.33 | 2900.62 | 1389.71 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13087.09 | 9261.23 | 3825.86 | 0.71 | 3.74
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 535.3 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 705.28 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 741.14 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 798.3 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 732.66 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 751.06 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 983.68 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 962.79 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 739.57 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1782.83 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 3214.19 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2411.98 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 3118.96 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1049.2 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1015.88 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2844.36 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 556.32 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 2968.91 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 944.59 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1847.94 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 3332.88 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2622.55 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 3293.42 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1088.12 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1062.52 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 3250.63 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 826.84 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 3224.67 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1004.35 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1987.15 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 3983.1 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 3164 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 3951.8 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1247.43 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1230.53 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 3941.43 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1073.83 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 3898.78 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1189.39 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 476.48 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 582.76 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 605.97 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 655.28 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 365.76 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 528.68 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 547.9 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 535.64 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 30358.37 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 9476.3 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 8951.54 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 10321.33 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 30093.49 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 2718.72 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 18819.79 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 2092.8 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 9785.33 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 81269.6 | 0.78
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 5701.72 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 15248.8 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.66 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.19 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.3 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.47 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.05 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.89 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.98 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.16 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 98.63 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.36 | 232.08 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 359.25 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 288.01 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 351.26 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 108.12 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 114.53 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 401.18 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 120.31 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 379.22 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 111.08 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.36 | 231.06 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 358.45 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 289.93 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 355.31 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.51 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 115.02 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 387.56 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.01 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 382.52 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 111.23 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.37 | 234.73 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 397.13 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 321.22 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 394.03 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 116.21 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 122.8 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.66 | 418.22 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 110.63 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.65 | 414.69 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 120.75 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.48 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.81 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.88 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.03 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.13 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.64 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.7 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.66 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.63 | 736.34 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.39 | 453.27 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.37 | 426.79 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 495.91 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.02 | 1161.21 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.12 | 137.18 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 608.93 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 99.13 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.37 | 423.91 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.71 | 1945.63 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.17 | 200.4 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.59 | 690.05 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.34 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 49738.6821 | 85.1499 | 315.0331 | 0 | 0.0014 | 38987.7388 | 21222.7899
February | 45545.1369 | 78.0891 | 289.4032 | 0 | 0.0013 | 35815.9414 | 19445.3168
March | 50829.2938 | 87.2594 | 323.849 | 0 | 0.0015 | 40078.9689 | 21712.432
April | 52519.85 | 90.4801 | 337.1268 | 0 | 0.0015 | 41722.4565 | 22466.4893
May | 57484.2529 | 99.2709 | 370.868 | 0 | 0.0017 | 45898.416 | 24613.9828
June | 58290.7556 | 100.836 | 377.428 | 0 | 0.0017 | 46710.4125 | 24976.5887
July | 62449.8106 | 108.1392 | 405.2119 | 0 | 0.0019 | 50149.0288 | 26769.5492
August | 62248.8941 | 107.7634 | 403.6889 | 0 | 0.0018 | 49960.5178 | 26680.6324
September | 58563.8976 | 101.2635 | 378.8423 | 0 | 0.0017 | 46885.4073 | 25089.1148
October | 57856.204 | 99.85 | 372.7701 | 0 | 0.0017 | 46133.7747 | 24766.9129
November | 51933.2307 | 89.3684 | 332.5658 | 0 | 0.0015 | 41157.9122 | 22205.4233
December | 49894.9321 | 85.5714 | 317.2346 | 0 | 0.0015 | 39260.3135 | 21304.8874
Annual Sum or Average | 657354.9406 | 1133.0414 | 4224.0219 | 0 | 0.0193 | 522760.8884 | 281254.1195
Minimum of Months | 45545.1369 | 78.0891 | 289.4032 | 0 | 0.0013 | 35815.9414 | 19445.3168
Maximum of Months | 62449.8106 | 108.1392 | 405.2119 | 0 | 0.0019 | 50149.0288 | 26769.5492
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 264943000000 | 162886.474 | 22-JAN-08:00 | 41071.521 | 57998.833 | 10976.376 | 0 | 52754.965 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 243389000000 | 167581.92 | 20-FEB-08:00 | 41071.521 | 57998.833 | 11245.764 | 0 | 57181.023 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 272359000000 | 169564.519 | 13-MAR-19:15 | 57185.041 | 38824.77 | 11126.815 | 0 | 51693.114 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 283527000000 | 176139.498 | 01-APR-19:15 | 57040.442 | 38772.136 | 11546.297 | 0 | 58045.845 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 311905000000 | 181171.038 | 15-MAY-19:15 | 57185.041 | 38824.77 | 11759.382 | 0 | 62667.067 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 317423000000 | 198402.898 | 27-JUN-19:15 | 57185.041 | 38824.77 | 12670.24 | 0 | 78988.068 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 340791000000 | 190482.663 | 04-JUL-19:15 | 57112.741 | 38807.225 | 12340.273 | 0 | 71487.645 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 339509000000 | 191119.5 | 21-AUG-19:15 | 57185.041 | 38824.77 | 12282.984 | 0 | 72091.927 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 318612000000 | 185211.851 | 10-SEP-19:15 | 57112.741 | 38807.225 | 12025.694 | 0 | 66531.412 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 313505000000 | 182516.137 | 06-OCT-19:15 | 57185.041 | 38824.77 | 11806.357 | 0 | 63965.19 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 279691000000 | 172385.265 | 01-NOV-19:15 | 57185.041 | 38824.77 | 11239.777 | 0 | 54400.899 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 266796000000 | 162607.264 | 16-DEC-08:00 | 41071.521 | 57998.833 | 10915.475 | 0 | 52536.656 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 3552450000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 243389000000 | 162607.264 |  | 41071.521 | 38772.136 | 10915.475 | 0 | 51693.114 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 340791000000 | 198402.898 |  | 57185.041 | 57998.833 | 12670.24 | 0 | 78988.068 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 77513.12 | 6751.31 | 0 | 84264.43
Cost per Total Building Area ($/m2) | 15.18 | 1.32 | 0 | 16.5
Cost per Net Conditioned Building Area ($/m2) | 19.61 | 1.71 | 0 | 21.31

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3903.21 | 764.4 | 987.31
Net Site Energy | 3903.21 | 764.4 | 987.31
Total Source Energy | 12212.7 | 2391.74 | 3089.18
Net Source Energy | 12212.7 | 2391.74 | 3089.18
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 13.68 | 113.31 | 0 | 0 | 0 | 0
Cooling | 889.39 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.34 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 264.43 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 470.34 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3130.08 | 773.13 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.852 | 0.976 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.375 | 0.412 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.375 | 0.412 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.375 | 0.412 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.375 | 0.412 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 72.38 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 111.83 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2388.25 | 1752.89 | 635.36 | 0.73 | 2.78
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2442.01 | 1799.42 | 642.59 | 0.74 | 2.77
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2570 | 1910.97 | 659.03 | 0.74 | 2.75
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2378.62 | 1797.04 | 581.58 | 0.76 | 2.8
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2353.5 | 1774.72 | 578.78 | 0.75 | 2.8
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3670.53 | 2805.51 | 865.02 | 0.76 | 2.56
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10219.86 | 7650.06 | 2569.8 | 0.75 | 2.41
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8159.91 | 6143.92 | 2016 | 0.75 | 2.41
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10064.24 | 7513.76 | 2550.48 | 0.75 | 2.41
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2753.48 | 2086.99 | 666.49 | 0.76 | 2.73
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2612.59 | 2020.82 | 591.77 | 0.77 | 2.77
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9877.71 | 7569.22 | 2308.48 | 0.77 | 2.42
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2860.89 | 2244.81 | 616.08 | 0.78 | 2.73
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9403.43 | 7145.19 | 2258.23 | 0.76 | 2.42
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2566.11 | 1979.06 | 587.05 | 0.77 | 2.77
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3656.29 | 2792.97 | 863.32 | 0.76 | 2.56
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10125.63 | 7567.38 | 2558.25 | 0.75 | 2.41
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8155.54 | 6140.03 | 2015.51 | 0.75 | 2.41
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10111.21 | 7554.57 | 2556.64 | 0.75 | 2.41
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2748.89 | 2082.87 | 666.02 | 0.76 | 2.73
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2645.07 | 2050.06 | 595.01 | 0.78 | 2.76
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9616.52 | 7335.53 | 2280.99 | 0.76 | 2.42
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2513.11 | 1931.49 | 581.63 | 0.77 | 2.78
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9514.59 | 7244.45 | 2270.14 | 0.76 | 2.42
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2582.82 | 1994.08 | 588.73 | 0.77 | 2.77
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3807.9 | 2936.51 | 871.39 | 0.77 | 2.54
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10440.26 | 7982.63 | 2457.63 | 0.76 | 2.42
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8453.93 | 6489.97 | 1963.96 | 0.77 | 2.42
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10443.31 | 7974.9 | 2468.41 | 0.76 | 2.42
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2834.67 | 2193.35 | 641.31 | 0.77 | 2.72
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2867.32 | 2250.63 | 616.69 | 0.78 | 2.73
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10379.9 | 8019.98 | 2359.93 | 0.77 | 2.42
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2676.36 | 2078.26 | 598.1 | 0.78 | 2.76
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10310.47 | 7957.56 | 2352.91 | 0.77 | 2.42
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2792.91 | 2190.16 | 602.75 | 0.78 | 2.74
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9877.39 | 7790.83 | 2086.56 | 0.79 | 4
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5880.53 | 4458.39 | 1422.14 | 0.76 | 3.9
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5538.86 | 4171.45 | 1367.41 | 0.75 | 3.88
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6359.07 | 4895.14 | 1463.93 | 0.77 | 3.94
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21615.93 | 14614.17 | 7001.76 | 0.68 | 3.45
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1631.37 | 1281.56 | 349.82 | 0.79 | 3.99
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12079.36 | 8166.65 | 3912.71 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1390.89 | 978.41 | 412.47 | 0.7 | 3.73
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8214.28 | 5595.79 | 2618.49 | 0.68 | 3.67
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 32234.96 | 24111.34 | 8123.63 | 0.75 | 3.63
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3685.43 | 2491.66 | 1193.77 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11084.7 | 7671.91 | 3412.79 | 0.69 | 3.7
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1106.26 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1071.47 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1110.23 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1258.17 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 29.84 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1045.36 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1067.12 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1291.18 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1272.95 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1060.06 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1901.49 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 4025.62 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 3118.26 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 3944.07 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1238 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1199.54 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 3661.43 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 734.42 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 3799.58 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1142.91 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1949.45 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 4138.46 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 3321.11 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 4116.12 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1275.78 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1245.23 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 4062.95 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1014.24 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 4042.73 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1200.14 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2222.65 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 5228.61 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 4217.83 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 5213.6 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1547.09 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1534.17 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 5197.91 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1394.87 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 5156.77 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1508.68 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1000.58 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 941.08 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 966.58 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1096.04 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 564.82 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 616.91 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 635.69 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 647.67 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 14359.67 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 8124.61 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 7598.98 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 8992.07 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 31883.7 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 2176.9 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 23249.57 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1656.07 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 10217.6 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 42488.2 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 6501.94 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 13713.52 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.44 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.33 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.45 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.91 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75.68 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.12 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.02 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 80.73 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 79.53 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.2 | 127.97 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 339.43 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 274.76 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 332.19 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.16 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 93.59 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 346.4 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 105.82 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 323.43 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.31 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.2 | 127.3 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 335.03 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 274.55 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 334.34 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 93.93 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 95.18 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 333.73 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.73 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 328.8 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 92.13 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.21 | 135.48 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 364.28 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 297.7 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 363.33 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 101.62 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.14 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 370.9 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.72 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 367.51 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.17 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 3.11 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.93 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 3.01 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.41 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.76 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.92 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.98 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.01 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.58 | 673.47 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 366.67 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.29 | 340.04 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 410.59 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.87 | 1009.67 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.1 | 110.24 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 564.22 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.06 | 72.22 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 391.74 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.68 | 1912.65 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.15 | 172.14 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.48 | 551.63 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.34 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 57901.2397 | 74.0961 | 301.8266 | 0 | 0.0009 | 102948.8164 | 22815.7214
February | 49877.9699 | 63.7378 | 258.7295 | 0 | 0.0007 | 88248.5596 | 19642.4671
March | 57588.3349 | 74.1411 | 306.4345 | 0 | 0.0009 | 104522.6243 | 22749.8433
April | 60942.2493 | 78.8682 | 330.0107 | 0 | 0.0009 | 112566.1777 | 24127.514
May | 68465.8587 | 88.8504 | 374.1917 | 0 | 0.0011 | 127637.3545 | 27137.8258
June | 71175.5065 | 92.535 | 391.3571 | 0 | 0.0011 | 133493.2545 | 28233.5341
July | 77546.1103 | 100.917 | 427.7806 | 0 | 0.0012 | 145917.8814 | 30773.4299
August | 75943.5805 | 98.8032 | 418.5433 | 0 | 0.0012 | 142766.874 | 30133.8277
September | 69439.1144 | 90.2365 | 381.234 | 0 | 0.0011 | 130040.0723 | 27539.4544
October | 65267.2216 | 84.5912 | 355.1935 | 0 | 0.001 | 121156.5523 | 25856.0249
November | 58105.6978 | 74.9737 | 311.5195 | 0 | 0.0009 | 106257.8491 | 22975.6865
December | 55770.4513 | 71.3709 | 290.741 | 0 | 0.0008 | 99167.6821 | 21976.294
Annual Sum or Average | 768023.3348 | 993.1211 | 4147.5618 | 0 | 0.0117 | 1414720 | 303961.6232
Minimum of Months | 49877.9699 | 63.7378 | 258.7295 | 0 | 0.0007 | 88248.5596 | 19642.4671
Maximum of Months | 77546.1103 | 100.917 | 427.7806 | 0 | 0.0012 | 145917.8814 | 30773.4299
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 227774000000 | 153994.348 | 22-JAN-20:00 | 57112.741 | 38807.225 | 9529.93 | 0 | 37809.673 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 195250000000 | 148411.323 | 20-FEB-20:45 | 57112.741 | 38807.225 | 9218.005 | 0 | 32538.574 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 231257000000 | 160171.811 | 26-MAR-19:15 | 57112.741 | 38807.225 | 9881.404 | 0 | 43635.661 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 249053000000 | 171270.016 | 30-APR-19:15 | 57112.741 | 38807.225 | 10414.752 | 0 | 54200.518 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 282398000000 | 183399.317 | 26-MAY-19:15 | 57185.041 | 38824.77 | 10909.581 | 0 | 65745.147 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 295354000000 | 180390.235 | 13-JUN-19:30 | 57185.041 | 38824.77 | 10821.847 | 0 | 62823.799 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 322844000000 | 189032.499 | 03-JUL-19:30 | 57185.041 | 38824.77 | 11188.545 | 0 | 71099.364 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 315872000000 | 195497.404 | 06-AUG-19:15 | 57112.741 | 38807.225 | 11544.528 | 0 | 77298.131 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 287714000000 | 181893.698 | 04-SEP-19:15 | 57112.741 | 38807.225 | 10811.199 | 0 | 64427.754 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 268059000000 | 172040.524 | 29-OCT-19:30 | 57112.741 | 38807.225 | 10386.387 | 0 | 54999.392 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 235096000000 | 161124.753 | 27-NOV-20:15 | 57185.041 | 38824.77 | 9766.815 | 0 | 44613.348 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 219409000000 | 160338.643 | 02-DEC-20:15 | 57040.442 | 38772.136 | 9754.987 | 0 | 44036.3 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 3130080000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 195250000000 | 148411.323 |  | 57040.442 | 38772.136 | 9218.005 | 0 | 32538.574 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 322844000000 | 195497.404 |  | 57185.041 | 38824.77 | 11544.528 | 0 | 77298.131 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 94229.24 | 6320.53 | 0 | 100549.77
Cost per Total Building Area ($/m2) | 18.45 | 1.24 | 0 | 19.69
Cost per Net Conditioned Building Area ($/m2) | 23.84 | 1.6 | 0 | 25.43

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3886.88 | 761.21 | 983.18
Net Site Energy | 3886.88 | 761.21 | 983.18
Total Source Energy | 10841.39 | 2123.18 | 2742.3
Net Source Energy | 10841.39 | 2123.18 | 2742.3
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 5.07 | 87.56 | 0 | 0 | 0 | 0
Cooling | 927.9 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.3 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 289.88 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 424.46 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 3185.38 | 701.5 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.363 | 1.712 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.261 | 0.279 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.261 | 0.279 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.261 | 0.279 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.261 | 0.279 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 72.38 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 111.83 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2477.77 | 1887.86 | 589.91 | 0.76 | 2.78
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2541.7 | 1943.45 | 598.25 | 0.76 | 2.77
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2787.51 | 2158.56 | 628.95 | 0.77 | 2.73
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2434.17 | 1918.59 | 515.58 | 0.79 | 2.81
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2291.99 | 1798.54 | 493.45 | 0.78 | 2.84
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4529.54 | 3617.54 | 912 | 0.8 | 2.44
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11060.75 | 8594.39 | 2466.37 | 0.78 | 2.43
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8851.18 | 6909.82 | 1941.36 | 0.78 | 2.43
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10878.83 | 8434.73 | 2444.1 | 0.78 | 2.43
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3109.15 | 2451.25 | 657.9 | 0.79 | 2.68
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2891.07 | 2308.97 | 582.1 | 0.8 | 2.73
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10189.92 | 8116.93 | 2072.99 | 0.8 | 2.44
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3073.32 | 2454.52 | 618.8 | 0.8 | 2.7
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9636 | 7649.52 | 1986.48 | 0.79 | 2.44
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2768.68 | 2211.22 | 557.46 | 0.8 | 2.76
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4524.12 | 3613.21 | 910.91 | 0.8 | 2.44
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11126.16 | 8651.63 | 2474.53 | 0.78 | 2.43
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8998.21 | 7039.21 | 1959.01 | 0.78 | 2.43
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11106.13 | 8634.07 | 2472.06 | 0.78 | 2.43
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3154.65 | 2491.35 | 663.3 | 0.79 | 2.67
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2954.32 | 2359.48 | 594.84 | 0.8 | 2.72
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9901.26 | 7888.62 | 2012.65 | 0.8 | 2.44
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2632.22 | 2102.23 | 529.98 | 0.8 | 2.78
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9793.32 | 7791.27 | 2002.05 | 0.8 | 2.44
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2818.5 | 2251.01 | 567.49 | 0.8 | 2.75
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4562.62 | 3643.96 | 918.66 | 0.8 | 2.44
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10682.67 | 8361.1 | 2321.57 | 0.78 | 2.43
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8658.48 | 6803.4 | 1855.08 | 0.79 | 2.43
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10698.51 | 8355.3 | 2343.21 | 0.78 | 2.43
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3037.01 | 2415.16 | 621.85 | 0.8 | 2.7
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3111.18 | 2484.76 | 626.42 | 0.8 | 2.69
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10370.69 | 8282.6 | 2088.08 | 0.8 | 2.44
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2710.62 | 2164.85 | 545.77 | 0.8 | 2.77
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10273.85 | 8205.26 | 2068.58 | 0.8 | 2.44
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2990.52 | 2388.39 | 602.13 | 0.8 | 2.71
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9878.64 | 7889.63 | 1989.01 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6172.44 | 4915.33 | 1257.11 | 0.8 | 4.03
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5908.41 | 4682.62 | 1225.79 | 0.79 | 4.01
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6306.4 | 5036.64 | 1269.76 | 0.8 | 4.04
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24745.87 | 16730.27 | 8015.6 | 0.68 | 3.44
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1806.64 | 1442.88 | 363.76 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13186.29 | 8915.03 | 4271.26 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1434.46 | 1076.42 | 358.05 | 0.75 | 3.87
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7524.25 | 5388.02 | 2136.23 | 0.72 | 3.77
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31327.07 | 24010.98 | 7316.09 | 0.77 | 3.68
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3866.4 | 2614 | 1252.39 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10299.43 | 7536.2 | 2763.23 | 0.73 | 3.82
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 838.23 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 818.54 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 843.1 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 918.72 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 958.01 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 977.94 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1211.06 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1197.13 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 977.1 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1699.23 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 3404.26 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2609.03 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 3322.91 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1088.39 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1056.55 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 3069.18 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 619.63 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 3203.58 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 995.76 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1732.41 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 3442 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2741.28 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 3415.4 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1107.68 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1082.31 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 3382.74 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 840.95 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 3361.87 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1029.97 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1876.52 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 4053.48 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 3248.91 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 4033.94 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1259.05 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1244.19 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 4035.29 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1082.72 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 3994.57 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1207.04 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 743.22 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 689.18 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 704.06 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 767.46 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 492.25 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 520.94 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 532.89 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 529.05 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 13970.72 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 8842.29 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 8410.84 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 9072.99 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 30917.37 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 2410.27 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 20757.76 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1834.06 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 9635.13 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 41142.59 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 5752.61 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 13342.43 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.7 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.64 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.72 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.96 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 85.76 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.69 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.11 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.94 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.79 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.27 | 174.18 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 400.29 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 323.7 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 391.79 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 116.22 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 111.17 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 389.61 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 118.18 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 365.69 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.46 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.27 | 173.97 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 403.33 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 330.61 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 402.39 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 118.36 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 113.6 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 378.74 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 101.22 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 373.43 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 108.38 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.28 | 175.45 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 392.93 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 321.26 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 391.61 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 115.7 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 119.64 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.63 | 398.79 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.23 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.62 | 395.06 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 115 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.4 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.22 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.27 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.48 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.59 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.68 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.72 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.71 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.6 | 692.2 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.37 | 429.77 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 407.11 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.38 | 441.89 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 1 | 1135.23 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.11 | 126.59 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.53 | 615.92 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 87.32 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 408.82 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.73 | 1967.11 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 180.6 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 590.27 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.34 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 46894.1641 | 75.7589 | 240.3047 | 0 | 0.0007 | 1774950 | 19586.6422
February | 42538.7619 | 68.7531 | 218.206 | 0 | 0.0006 | 1611720 | 17770.5661
March | 50492.1178 | 82.6616 | 266.6276 | 0 | 0.0007 | 1969430 | 21199.6567
April | 51379.5879 | 84.6157 | 274.94 | 0 | 0.0008 | 2030860 | 21622.9567
May | 56760.1438 | 93.9764 | 307.3458 | 0 | 0.0008 | 2270250 | 23937.8631
June | 63577.5924 | 105.765 | 347.8868 | 0 | 0.0009 | 2569740 | 26863.718
July | 70380.7365 | 117.3009 | 386.693 | 0 | 0.0011 | 2856400 | 29760.3727
August | 68559.6401 | 114.1863 | 376.1126 | 0 | 0.001 | 2778240 | 28982.2903
September | 62590.7617 | 104.0038 | 341.6219 | 0 | 0.0009 | 2523460 | 26434.6545
October | 55545.8404 | 91.7572 | 299.2614 | 0 | 0.0008 | 2210530 | 23404.6493
November | 48811.2394 | 79.9355 | 257.9374 | 0 | 0.0007 | 1905250 | 20496.5189
December | 47174.0799 | 76.1529 | 241.3176 | 0 | 0.0007 | 1782430 | 19697.6654
Annual Sum or Average | 664704.6659 | 1094.8673 | 3558.2547 | 0 | 0.0097 | 26283300 | 279757.5539
Minimum of Months | 42538.7619 | 68.7531 | 218.206 | 0 | 0.0006 | 1611720 | 17770.5661
Maximum of Months | 70380.7365 | 117.3009 | 386.693 | 0 | 0.0011 | 2856400 | 29760.3727
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 215113000000 | 139677.212 | 29-JAN-20:15 | 57112.741 | 38807.225 | 9385.615 | 0 | 23636.852 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 195332000000 | 139369.362 | 27-FEB-20:15 | 57185.041 | 38824.77 | 9305.327 | 0 | 23319.446 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 238684000000 | 160214.271 | 17-MAR-19:15 | 57185.041 | 38824.77 | 10520.034 | 0 | 42949.648 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 246128000000 | 160975.303 | 02-APR-19:15 | 57112.741 | 38807.225 | 10659.82 | 0 | 43660.738 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 275141000000 | 186286.582 | 28-MAY-19:30 | 57112.741 | 38807.225 | 12016.093 | 0 | 67615.744 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 311438000000 | 213626.387 | 27-JUN-19:45 | 57185.041 | 38824.77 | 13201.672 | 0 | 93680.125 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 346179000000 | 209665.091 | 11-JUL-19:45 | 57185.041 | 38824.77 | 13102.472 | 0 | 89818.029 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 336707000000 | 212790.005 | 01-AUG-19:30 | 57185.041 | 38824.77 | 13176.356 | 0 | 92869.06 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 305828000000 | 194752.812 | 09-SEP-19:15 | 57040.442 | 38772.136 | 12439.739 | 0 | 75765.716 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 267903000000 | 165755.802 | 02-OCT-19:30 | 57185.041 | 38824.77 | 10887.726 | 0 | 48123.486 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 230905000000 | 144276.252 | 05-NOV-19:15 | 57112.741 | 38807.225 | 9656.188 | 0 | 27965.318 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 216020000000 | 139906.237 | 13-DEC-20:45 | 57185.041 | 38824.77 | 9328.641 | 0 | 23833.007 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 3185380000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 195332000000 | 139369.362 |  | 57040.442 | 38772.136 | 9305.327 | 0 | 23319.446 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 346179000000 | 213626.387 |  | 57185.041 | 38824.77 | 13201.672 | 0 | 93680.125 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 75833.16 | 5987.94 | 0 | 81821.09
Cost per Total Building Area ($/m2) | 14.85 | 1.17 | 0 | 16.02
Cost per Net Conditioned Building Area ($/m2) | 19.18 | 1.51 | 0 | 20.7

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3807.15 | 745.59 | 963.01
Net Site Energy | 3807.15 | 745.59 | 963.01
Total Source Energy | 10654.94 | 2086.67 | 2695.14
Net Source Energy | 10654.94 | 2086.67 | 2695.14
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 33.7 | 210.47 | 0 | 0 | 0 | 0
Cooling | 609.63 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.57 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 253.69 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 547.36 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2859.83 | 947.31 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.409 | 0.454 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.409 | 0.454 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.409 | 0.454 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.409 | 0.454 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 4.092 | 0.255 | 0.129 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 4.092 | 0.255 | 0.129 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 4.092 | 0.255 | 0.129 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.255 | 0.129 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.255 | 0.129 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.255 | 0.129 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.255 | 0.129 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.255 | 0.129 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.255 | 0.129 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.255 | 0.129 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.255 | 0.129 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.255 | 0.129 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.255 | 0.129 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 4.092 | 0.255 | 0.129 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.255 | 0.129 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 4.092 | 0.255 | 0.129 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 4.09 | 0.255 | 0.129
North Total or Average |  |  | 72.38 | 4.09 | 0.255 | 0.129
Non-North Total or Average |  |  | 111.83 | 4.09 | 0.255 | 0.129
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2237.46 | 1686.16 | 551.3 | 0.75 | 2.82
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2289.31 | 1732.08 | 557.23 | 0.76 | 2.81
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2399.78 | 1830.23 | 569.55 | 0.76 | 2.8
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2289.08 | 1734.46 | 554.62 | 0.76 | 2.82
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2268.85 | 1718.98 | 549.88 | 0.76 | 2.82
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3350.9 | 2625.94 | 724.96 | 0.78 | 2.63
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9739.26 | 7497.71 | 2241.56 | 0.77 | 2.42
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7777.02 | 6019.18 | 1757.84 | 0.77 | 2.42
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9587.52 | 7362.03 | 2225.49 | 0.77 | 2.42
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2618.27 | 2038.78 | 579.5 | 0.78 | 2.77
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2433.45 | 1934.71 | 498.74 | 0.8 | 2.82
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9714.13 | 7496.51 | 2217.62 | 0.77 | 2.42
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2845.63 | 2246.44 | 599.19 | 0.79 | 2.73
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8784.89 | 6866.36 | 1918.53 | 0.78 | 2.43
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2396.7 | 1900.99 | 495.71 | 0.79 | 2.83
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3339.99 | 2616.12 | 723.87 | 0.78 | 2.63
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9785.45 | 7538.93 | 2246.52 | 0.77 | 2.42
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7889.33 | 6119.81 | 1769.52 | 0.78 | 2.43
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9772.95 | 7527.77 | 2245.18 | 0.77 | 2.42
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2652.42 | 2069.45 | 582.97 | 0.78 | 2.76
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2472.55 | 1970.62 | 501.93 | 0.8 | 2.81
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9011.02 | 7072.78 | 1938.24 | 0.78 | 2.43
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2355.31 | 1863.05 | 492.26 | 0.79 | 2.83
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8911 | 6981.43 | 1929.57 | 0.78 | 2.43
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2419.13 | 1921.57 | 497.57 | 0.79 | 2.82
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3504.73 | 2775.78 | 728.95 | 0.79 | 2.61
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10059.76 | 7924.21 | 2135.55 | 0.79 | 2.43
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8121.78 | 6431.01 | 1690.77 | 0.79 | 2.44
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10066.99 | 7920.03 | 2146.97 | 0.79 | 2.43
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2723.43 | 2167.82 | 555.61 | 0.8 | 2.76
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2787.77 | 2226.47 | 561.3 | 0.8 | 2.75
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9851.84 | 7843.06 | 2008.78 | 0.8 | 2.44
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2554.41 | 2040.1 | 514.32 | 0.8 | 2.8
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9784.25 | 7780.97 | 2003.28 | 0.8 | 2.44
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2717.41 | 2170.27 | 547.14 | 0.8 | 2.77
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9639.91 | 7698.96 | 1940.95 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5514.82 | 4289.77 | 1225.05 | 0.78 | 3.96
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5191.81 | 4013.87 | 1177.94 | 0.77 | 3.95
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6106.82 | 4839.43 | 1267.39 | 0.79 | 4.01
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21487.06 | 14527.04 | 6960.02 | 0.68 | 3.45
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1575.67 | 1258.42 | 317.25 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12222.88 | 8263.68 | 3959.19 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1275.14 | 923.53 | 351.61 | 0.72 | 3.79
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8068.47 | 5560.85 | 2507.63 | 0.69 | 3.69
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 31553.97 | 24102.93 | 7451.04 | 0.76 | 3.67
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3716.7 | 2512.8 | 1203.9 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10576.33 | 7382.8 | 3193.53 | 0.7 | 3.72
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1479.39 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1357.93 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1395.58 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1580.95 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 83.34 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1213.66 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1235.37 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1466.24 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1452.47 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1234.99 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 2135.02 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 4515.63 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 3497.47 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 4432.32 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1364.78 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1329.41 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 4170.19 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 853.13 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 4305.67 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1280.25 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 2185.92 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 4635.74 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 3701.49 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 4612.15 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1403.88 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1377.39 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 4572.77 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1152.56 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 4551.76 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1338.05 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2529.96 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 5986.77 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 4809.63 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 5970.4 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1740.38 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1735.04 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 5970.8 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1608.19 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 5928.1 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1707.26 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1358.41 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1216.16 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1241.99 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1413.81 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 776.36 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 776.02 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 794.07 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 812.68 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 14139.21 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 7995.53 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 7498.16 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 9067.3 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 33135.5 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 2108.22 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 25062 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1629.8 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 10484.56 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 42941.08 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 6943.5 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 13577.34 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.76 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.37 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.49 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 5.09 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.27 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75.5 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 77.96 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 83.25 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.22 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 77.51 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 123.6 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 345.16 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 278.97 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 337.81 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 95.21 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 92.66 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 346.17 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.68 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 322.15 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.79 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 123.06 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 347.39 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 284.44 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 346.78 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.88 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.65 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 333.54 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.68 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 328.5 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.93 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.21 | 132.33 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 375.32 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 306.51 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 374.55 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.97 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 107.2 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 376.2 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 98.23 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 372.76 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.49 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.37 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.91 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.99 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.55 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.5 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.5 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.55 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.61 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.58 | 675.47 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 364.57 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.29 | 338.52 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.36 | 420.7 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.87 | 1003.65 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.1 | 110.41 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 570.92 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.06 | 71.27 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 397.05 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.73 | 1966.01 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.15 | 173.61 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.46 | 538.29 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.34 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 47454.8387 | 84.8775 | 205.1249 | 0 | 0.0008 | 364816.3759 | 20284.807
February | 43094.0173 | 77.483 | 188.2613 | 0 | 0.0007 | 334828.5172 | 18458.1707
March | 46059.2998 | 84.0568 | 207.305 | 0 | 0.0008 | 368711.0237 | 19842.9932
April | 47135.8491 | 87.072 | 217.3004 | 0 | 0.0008 | 386499.2637 | 20403.8104
May | 52697.1015 | 98.461 | 248.4087 | 0 | 0.0009 | 441840.7229 | 22914.1851
June | 54784.5088 | 102.8636 | 260.7111 | 0 | 0.001 | 463727.4652 | 23868.2411
July | 59438.4657 | 111.894 | 284.2906 | 0 | 0.001 | 505671.1557 | 25922.8328
August | 58535.2478 | 110.1628 | 279.8195 | 0 | 0.001 | 497718.1782 | 25526.0686
September | 54540.5591 | 102.4308 | 259.6739 | 0 | 0.001 | 461882.8835 | 23764.2897
October | 49569.0562 | 92.1306 | 231.2816 | 0 | 0.0009 | 411372.2672 | 21509.1492
November | 44776.6986 | 81.8046 | 201.9665 | 0 | 0.0007 | 359216.911 | 19298.6122
December | 46648.9864 | 84.0087 | 204.448 | 0 | 0.0008 | 363618.3604 | 19993.2122
Annual Sum or Average | 604734.629 | 1117.2454 | 2788.5913 | 0 | 0.0103 | 4959900 | 261786.3722
Minimum of Months | 43094.0173 | 77.483 | 188.2613 | 0 | 0.0007 | 334828.5172 | 18458.1707
Maximum of Months | 59438.4657 | 111.894 | 284.2906 | 0 | 0.001 | 505671.1557 | 25922.8328
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 210350000000 | 137359.166 | 24-JAN-20:30 | 57185.041 | 38824.77 | 8582.489 | 0 | 22032.088 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 193059000000 | 139004.303 | 20-FEB-20:00 | 57112.741 | 38807.225 | 8865.154 | 0 | 23484.403 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 212595000000 | 145617.432 | 28-MAR-19:30 | 57185.041 | 38824.77 | 9314.937 | 0 | 29557.906 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 222852000000 | 156465.601 | 15-APR-19:15 | 57040.442 | 38772.136 | 9974.483 | 0 | 39943.762 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 254761000000 | 171288.337 | 14-MAY-19:30 | 57112.741 | 38807.225 | 10732.965 | 0 | 53900.627 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 267381000000 | 174137.407 | 19-JUN-19:00 | 57185.041 | 38824.77 | 10874.862 | 0 | 56517.956 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 291565000000 | 185946.626 | 02-JUL-19:00 | 57112.741 | 38807.225 | 11524.282 | 0 | 67767.598 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 286980000000 | 175791.64 | 14-AUG-19:30 | 57185.041 | 38824.77 | 10898.011 | 0 | 58149.04 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 266317000000 | 167152.049 | 10-SEP-19:15 | 57112.741 | 38807.225 | 10507.476 | 0 | 49989.828 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 237193000000 | 156158.593 | 21-OCT-19:15 | 57040.442 | 38772.136 | 9887.969 | 0 | 39723.268 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 207121000000 | 140507.653 | 22-NOV-20:00 | 57185.041 | 38824.77 | 8915.968 | 0 | 24847.096 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 209659000000 | 137640.085 | 04-DEC-20:00 | 57185.041 | 38824.77 | 8648.132 | 0 | 22247.364 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2859830000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 193059000000 | 137359.166 |  | 57040.442 | 38772.136 | 8582.489 | 0 | 22032.088 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 291565000000 | 185946.626 |  | 57185.041 | 38824.77 | 11524.282 | 0 | 67767.598 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 79669.8 | 10032.33 | 0 | 89702.13
Cost per Total Building Area ($/m2) | 15.6 | 1.96 | 0 | 17.57
Cost per Net Conditioned Building Area ($/m2) | 20.15 | 2.54 | 0 | 22.69

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3503.66 | 686.16 | 886.24
Net Site Energy | 3503.66 | 686.16 | 886.24
Total Source Energy | 9246.92 | 1810.92 | 2338.99
Net Source Energy | 9246.92 | 1810.92 | 2338.99
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.47 | 75.38 | 0 | 0 | 0 | 0
Cooling | 494.5 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.55 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 248.66 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 532.4 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2706.4 | 797.25 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 1.249 | 1.536 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.568 | 0.659 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.44 | 0.272 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.44 | 0.272 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.44 | 0.272 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.44 | 0.272 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.44 | 0.272 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.44 | 0.272 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.44 | 0.272 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.44 | 0.272 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.44 | 0.272 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.44 | 0.272 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.44 | 0.272 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.44 | 0.272 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.44 | 0.272 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.44 | 0.272 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.44 | 0.272 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.44 | 0.272 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.83 | 0.44 | 0.272
North Total or Average |  |  | 72.38 | 5.83 | 0.44 | 0.272
Non-North Total or Average |  |  | 111.83 | 5.83 | 0.44 | 0.272
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2207.88 | 1763.33 | 444.54 | 0.8 | 2.87
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2277.03 | 1818.56 | 458.47 | 0.8 | 2.85
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2381.47 | 1901.98 | 479.5 | 0.8 | 2.83
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1783.98 | 1424.79 | 359.2 | 0.8 | 2.9
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1849.41 | 1477.04 | 372.37 | 0.8 | 2.9
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3568.7 | 2850.16 | 718.54 | 0.8 | 2.6
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9719.77 | 7762.74 | 1957.02 | 0.8 | 2.44
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7972.89 | 6367.59 | 1605.3 | 0.8 | 2.44
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9521.88 | 7604.7 | 1917.18 | 0.8 | 2.44
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2616.89 | 2090 | 526.9 | 0.8 | 2.79
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2120.61 | 1693.64 | 426.97 | 0.8 | 2.89
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8269.76 | 6604.69 | 1665.07 | 0.8 | 2.44
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2553.47 | 2039.34 | 514.13 | 0.8 | 2.8
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7672.59 | 6127.76 | 1544.84 | 0.8 | 2.44
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2089.92 | 1669.12 | 420.79 | 0.8 | 2.89
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3514.46 | 2806.84 | 707.62 | 0.8 | 2.61
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9673.56 | 7725.84 | 1947.72 | 0.8 | 2.44
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8039.46 | 6420.76 | 1618.7 | 0.8 | 2.44
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9657.8 | 7713.25 | 1944.55 | 0.8 | 2.44
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2626.08 | 2097.33 | 528.75 | 0.8 | 2.79
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2148.03 | 1715.54 | 432.5 | 0.8 | 2.88
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7923.95 | 6328.5 | 1595.45 | 0.8 | 2.44
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2096.06 | 1674.03 | 422.03 | 0.8 | 2.89
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7804.25 | 6232.9 | 1571.34 | 0.8 | 2.44
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2097.05 | 1674.82 | 422.23 | 0.8 | 2.89
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3648.42 | 2913.83 | 734.59 | 0.8 | 2.59
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9667.83 | 7721.26 | 1946.57 | 0.8 | 2.44
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7946.79 | 6346.74 | 1600.04 | 0.8 | 2.44
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9657.95 | 7713.37 | 1944.58 | 0.8 | 2.44
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2610.94 | 2085.24 | 525.7 | 0.8 | 2.79
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2480.25 | 1980.86 | 499.39 | 0.8 | 2.81
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9087.17 | 7257.52 | 1829.65 | 0.8 | 2.44
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2364.76 | 1888.63 | 476.13 | 0.8 | 2.84
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9005.74 | 7192.48 | 1813.26 | 0.8 | 2.44
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2430.04 | 1940.77 | 489.28 | 0.8 | 2.82
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8993.17 | 7182.44 | 1810.73 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5148.18 | 4111.62 | 1036.56 | 0.8 | 4.04
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4725.57 | 3774.1 | 951.47 | 0.8 | 4.04
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5894.81 | 4707.92 | 1186.89 | 0.8 | 4.04
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 21278.78 | 14953.02 | 6325.76 | 0.7 | 3.51
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1703.09 | 1360.19 | 342.91 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12923.65 | 8737.46 | 4186.19 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1185.44 | 938.15 | 247.29 | 0.79 | 4.01
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6287.39 | 4684.44 | 1602.95 | 0.75 | 3.86
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27567.85 | 21883.81 | 5684.04 | 0.79 | 3.76
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3372.71 | 2280.23 | 1092.48 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8002.8 | 6005.19 | 1997.61 | 0.75 | 3.87
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 404.39 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 476.04 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 508.92 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 632.29 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 717.49 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 736.46 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 950.44 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 937.61 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 730.61 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1330.6 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 2687.58 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2032.62 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 2622.95 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 895.17 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 859.77 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2337.19 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 578.6 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 2482.21 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 789.53 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1376.24 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 2800.68 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2229.69 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 2782.07 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 930.56 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 902.16 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 2734.52 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 664.09 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 2718.09 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 842.93 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1636.5 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 3861.95 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 3103.29 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 3849.76 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1194.05 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1181.11 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 3842.25 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1034.62 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 3804.77 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1147.08 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 323.07 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 363.43 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 386.57 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 494.84 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 181.71 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 276.82 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 293.07 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 302.05 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 25899.1 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 7668.13 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 7083.37 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 8701.31 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 29114.04 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 2356.69 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 19373.4 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1749.51 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 8959.53 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 78114.54 | 0.78
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 5020.69 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 11356.12 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.26 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.48 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.58 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.97 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.9 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 87.56 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.58 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 68.6 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 71.12 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.22 | 137.23 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 373.76 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 306.58 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 366.15 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.63 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.54 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 318 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 98.19 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 295.04 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 80.36 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.21 | 135.14 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 371.98 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 309.14 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 371.37 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.98 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.6 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 304.7 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 80.6 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 300.1 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 80.64 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.22 | 140.29 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 371.76 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 305.58 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 371.38 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.4 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 95.37 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 349.43 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.93 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 346.3 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 93.44 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.01 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.13 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.2 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.54 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.57 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.86 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.91 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.94 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.54 | 630.15 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 360.73 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.29 | 331.12 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.36 | 413.05 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.95 | 1082.27 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.1 | 119.34 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 603.66 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.07 | 81.42 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 376.33 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.64 | 1872.21 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.14 | 157.54 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 487.13 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.34 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 22557.0733 | 19.5197 | 171.7356 | 0 | 0.0001 | 1036100 | 8330.9994
February | 20440.7884 | 17.6866 | 155.942 | 0 | 0.0001 | 940814.1084 | 7550.3642
March | 22501.7235 | 19.4585 | 173.6994 | 0 | 0.0001 | 1047950 | 8317.8343
April | 21925.1623 | 18.9474 | 171.4881 | 0 | 0.0001 | 1034620 | 8111.539
May | 23094.6635 | 19.941 | 183.6933 | 0 | 0.0001 | 1108270 | 8553.5429
June | 22551.3071 | 19.4608 | 181.3334 | 0 | 0.0001 | 1094040 | 8358.2864
July | 24452.9884 | 21.0853 | 199.5908 | 0 | 0.0001 | 1204200 | 9072.164
August | 24959.4364 | 21.5187 | 204.326 | 0 | 0.0001 | 1232780 | 9261.8934
September | 24077.6667 | 20.7608 | 196.6903 | 0 | 0.0001 | 1186710 | 8933.4153
October | 24107.6604 | 20.7988 | 194.7614 | 0 | 0.0001 | 1175060 | 8937.9112
November | 22526.6954 | 19.4584 | 177.7722 | 0 | 0.0001 | 1072540 | 8338.903
December | 22905.8374 | 19.8082 | 176.7683 | 0 | 0.0001 | 1066470 | 8467.0618
Annual Sum or Average | 276101.0029 | 238.4441 | 2187.8007 | 0 | 0.0011 | 13199600 | 102233.9148
Minimum of Months | 20440.7884 | 17.6866 | 155.942 | 0 | 0.0001 | 940814.1084 | 7550.3642
Maximum of Months | 24959.4364 | 21.5187 | 204.326 | 0 | 0.0001 | 1232780 | 9261.8934
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 212439000000 | 136712.763 | 26-JAN-20:30 | 57185.041 | 38824.77 | 8705.222 | 0 | 21262.952 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 192902000000 | 138018.643 | 12-FEB-20:30 | 57112.741 | 38807.225 | 8847.672 | 0 | 22516.226 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 214870000000 | 136288.15 | 04-MAR-20:00 | 57040.442 | 38772.136 | 8712.25 | 0 | 21028.545 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 212136000000 | 143421.737 | 11-APR-19:15 | 57185.041 | 38824.77 | 9094.56 | 0 | 27582.588 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 227237000000 | 147499.922 | 29-MAY-19:15 | 57112.741 | 38807.225 | 9579.787 | 0 | 31265.389 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 224319000000 | 145985.994 | 28-JUN-19:15 | 57185.041 | 38824.77 | 9400.439 | 0 | 29840.966 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 246907000000 | 149019.128 | 10-JUL-19:15 | 57185.041 | 38824.77 | 9630.99 | 0 | 32643.549 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 252765000000 | 150881.676 | 16-AUG-19:15 | 57185.041 | 38824.77 | 9740.604 | 0 | 34396.482 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 243319000000 | 150732.717 | 24-SEP-19:00 | 57112.741 | 38807.225 | 9749.548 | 0 | 34328.424 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 240931000000 | 145138.317 | 05-OCT-19:30 | 57185.041 | 38824.77 | 9350.801 | 0 | 29042.926 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 219911000000 | 139937.587 | 09-NOV-20:45 | 57185.041 | 38824.77 | 8939.348 | 0 | 24253.65 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 218666000000 | 136737.854 | 18-DEC-20:30 | 57185.041 | 38824.77 | 8709.436 | 0 | 21283.828 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2706400000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 192902000000 | 136288.15 |  | 57040.442 | 38772.136 | 8705.222 | 0 | 21028.545 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 252765000000 | 150881.676 |  | 57185.041 | 38824.77 | 9749.548 | 0 | 34396.482 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 92393.51 | 6709.58 | 0 | 99103.09
Cost per Total Building Area ($/m2) | 18.09 | 1.31 | 0 | 19.41
Cost per Net Conditioned Building Area ($/m2) | 23.37 | 1.7 | 0 | 25.07

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3730.96 | 730.67 | 943.74
Net Site Energy | 3730.96 | 730.67 | 943.74
Total Source Energy | 11315.98 | 2216.12 | 2862.35
Net Source Energy | 11315.98 | 2216.12 | 2862.35
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 8.58 | 147.51 | 0 | 0 | 0 | 0
Cooling | 675.86 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.38 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 267.14 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 479.78 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2914.19 | 816.77 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.908 | 1.051 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.273 | 0.292 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.273 | 0.292 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.273 | 0.292 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.273 | 0.292 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 5.835 | 0.251 | 0.11 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 5.835 | 0.251 | 0.11 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 5.835 | 0.251 | 0.11 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 72.38 | 5.83 | 0.251 | 0.11
Non-North Total or Average |  |  | 111.83 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2090.17 | 1659.55 | 430.62 | 0.79 | 2.89
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2147.23 | 1710.6 | 436.63 | 0.8 | 2.88
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2296.21 | 1833.88 | 462.33 | 0.8 | 2.85
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2108.56 | 1684.01 | 424.55 | 0.8 | 2.89
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2060.24 | 1645.42 | 414.82 | 0.8 | 2.9
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3836.35 | 3063.92 | 772.43 | 0.8 | 2.55
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10059.94 | 8034.42 | 2025.52 | 0.8 | 2.44
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8173.1 | 6527.49 | 1645.61 | 0.8 | 2.44
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9848.96 | 7865.92 | 1983.04 | 0.8 | 2.44
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2801.97 | 2237.81 | 564.16 | 0.8 | 2.75
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2701.39 | 2157.48 | 543.91 | 0.8 | 2.77
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9872.12 | 7884.42 | 1987.7 | 0.8 | 2.44
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3005.7 | 2400.52 | 605.18 | 0.8 | 2.71
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9213.26 | 7358.22 | 1855.04 | 0.8 | 2.44
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2614.67 | 2088.22 | 526.45 | 0.8 | 2.79
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3823.4 | 3053.58 | 769.82 | 0.8 | 2.55
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10173.09 | 8124.8 | 2048.3 | 0.8 | 2.44
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8369.97 | 6684.72 | 1685.25 | 0.8 | 2.44
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10153.16 | 8108.88 | 2044.29 | 0.8 | 2.44
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2867.42 | 2290.08 | 577.34 | 0.8 | 2.74
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2774.79 | 2216.1 | 558.69 | 0.8 | 2.76
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9589.77 | 7658.92 | 1930.85 | 0.8 | 2.44
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2550.58 | 2037.03 | 513.55 | 0.8 | 2.8
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9449.07 | 7546.55 | 1902.52 | 0.8 | 2.44
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2668.42 | 2131.15 | 537.27 | 0.8 | 2.78
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3872.38 | 3092.7 | 779.68 | 0.8 | 2.54
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9987.66 | 7976.69 | 2010.96 | 0.8 | 2.44
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8186.98 | 6538.57 | 1648.4 | 0.8 | 2.44
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9964.34 | 7958.07 | 2006.27 | 0.8 | 2.44
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2832.31 | 2262.04 | 570.27 | 0.8 | 2.75
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2946.92 | 2353.57 | 593.35 | 0.8 | 2.72
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10128.85 | 8089.46 | 2039.39 | 0.8 | 2.44
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2627.98 | 2098.85 | 529.13 | 0.8 | 2.79
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10031.94 | 8012.06 | 2019.88 | 0.8 | 2.44
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2840.84 | 2268.85 | 571.99 | 0.8 | 2.74
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9247.43 | 7385.51 | 1861.92 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5781.85 | 4617.7 | 1164.14 | 0.8 | 4.04
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5445.52 | 4349.1 | 1096.43 | 0.8 | 4.04
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5890.44 | 4704.43 | 1186.01 | 0.8 | 4.04
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 22980.24 | 15610.66 | 7369.58 | 0.68 | 3.45
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1612.27 | 1287.65 | 324.62 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12789.6 | 8646.83 | 4142.77 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1087.03 | 850.27 | 236.76 | 0.78 | 3.98
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6597.07 | 4989.68 | 1607.38 | 0.76 | 3.89
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 29226.05 | 23341.54 | 5884.51 | 0.8 | 3.73
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3728.06 | 2520.48 | 1207.58 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8606.95 | 6581.56 | 2025.39 | 0.76 | 3.92
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1075.79 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 986.08 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1012.29 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1117.32 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1092.29 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1113.41 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1342.84 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1327.79 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1112.72 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1814.06 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 3818.09 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2963.09 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 3736.37 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1186.99 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1153.75 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 3486.57 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 676.31 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 3622.88 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1100.11 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1844.53 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 3859.65 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 3099.55 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 3836.79 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1207.72 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1180.74 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 3802.22 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 945.37 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 3782 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1135.7 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2033.78 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 4623.53 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 3730.94 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 4607.81 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1397.97 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1384.15 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 4606.37 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1231.89 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 4565.65 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1356.87 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 964.29 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 852.7 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 869.14 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 957.5 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 588.74 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 580.95 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 592.85 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 598.46 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 12820.57 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 8214.39 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 7782.92 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 8353.74 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 30662.08 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 2068.78 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 21832.47 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1539.25 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 9723.9 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 41130.06 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 5980.07 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 12560.87 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.61 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.31 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.4 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.75 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 79.35 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.12 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.3 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.08 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 79.22 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.23 | 147.52 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 386.84 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 314.28 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 378.72 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 107.75 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.88 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 379.62 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 115.58 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 354.28 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.54 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.23 | 147.02 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 391.19 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 321.85 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 390.42 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 110.26 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.7 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 368.76 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 98.08 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 363.35 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 102.61 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.23 | 148.91 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 384.06 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 314.82 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 383.16 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 108.91 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 113.32 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 389.49 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 101.05 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 385.76 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 109.24 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 3.23 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.86 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.92 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 3.21 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.98 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.95 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.99 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 2.01 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.56 | 647.97 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 405.13 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.33 | 381.57 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.36 | 412.74 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.94 | 1068.1 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.1 | 112.97 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 597.4 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.06 | 72.76 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.35 | 409.06 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.77 | 1930.85 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.15 | 174.14 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.47 | 547.36 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.34 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 50823.0255 | 79.1134 | 310.1822 | 0 | 0.0006 | 1546820 | 21017.848
February | 46189.6534 | 72.5965 | 288.4417 | 0 | 0.0005 | 1438430 | 19174.0136
March | 50898.402 | 80.1439 | 319.2258 | 0 | 0.0006 | 1591950 | 21143.9369
April | 53667.5402 | 85.6504 | 347.3665 | 0 | 0.0007 | 1732330 | 22413.4075
May | 58245.3318 | 93.4133 | 381.2924 | 0 | 0.0007 | 1901540 | 24372.7545
June | 65297.7565 | 105.3255 | 433.1147 | 0 | 0.0008 | 2160000 | 27386.3728
July | 72205.3029 | 116.7111 | 481.2221 | 0 | 0.0009 | 2399930 | 30308.7748
August | 71232.8862 | 115.1022 | 474.3922 | 0 | 0.0009 | 2365860 | 29896.7343
September | 63251.5307 | 101.9381 | 418.7261 | 0 | 0.0008 | 2088240 | 26519.1444
October | 56832.1148 | 90.9896 | 370.5639 | 0 | 0.0007 | 1848030 | 23765.0598
November | 49965.2839 | 79.018 | 316.6001 | 0 | 0.0006 | 1578870 | 20791.9866
December | 50604.2324 | 79.1059 | 311.9773 | 0 | 0.0006 | 1555780 | 20961.9827
Annual Sum or Average | 689213.0604 | 1099.1079 | 4453.1051 | 0 | 0.0084 | 22207800 | 287752.016
Minimum of Months | 46189.6534 | 72.5965 | 288.4417 | 0 | 0.0005 | 1438430 | 19174.0136
Maximum of Months | 72205.3029 | 116.7111 | 481.2221 | 0 | 0.0009 | 2399930 | 30308.7748
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 202979000000 | 126992.927 | 18-JAN-20:00 | 57185.041 | 38824.77 | 8095.943 | 0 | 12152.394 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 188756000000 | 132651.312 | 26-FEB-20:00 | 57112.741 | 38807.225 | 8662.284 | 0 | 17334.283 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 208902000000 | 137547.881 | 31-MAR-19:00 | 57185.041 | 38824.77 | 9066.157 | 0 | 21737.135 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 227323000000 | 157075.906 | 21-APR-19:15 | 57185.041 | 38824.77 | 10172.976 | 0 | 40158.34 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 249527000000 | 165072.114 | 31-MAY-19:15 | 57185.041 | 38824.77 | 10612.109 | 0 | 47715.415 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 283444000000 | 196716.577 | 27-JUN-19:15 | 57185.041 | 38824.77 | 12323.441 | 0 | 77648.546 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 314928000000 | 193492.091 | 25-JUL-19:15 | 57185.041 | 38824.77 | 12026.011 | 0 | 74721.49 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 310458000000 | 189298.039 | 06-AUG-19:15 | 57112.741 | 38807.225 | 11996.208 | 0 | 70647.086 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 274027000000 | 173893.657 | 01-SEP-19:00 | 57185.041 | 38824.77 | 11211.52 | 0 | 55937.548 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 242506000000 | 153613.508 | 06-OCT-19:30 | 57185.041 | 38824.77 | 9987.394 | 0 | 36881.525 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 207186000000 | 135349.228 | 09-NOV-20:00 | 57185.041 | 38824.77 | 8873.043 | 0 | 19731.595 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 204156000000 | 130032.712 | 05-DEC-20:30 | 57185.041 | 38824.77 | 8390.586 | 0 | 14897.536 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2914190000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 188756000000 | 126992.927 |  | 57112.741 | 38807.225 | 8095.943 | 0 | 12152.394 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 314928000000 | 196716.577 |  | 57185.041 | 38824.77 | 12323.441 | 0 | 77648.546 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 76729.19 | 6587.01 | 0 | 83316.2
Cost per Total Building Area ($/m2) | 15.03 | 1.29 | 0 | 16.32
Cost per Net Conditioned Building Area ($/m2) | 19.41 | 1.67 | 0 | 21.07

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3476.76 | 680.89 | 879.44
Net Site Energy | 3476.76 | 680.89 | 879.44
Total Source Energy | 8786.76 | 1720.8 | 2222.59
Net Source Energy | 8786.76 | 1720.8 | 2222.59
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 2.8 | 197.71 | 0 | 0 | 0 | 0
Cooling | 310.87 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.2 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 215.23 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 598.24 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2491.33 | 985.43 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.738 | 0.83 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.5 | 0.569 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.5 | 0.569 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.5 | 0.569 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.5 | 0.569 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 4.092 | 0.392 | 0.253 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 4.092 | 0.392 | 0.253 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 4.092 | 0.392 | 0.253 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.392 | 0.253 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.392 | 0.253 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.392 | 0.253 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.392 | 0.253 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.392 | 0.253 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.392 | 0.253 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.392 | 0.253 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.392 | 0.253 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.392 | 0.253 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.392 | 0.253 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 4.092 | 0.392 | 0.253 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 72.38 | 4.09 | 0.392 | 0.253
Non-North Total or Average |  |  | 111.83 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1950.69 | 1557.93 | 392.76 | 0.8 | 2.9
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2017.18 | 1611.03 | 406.15 | 0.8 | 2.9
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1991.63 | 1590.63 | 401.01 | 0.8 | 2.9
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1361.88 | 1087.67 | 274.21 | 0.8 | 2.9
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1522.35 | 1215.83 | 306.52 | 0.8 | 2.9
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2948.42 | 2354.77 | 593.65 | 0.8 | 2.72
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9731.43 | 7772.06 | 1959.37 | 0.8 | 2.44
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8056 | 6433.96 | 1622.03 | 0.8 | 2.44
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9520.38 | 7603.5 | 1916.88 | 0.8 | 2.44
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2503.11 | 1999.12 | 503.99 | 0.8 | 2.81
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1911.55 | 1526.67 | 384.88 | 0.8 | 2.9
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7861.81 | 6278.87 | 1582.93 | 0.8 | 2.44
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2441.86 | 1950.2 | 491.65 | 0.8 | 2.82
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7239.97 | 5782.24 | 1457.73 | 0.8 | 2.44
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1919.8 | 1533.26 | 386.54 | 0.8 | 2.9
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2914.89 | 2327.99 | 586.9 | 0.8 | 2.73
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9795.18 | 7822.97 | 1972.21 | 0.8 | 2.44
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8231.38 | 6574.04 | 1657.35 | 0.8 | 2.44
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9779.46 | 7810.42 | 1969.04 | 0.8 | 2.44
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2553.69 | 2039.52 | 514.17 | 0.8 | 2.8
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1964.38 | 1568.86 | 395.52 | 0.8 | 2.9
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7569.73 | 6045.6 | 1524.12 | 0.8 | 2.44
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1995.11 | 1593.4 | 401.7 | 0.8 | 2.9
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7449.84 | 5949.85 | 1499.99 | 0.8 | 2.44
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1947.2 | 1555.14 | 392.06 | 0.8 | 2.9
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2989.49 | 2387.57 | 601.92 | 0.8 | 2.71
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9953.94 | 7949.77 | 2004.17 | 0.8 | 2.44
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8334.27 | 6656.21 | 1678.06 | 0.8 | 2.44
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9951.27 | 7947.63 | 2003.64 | 0.8 | 2.44
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2600.62 | 2077 | 523.62 | 0.8 | 2.79
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2185.75 | 1745.66 | 440.09 | 0.8 | 2.87
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8289.93 | 6620.79 | 1669.13 | 0.8 | 2.44
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2135.63 | 1705.63 | 430 | 0.8 | 2.88
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8213.53 | 6559.78 | 1653.75 | 0.8 | 2.44
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2168.97 | 1732.26 | 436.71 | 0.8 | 2.88
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7230.52 | 5774.7 | 1455.83 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4610.99 | 3682.59 | 928.4 | 0.8 | 4.04
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4257.48 | 3400.26 | 857.22 | 0.8 | 4.04
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5022.33 | 4011.11 | 1011.22 | 0.8 | 4.04
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16174.87 | 12334.32 | 3840.55 | 0.76 | 3.89
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1414.48 | 1129.68 | 284.8 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9600.19 | 7104.5 | 2495.69 | 0.74 | 3.84
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 886.33 | 707.87 | 178.46 | 0.8 | 4.04
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5128.25 | 4056.12 | 1072.13 | 0.79 | 4.01
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26090.24 | 20837.11 | 5253.13 | 0.8 | 3.77
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2180.21 | 1653.72 | 526.5 | 0.76 | 3.9
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5735.44 | 4554.03 | 1181.4 | 0.79 | 4.02
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 558.62 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 584.19 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 623.2 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 769.21 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 776.61 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 795.66 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1003.43 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 995.48 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 793.77 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1353.25 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 2860.14 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2167.73 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 2805.95 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 932.09 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 897.78 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 2558.17 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 639.54 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 2668.52 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 831.16 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1397.9 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 2982.41 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 2369.35 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 2970.45 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 969.24 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 942.16 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 2923.62 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 704.6 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 2911.51 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 888.98 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 1686.41 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 4120.18 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 3305.09 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 4113.5 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1253.18 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1243.45 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 4111.15 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1101.35 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 4075.48 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1216.86 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 465.74 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 466.28 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 492.47 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 625.87 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 218.25 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 299.16 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 315.97 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 331.74 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 20985.57 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 13354.24 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 6585.28 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 7647.02 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 29367.39 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1963.61 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 20443.53 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1405.93 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 8864.11 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 75695.22 | 0.78
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 5064.16 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 10014.36 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.73 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.81 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.93 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.39 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75.01 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 77.57 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.58 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.08 | 52.37 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 58.54 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 113.38 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 374.21 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 309.78 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 366.09 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.25 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 73.51 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 302.31 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 93.9 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 278.4 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 73.82 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 112.09 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 376.66 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 316.52 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 376.05 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 98.2 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75.54 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 291.08 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.72 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 286.47 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 74.88 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 114.96 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 382.76 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 320.48 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 382.66 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.05 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 318.77 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.12 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 315.84 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 83.4 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.44 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.45 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.53 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.94 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.68 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.93 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.98 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 1.03 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.44 | 506.64 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.28 | 323.09 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.26 | 298.32 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.3 | 351.91 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.88 | 1003.85 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 99.11 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 565.43 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.05 | 62.11 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.3 | 351.79 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.58 | 1795.5 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.12 | 136.09 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 396.81 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.34 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 22679.7795 | 19.6894 | 161.2996 | 0 | 0.0001 | 973089.3061 | 8341.6286
February | 20459.3796 | 17.7328 | 150.6953 | 0 | 0.0001 | 909137.911 | 7540.791
March | 22299.4115 | 19.3355 | 162.8314 | 0 | 0.0001 | 982348.5229 | 8214.6559
April | 21639.3561 | 18.7474 | 160.846 | 0 | 0.0001 | 970383.1105 | 7980.1524
May | 22436.9906 | 19.4211 | 169.8679 | 0 | 0.0001 | 1024830 | 8283.7406
June | 21761.4156 | 18.8226 | 167.2106 | 0 | 0.0001 | 1008800 | 8041.8154
July | 22901.917 | 19.7941 | 178.6507 | 0 | 0.0001 | 1077830 | 8471.4483
August | 22933.4077 | 19.8199 | 179.1543 | 0 | 0.0001 | 1080870 | 8483.8836
September | 22706.3457 | 19.6173 | 178.5152 | 0 | 0.0001 | 1077020 | 8403.3474
October | 23110.9604 | 19.9812 | 179.1372 | 0 | 0.0001 | 1080760 | 8545.2826
November | 21822.8828 | 18.8966 | 163.9613 | 0 | 0.0001 | 989185.1636 | 8053.176
December | 22512.7535 | 19.5348 | 161.8386 | 0 | 0.0001 | 976348.167 | 8285.4649
Annual Sum or Average | 267264.6001 | 231.3929 | 2014.008 | 0 | 0.001 | 12150600 | 98645.3865
Minimum of Months | 20459.3796 | 17.7328 | 150.6953 | 0 | 0.0001 | 909137.911 | 7540.791
Maximum of Months | 23110.9604 | 19.9812 | 179.1543 | 0 | 0.0001 | 1080870 | 8545.2826
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 199520000000 | 129185.074 | 15-JAN-20:30 | 57112.741 | 38807.225 | 7503.482 | 0 | 15026.847 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 186407000000 | 135610.097 | 15-FEB-20:30 | 57185.041 | 38824.77 | 8051.665 | 0 | 20813.843 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 201418000000 | 131664.504 | 30-MAR-19:00 | 57185.041 | 38824.77 | 7688.131 | 0 | 17231.784 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 198965000000 | 137689.026 | 29-APR-19:15 | 57040.442 | 38772.136 | 8284.594 | 0 | 22857.076 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 210128000000 | 139427.421 | 25-MAY-19:15 | 57185.041 | 38824.77 | 8343.343 | 0 | 24339.488 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 206843000000 | 140319.747 | 16-JUN-19:30 | 57185.041 | 38824.77 | 8476.121 | 0 | 25099.036 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 220996000000 | 159663.821 | 02-JUL-19:30 | 57112.741 | 38807.225 | 9651.881 | 0 | 43357.195 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 221620000000 | 140958.133 | 27-AUG-19:15 | 57112.741 | 38807.225 | 8518.305 | 0 | 25785.083 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 220830000000 | 151629.892 | 28-SEP-19:00 | 57185.041 | 38824.77 | 9107.564 | 0 | 35777.738 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 221597000000 | 139836.967 | 13-OCT-19:30 | 57185.041 | 38824.77 | 8418.117 | 0 | 24674.26 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 202820000000 | 133186.086 | 12-NOV-20:45 | 57112.741 | 38807.225 | 7851.87 | 0 | 18679.471 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 200188000000 | 128740.801 | 03-DEC-20:30 | 57112.741 | 38807.225 | 7408.469 | 0 | 14677.587 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2491330000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 186407000000 | 128740.801 |  | 57040.442 | 38772.136 | 7408.469 | 0 | 14677.587 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 221620000000 | 159663.821 |  | 57185.041 | 38824.77 | 9651.881 | 0 | 43357.195 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 100460.79 | 8297.39 | 0 | 108758.18
Cost per Total Building Area ($/m2) | 19.67 | 1.62 | 0 | 21.3
Cost per Net Conditioned Building Area ($/m2) | 25.41 | 2.1 | 0 | 27.51

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3905.27 | 764.81 | 987.83
Net Site Energy | 3905.27 | 764.81 | 987.83
Total Source Energy | 11087.98 | 2171.47 | 2804.68
Net Source Energy | 11087.98 | 2171.47 | 2804.68
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 56.96 | 360.99 | 0 | 0 | 0 | 0
Cooling | 494.55 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.37 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 232.83 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 607.86 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2746.95 | 1158.33 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.505 | 0.547 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.329 | 0.358 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.329 | 0.358 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.329 | 0.358 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.329 | 0.358 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 3.354 | 0.355 | 0.274 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 3.354 | 0.355 | 0.274 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 3.354 | 0.355 | 0.274 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.354 | 0.355 | 0.274 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.354 | 0.355 | 0.274 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.354 | 0.355 | 0.274 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.354 | 0.355 | 0.274 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.354 | 0.355 | 0.274 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.354 | 0.355 | 0.274 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.355 | 0.274 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.355 | 0.274 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.355 | 0.274 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.355 | 0.274 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 3.354 | 0.355 | 0.274 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.355 | 0.274 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.354 | 0.355 | 0.274 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.35 | 0.355 | 0.274
North Total or Average |  |  | 72.38 | 3.35 | 0.355 | 0.274
Non-North Total or Average |  |  | 111.83 | 3.35 | 0.355 | 0.274
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2157.58 | 1603.6 | 553.98 | 0.74 | 2.83
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2207.71 | 1647.45 | 560.26 | 0.75 | 2.82
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2276.48 | 1707.75 | 568.73 | 0.75 | 2.81
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2176.64 | 1620.31 | 556.33 | 0.74 | 2.83
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2198.59 | 1639.53 | 559.06 | 0.75 | 2.82
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3049.84 | 2338.51 | 711.33 | 0.77 | 2.68
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9515.43 | 7253.39 | 2262.04 | 0.76 | 2.42
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7620.84 | 5834.59 | 1786.25 | 0.77 | 2.42
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9385.31 | 7127.26 | 2258.05 | 0.76 | 2.41
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2521.37 | 1939.82 | 581.55 | 0.77 | 2.78
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2468.42 | 1892.76 | 575.66 | 0.77 | 2.79
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9551.39 | 7274.22 | 2277.17 | 0.76 | 2.42
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2800.4 | 2182.36 | 618.04 | 0.78 | 2.74
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9054.42 | 6835.19 | 2219.23 | 0.75 | 2.41
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2429.65 | 1858.35 | 571.3 | 0.76 | 2.79
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3037.97 | 2328 | 709.97 | 0.77 | 2.68
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9587.22 | 7305.91 | 2281.31 | 0.76 | 2.42
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7736.09 | 5936.85 | 1799.24 | 0.77 | 2.42
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9574.62 | 7294.76 | 2279.86 | 0.76 | 2.42
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2564.58 | 1975.31 | 589.26 | 0.77 | 2.77
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2508.85 | 1928.67 | 580.17 | 0.77 | 2.78
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9296.73 | 7049.03 | 2247.7 | 0.76 | 2.41
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2418.79 | 1848.71 | 570.07 | 0.76 | 2.8
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9193.51 | 6957.88 | 2235.63 | 0.76 | 2.41
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2451.52 | 1877.75 | 573.77 | 0.77 | 2.79
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3119.39 | 2411.93 | 707.46 | 0.77 | 2.67
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9631.06 | 7453.86 | 2177.2 | 0.77 | 2.42
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7786.61 | 6060.9 | 1725.72 | 0.78 | 2.43
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9624.34 | 7447.82 | 2176.52 | 0.77 | 2.42
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2577.56 | 2015.78 | 561.79 | 0.78 | 2.78
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2548.61 | 2022.9 | 525.71 | 0.79 | 2.8
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9461.38 | 7352.49 | 2108.89 | 0.78 | 2.43
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2398.24 | 1881.24 | 517 | 0.78 | 2.82
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9395.06 | 7292.85 | 2102.21 | 0.78 | 2.43
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2491.57 | 1970.88 | 520.69 | 0.79 | 2.81
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9145.46 | 7284.76 | 1860.69 | 0.8 | 4.03
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5407.06 | 4143.5 | 1263.56 | 0.77 | 3.93
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5096.92 | 3876.08 | 1220.84 | 0.76 | 3.91
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5622.08 | 4351.66 | 1270.42 | 0.77 | 3.95
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20197.08 | 13654.91 | 6542.17 | 0.68 | 3.45
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1489.58 | 1177.93 | 311.65 | 0.79 | 4.01
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11588.32 | 7834.67 | 3753.65 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1211.63 | 858.9 | 352.74 | 0.71 | 3.75
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8043.98 | 5460.69 | 2583.29 | 0.68 | 3.66
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30832.15 | 23411.21 | 7420.94 | 0.76 | 3.66
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3462.55 | 2340.97 | 1121.58 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10344.72 | 7094.25 | 3250.47 | 0.69 | 3.68
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1695.41 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1513.53 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1551.18 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1730.4 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 71.94 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1308.78 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1330.11 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1551.42 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1543.06 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1333.85 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 2215.81 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 4802.85 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 3719.24 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 4730.61 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1428.62 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1392.98 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 4470.96 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 927.93 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 4608.16 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1349.24 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 2260.81 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 4915.16 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 3912.33 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 4897.81 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1465.38 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1436.91 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 4855.85 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1219.98 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 4837.61 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1403.72 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2586.72 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 6181.57 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 4952.2 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 6170.63 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1781.58 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1774.33 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 6167.9 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1652.49 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 6127.05 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1753.9 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1568.09 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1371.75 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1399.27 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1562.28 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 835.15 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 804.03 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 821.96 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 842.56 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 14009.67 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 8019.32 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 7516.85 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 8453.24 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 34907.76 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 2013.59 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 27201.59 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1578.95 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 10879.68 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 43540.18 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 7424.37 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 13753.77 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.28 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.72 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.83 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.39 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.22 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 70.46 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 72.79 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75.99 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 71.35 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 72.37 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 107.1 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 329.69 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 266.71 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 322.37 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 89.23 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 86.69 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 330.25 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 102.02 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 306.74 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.84 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.54 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 331.95 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 272.21 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 331.35 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.99 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.63 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 318.18 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.32 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 313.3 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 85.88 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 111.65 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 345.45 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 282.9 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 345.12 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.64 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.69 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 342.5 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.65 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 339.25 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 93.82 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.89 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.27 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.36 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.87 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.6 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.51 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.56 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.63 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 637.14 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.3 | 345.54 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.28 | 320.05 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 367.55 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.81 | 943.39 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 102.14 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.47 | 541.28 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.06 | 64.17 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.33 | 379.98 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.66 | 1894.77 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.14 | 161.73 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 502.32 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.34 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 44899.377 | 80.3894 | 219.0319 | 0 | 0.0009 | 13619.9967 | 19163.7968
February | 38618.7745 | 69.2961 | 189.2307 | 0 | 0.0008 | 11766.9329 | 16496.9986
March | 40385.5438 | 73.8825 | 205.7075 | 0 | 0.0008 | 12792.0232 | 17381.214
April | 38857.9877 | 72.3971 | 205.1551 | 0 | 0.0008 | 12758.1227 | 16843.4817
May | 42965.5446 | 81.6424 | 235.6346 | 0 | 0.001 | 14654.1061 | 18769.569
June | 46423.1471 | 89.3609 | 260.938 | 0 | 0.0011 | 16228.0931 | 20385.0348
July | 50654.8318 | 97.9324 | 287.0746 | 0 | 0.0012 | 17853.699 | 22282.156
August | 50657.6416 | 97.9758 | 287.3006 | 0 | 0.0012 | 17867.7686 | 22286.8715
September | 44079.4061 | 84.7214 | 247.0574 | 0 | 0.001 | 15364.7992 | 19344.1623
October | 42476.6979 | 80.3564 | 230.9819 | 0 | 0.0009 | 14364.6378 | 18523.3631
November | 39787.9292 | 73.7775 | 208.1204 | 0 | 0.0008 | 12942.4082 | 17214.3763
December | 42303.9924 | 76.3064 | 209.4841 | 0 | 0.0009 | 13026.4939 | 18107.5989
Annual Sum or Average | 522110.8737 | 978.0383 | 2785.7167 | 0 | 0.0113 | 173239.0815 | 226798.6232
Minimum of Months | 38618.7745 | 69.2961 | 189.2307 | 0 | 0.0008 | 11766.9329 | 16496.9986
Maximum of Months | 50657.6416 | 97.9758 | 287.3006 | 0 | 0.0012 | 17867.7686 | 22286.8715
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 215964000000 | 135741.066 | 31-JAN-07:15 | 37896.934 | 51279.599 | 7080.68 | 28749.074 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 186581000000 | 124785.602 | 15-FEB-20:45 | 57185.041 | 38824.77 | 7292.472 | 0 | 10748.541 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 202835000000 | 142574.938 | 09-MAR-20:00 | 57185.041 | 38824.77 | 8566.463 | 0 | 27263.886 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 202298000000 | 144051.121 | 04-APR-19:30 | 57185.041 | 38824.77 | 8730.695 | 0 | 28575.836 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 232361000000 | 156854.291 | 15-MAY-19:15 | 57185.041 | 38824.77 | 9414.507 | 0 | 40695.194 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 257319000000 | 175826.241 | 30-JUN-19:45 | 57185.041 | 38824.77 | 10355.114 | 0 | 58726.537 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 283095000000 | 185650.205 | 24-JUL-19:30 | 57185.041 | 38824.77 | 10785.208 | 0 | 68120.408 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 283319000000 | 185068.117 | 17-AUG-19:15 | 57185.041 | 38824.77 | 10744.562 | 0 | 67578.965 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 243630000000 | 159290.065 | 09-SEP-19:15 | 57040.442 | 38772.136 | 9621.672 | 0 | 43121.037 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 227772000000 | 154039.855 | 20-OCT-19:30 | 57185.041 | 38824.77 | 9226.47 | 0 | 38068.796 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 205220000000 | 148421.224 | 04-NOV-19:30 | 57040.442 | 38772.136 | 9013.038 | 0 | 32860.831 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 206553000000 | 126966.631 | 21-DEC-07:15 | 37896.934 | 51279.599 | 6732.01 | 20323.309 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2746950000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 186581000000 | 124785.602 |  | 37896.934 | 38772.136 | 6732.01 | 0 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 283319000000 | 185650.205 |  | 57185.041 | 51279.599 | 10785.208 | 28749.074 | 68120.408 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 52737.13 | 11578.43 | 0 | 64315.55
Cost per Total Building Area ($/m2) | 10.33 | 2.27 | 0 | 12.6
Cost per Net Conditioned Building Area ($/m2) | 13.34 | 2.93 | 0 | 16.27

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3726.02 | 729.7 | 942.49
Net Site Energy | 3726.02 | 729.7 | 942.49
Total Source Energy | 10074.06 | 1972.9 | 2548.21
Net Source Energy | 10074.06 | 1972.9 | 2548.21
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 24.26 | 242.39 | 0 | 0 | 0 | 0
Cooling | 450.96 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.34 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 259.98 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 596.38 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2697.78 | 1028.24 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.568 | 0.621 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.335 | 0.365 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.335 | 0.365 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.335 | 0.365 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.335 | 0.365 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 4.092 | 0.362 | 0.225 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 4.092 | 0.362 | 0.225 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 4.092 | 0.362 | 0.225 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.362 | 0.225 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.362 | 0.225 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.362 | 0.225 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.362 | 0.225 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.362 | 0.225 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.362 | 0.225 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.362 | 0.225 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.362 | 0.225 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.362 | 0.225 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.362 | 0.225 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 4.092 | 0.362 | 0.225 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.362 | 0.225 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 4.092 | 0.362 | 0.225 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 4.09 | 0.362 | 0.225
North Total or Average |  |  | 72.38 | 4.09 | 0.362 | 0.225
Non-North Total or Average |  |  | 111.83 | 4.09 | 0.362 | 0.225
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1980.81 | 1581.98 | 398.83 | 0.8 | 2.9
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2046.45 | 1634.4 | 412.04 | 0.8 | 2.9
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2044.2 | 1632.61 | 411.59 | 0.8 | 2.9
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1897.74 | 1515.64 | 382.1 | 0.8 | 2.9
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2055.43 | 1641.58 | 413.85 | 0.8 | 2.9
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3151.97 | 2517.34 | 634.63 | 0.8 | 2.68
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9811.39 | 7835.92 | 1975.47 | 0.8 | 2.44
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7947.46 | 6347.28 | 1600.18 | 0.8 | 2.44
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9599.9 | 7667.01 | 1932.89 | 0.8 | 2.44
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2550.41 | 2036.9 | 513.51 | 0.8 | 2.8
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2460.85 | 1965.37 | 495.48 | 0.8 | 2.82
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9922.72 | 7924.84 | 1997.89 | 0.8 | 2.44
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3075.14 | 2455.97 | 619.16 | 0.8 | 2.7
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9171.64 | 7324.98 | 1846.66 | 0.8 | 2.44
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2458.05 | 1963.14 | 494.92 | 0.8 | 2.82
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3131.82 | 2501.24 | 630.58 | 0.8 | 2.69
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9901.34 | 7907.76 | 1993.58 | 0.8 | 2.44
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8118.31 | 6483.73 | 1634.58 | 0.8 | 2.44
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9881.7 | 7892.07 | 1989.63 | 0.8 | 2.44
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2603.65 | 2079.42 | 524.23 | 0.8 | 2.79
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2518.66 | 2011.54 | 507.12 | 0.8 | 2.81
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9535.05 | 7615.22 | 1919.83 | 0.8 | 2.44
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2517.45 | 2010.58 | 506.88 | 0.8 | 2.81
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9384.15 | 7494.7 | 1889.45 | 0.8 | 2.44
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2482.26 | 1982.47 | 499.79 | 0.8 | 2.81
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3233.34 | 2582.33 | 651.02 | 0.8 | 2.67
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10063.14 | 8036.98 | 2026.16 | 0.8 | 2.44
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8229.53 | 6572.56 | 1656.97 | 0.8 | 2.44
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10042.95 | 8020.85 | 2022.09 | 0.8 | 2.44
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2656.93 | 2121.97 | 534.96 | 0.8 | 2.78
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2730.29 | 2180.56 | 549.73 | 0.8 | 2.77
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10140.5 | 8098.77 | 2041.74 | 0.8 | 2.44
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2607.33 | 2082.36 | 524.97 | 0.8 | 2.79
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10040.66 | 8019.02 | 2021.63 | 0.8 | 2.44
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2681.26 | 2141.4 | 539.86 | 0.8 | 2.77
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9868.37 | 7881.43 | 1986.95 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5578.69 | 4455.45 | 1123.24 | 0.8 | 4.04
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5131.12 | 4098 | 1033.12 | 0.8 | 4.04
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5686.48 | 4541.54 | 1144.94 | 0.8 | 4.04
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17308.7 | 12937.53 | 4371.17 | 0.75 | 3.85
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1536.83 | 1227.4 | 309.43 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11790.89 | 8305.95 | 3484.94 | 0.7 | 3.73
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 890.76 | 711.41 | 179.35 | 0.8 | 4.04
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6330.19 | 5055.64 | 1274.55 | 0.8 | 4.04
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 32413.72 | 25887.39 | 6526.33 | 0.8 | 3.73
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3135.91 | 2295.74 | 840.17 | 0.73 | 3.82
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7724.21 | 6168.98 | 1555.23 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1311.49 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1181.64 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1217.17 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1391.71 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 45.49 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1148.64 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1170.39 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1394.1 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1380.42 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1169.52 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1907.59 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 4108.26 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 3189.96 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 4030.74 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1255.27 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1217.87 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 3758.49 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 740.3 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 3898.61 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1166.89 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1947.48 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 4200.59 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 3370.17 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 4181.74 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1287.69 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1257.84 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 4133.14 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1030.33 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 4114.05 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1216.68 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2259.69 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 5420.64 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 4372.07 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 5408.67 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1592.14 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1582.86 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 5399.32 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1449.9 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 5358.28 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1560.36 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1191.81 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1047 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1071.41 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1225.84 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 666.03 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 651.52 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 667.02 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 685 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 12396.71 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 7308.84 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 6797.61 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 7431.98 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 29664.31 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1755.63 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 22833.96 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1260.98 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 9858.71 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 41298.23 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 6217.79 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 11809.5 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.94 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.45 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.59 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.24 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.17 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.17 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.69 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.61 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 72.97 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 79.04 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 121.2 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 377.28 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 305.61 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 369.15 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 98.07 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.63 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 381.56 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 118.25 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 352.68 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.52 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.19 | 120.43 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 380.74 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 312.18 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 379.98 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.12 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.85 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 366.65 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.8 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 360.85 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 95.45 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.2 | 124.33 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 386.96 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 316.45 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 386.18 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 102.17 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.99 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 389.94 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.26 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 386.1 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.1 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.49 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.94 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 4.04 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.62 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.51 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.45 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.51 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.58 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.6 | 691.48 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 390.9 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 359.54 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.34 | 398.45 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.9 | 1025.29 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 107.69 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.53 | 614.46 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.05 | 62.42 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.38 | 443.56 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.96 | 2141.44 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.16 | 179.94 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.47 | 541.23 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.34 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 60606.1411 | 100.7104 | 247.5982 | 0 | 0.001 | 257428.4037 | 25458.3454
February | 54274.2082 | 90.5011 | 223.4216 | 0 | 0.0009 | 232294.1336 | 22829.1972
March | 59617.3993 | 99.8644 | 247.8727 | 0 | 0.001 | 257719.4349 | 25121.1911
April | 59466.538 | 100.6686 | 252.9655 | 0 | 0.001 | 263021.9746 | 25161.286
May | 65849.9788 | 112.4443 | 285.3674 | 0 | 0.0011 | 296718.5819 | 27957.3216
June | 68263.4989 | 117.1414 | 298.9431 | 0 | 0.0012 | 310838.1285 | 29038.4865
July | 75313.8207 | 129.5873 | 331.6986 | 0 | 0.0013 | 344899.2697 | 32071.6873
August | 73547.6583 | 126.5143 | 323.7358 | 0 | 0.0013 | 336619.4017 | 31316.2457
September | 67536.3858 | 115.9402 | 296.011 | 0 | 0.0012 | 307789.6911 | 28733.7505
October | 63297.9559 | 107.7178 | 272.3123 | 0 | 0.0011 | 283141.6809 | 26837.6653
November | 58204.2298 | 97.7958 | 243.613 | 0 | 0.001 | 253292.6121 | 24555.0032
December | 60885.2882 | 101.2481 | 249.1379 | 0 | 0.001 | 259029.7348 | 25582.8402
Annual Sum or Average | 766863.1028 | 1300.1337 | 3272.677 | 0 | 0.0129 | 3402790 | 324663.0201
Minimum of Months | 54274.2082 | 90.5011 | 223.4216 | 0 | 0.0009 | 232294.1336 | 22829.1972
Maximum of Months | 75313.8207 | 129.5873 | 331.6986 | 0 | 0.0013 | 344899.2697 | 32071.6873
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 204092000000 | 127925.238 | 26-JAN-20:30 | 57185.041 | 38824.77 | 8406.326 | 0 | 12774.323 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 184166000000 | 131471.522 | 14-FEB-20:30 | 57185.041 | 38824.77 | 8771.787 | 0 | 15955.146 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 204323000000 | 134879.817 | 20-MAR-19:15 | 57185.041 | 38824.77 | 9087.343 | 0 | 19047.885 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 208527000000 | 145774.296 | 22-APR-19:15 | 57040.442 | 38772.136 | 9881.604 | 0 | 29345.336 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 235242000000 | 153070.837 | 30-MAY-19:15 | 57185.041 | 38824.77 | 10276.669 | 0 | 36049.579 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 246436000000 | 160121.669 | 28-JUN-19:30 | 57185.041 | 38824.77 | 10679.597 | 0 | 42697.483 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 273440000000 | 170140.014 | 30-JUL-19:15 | 57112.741 | 38807.225 | 11319.384 | 0 | 52165.884 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 266876000000 | 168346.638 | 01-AUG-19:15 | 57185.041 | 38824.77 | 11204.866 | 0 | 50397.182 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 244019000000 | 155898.086 | 02-SEP-19:15 | 57040.442 | 38772.136 | 10540.591 | 0 | 38810.139 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 224478000000 | 145554.57 | 01-OCT-19:15 | 57112.741 | 38807.225 | 10009.852 | 0 | 28889.973 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 200813000000 | 134817.538 | 09-NOV-20:00 | 57185.041 | 38824.77 | 9060.371 | 0 | 19012.577 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 205362000000 | 126497.938 | 08-DEC-20:00 | 57185.041 | 38824.77 | 8266.315 | 0 | 11487.034 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2697780000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 184166000000 | 126497.938 |  | 57040.442 | 38772.136 | 8266.315 | 0 | 11487.034 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 273440000000 | 170140.014 |  | 57185.041 | 38824.77 | 11319.384 | 0 | 52165.884 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 27865.59 | 7352.32 | 0 | 35217.91
Cost per Total Building Area ($/m2) | 5.46 | 1.44 | 0 | 6.9
Cost per Net Conditioned Building Area ($/m2) | 7.05 | 1.86 | 0 | 8.91

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3618.07 | 708.56 | 915.18
Net Site Energy | 3618.07 | 708.56 | 915.18
Total Source Energy | 5552.75 | 1087.45 | 1404.56
Net Source Energy | 5552.75 | 1087.45 | 1404.56
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 22.31 | 324.92 | 0 | 0 | 0 | 0
Cooling | 261.49 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.1 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 218.21 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 639.32 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2464.34 | 1153.72 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.522 | 0.567 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.363 | 0.399 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.363 | 0.399 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.363 | 0.399 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.363 | 0.399 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 4.092 | 0.392 | 0.253 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 4.092 | 0.392 | 0.253 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 4.092 | 0.392 | 0.253 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.392 | 0.253 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.392 | 0.253 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.392 | 0.253 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.392 | 0.253 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.392 | 0.253 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 4.092 | 0.392 | 0.253 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.392 | 0.253 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.392 | 0.253 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.392 | 0.253 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 4.092 | 0.392 | 0.253 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 4.092 | 0.392 | 0.253 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 4.092 | 0.392 | 0.253 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 4.092 | 0.392 | 0.253 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 72.38 | 4.09 | 0.392 | 0.253
Non-North Total or Average |  |  | 111.83 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1939.56 | 1549.04 | 390.52 | 0.8 | 2.9
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2008.97 | 1604.47 | 404.5 | 0.8 | 2.9
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2012.35 | 1607.17 | 405.18 | 0.8 | 2.9
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1551.32 | 1238.97 | 312.35 | 0.8 | 2.9
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1667.88 | 1332.06 | 335.82 | 0.8 | 2.9
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2770.1 | 2212.35 | 557.74 | 0.8 | 2.76
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9588.88 | 7658.21 | 1930.67 | 0.8 | 2.44
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7942.09 | 6342.99 | 1599.1 | 0.8 | 2.44
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9372.19 | 7485.14 | 1887.04 | 0.8 | 2.44
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2500.86 | 1997.32 | 503.53 | 0.8 | 2.81
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2071.56 | 1654.47 | 417.1 | 0.8 | 2.9
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8263.84 | 6599.96 | 1663.88 | 0.8 | 2.44
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2561.92 | 2046.09 | 515.83 | 0.8 | 2.8
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7637.82 | 6099.99 | 1537.84 | 0.8 | 2.44
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2057.98 | 1643.62 | 414.36 | 0.8 | 2.9
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2751.44 | 2197.45 | 553.99 | 0.8 | 2.76
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9663.27 | 7717.62 | 1945.65 | 0.8 | 2.44
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8126.51 | 6490.28 | 1636.23 | 0.8 | 2.44
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9648.07 | 7705.48 | 1942.59 | 0.8 | 2.44
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2558.19 | 2043.11 | 515.08 | 0.8 | 2.8
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2128.03 | 1699.56 | 428.47 | 0.8 | 2.88
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7968.24 | 6363.88 | 1604.36 | 0.8 | 2.44
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2105 | 1681.17 | 423.83 | 0.8 | 2.89
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7844.21 | 6264.82 | 1579.39 | 0.8 | 2.44
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2089.33 | 1668.65 | 420.67 | 0.8 | 2.89
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2815.7 | 2248.77 | 566.93 | 0.8 | 2.75
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9586.94 | 7656.66 | 1930.28 | 0.8 | 2.44
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8033.96 | 6416.36 | 1617.59 | 0.8 | 2.44
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9586.98 | 7656.69 | 1930.29 | 0.8 | 2.44
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2544.19 | 2031.93 | 512.26 | 0.8 | 2.8
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2293.23 | 1831.5 | 461.73 | 0.8 | 2.85
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8483.92 | 6775.72 | 1708.19 | 0.8 | 2.44
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2184.01 | 1744.27 | 439.74 | 0.8 | 2.87
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8404.07 | 6711.96 | 1692.12 | 0.8 | 2.44
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2253.9 | 1800.09 | 453.81 | 0.8 | 2.86
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8247.25 | 6586.71 | 1660.54 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4818.48 | 3848.3 | 970.17 | 0.8 | 4.04
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4458.53 | 3560.83 | 897.7 | 0.8 | 4.04
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5004.73 | 3997.05 | 1007.68 | 0.8 | 4.04
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17503.03 | 12933.83 | 4569.21 | 0.74 | 3.82
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1410.72 | 1126.68 | 284.04 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10853.44 | 7661.61 | 3191.83 | 0.71 | 3.74
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 865.44 | 691.19 | 174.25 | 0.8 | 4.04
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5561.19 | 4318.72 | 1242.48 | 0.78 | 3.96
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26934.8 | 21511.62 | 5423.18 | 0.8 | 3.77
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2643.91 | 1911.38 | 732.54 | 0.72 | 3.79
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6573.18 | 5136.96 | 1436.21 | 0.78 | 3.98
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1114.56 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1033.36 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1071.04 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1228.94 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1053.78 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1074.63 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1285.88 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1275.26 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1073.1 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 1772.19 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 3878.15 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 2995.88 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 3813.87 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1188.27 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1152.4 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 3538.72 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 762.69 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 3678.59 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1096.74 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 1812.86 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 3985.17 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 3187.17 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 3971.98 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1223.36 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1194.66 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 3924.14 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 968.29 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 3908.06 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1151.56 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2100.58 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 5105.36 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 4108.56 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 5098.21 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1503.46 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1492.98 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 5092.42 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1359.31 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 5054.35 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1477.74 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1004.17 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 903.53 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 929.24 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1071.09 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 507.15 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 530.36 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 547.13 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 565.91 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 12435.26 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 7550.42 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 7057.7 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 7805.45 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 32953.13 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1931.42 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 24167.23 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1432.84 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 9833.14 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 41225.17 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 6219.83 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 11620.97 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.5 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 3.25 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.37 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.86 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 74.58 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 77.25 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 77.38 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 59.65 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 64.14 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.52 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 368.72 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 305.4 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 360.39 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.17 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 79.66 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 317.77 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 98.51 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 293.7 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 79.14 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 105.8 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 371.58 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 312.49 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 371 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 98.37 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.83 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 306.41 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 80.94 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 301.64 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 80.34 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 108.27 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 368.65 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 308.93 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 368.65 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 97.83 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.18 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 326.23 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 83.98 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 323.16 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 86.67 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 3.16 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.84 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.03 | 2.92 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.37 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.59 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.67 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.72 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.02 | 1.78 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.5 | 577.88 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.29 | 337.63 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.27 | 312.41 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.3 | 350.68 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.89 | 1008.92 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 98.85 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.49 | 568.67 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.05 | 60.64 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 366.28 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.63 | 1853.62 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.13 | 147.1 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.38 | 439.1 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.34 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 16269.7077 | 21.3887 | 42.3383 | 0 | 0.0002 | 559184.6693 | 6340.0204
February | 14109.8039 | 18.7635 | 38.0853 | 0 | 0.0002 | 503048.5335 | 5521.2851
March | 15535.9397 | 20.7241 | 42.3445 | 0 | 0.0002 | 559315.8094 | 6086.2168
April | 14469.1072 | 19.6339 | 41.5618 | 0 | 0.0002 | 549030.7287 | 5703.9307
May | 14647.3735 | 20.3677 | 45.2151 | 0 | 0.0002 | 597365.1073 | 5826.8978
June | 14029.2656 | 19.8108 | 45.2388 | 0 | 0.0002 | 597720.303 | 5613.4101
July | 14705.1359 | 21.0764 | 49.4053 | 0 | 0.0002 | 652813.1299 | 5917.1732
August | 14786.8103 | 21.2695 | 50.165 | 0 | 0.0002 | 662861.4127 | 5958.1788
September | 14281.6427 | 20.2513 | 46.5898 | 0 | 0.0002 | 615582.7807 | 5723.4037
October | 14637.7644 | 20.2781 | 44.6985 | 0 | 0.0002 | 590529.5788 | 5814.9076
November | 14866.9753 | 19.9349 | 41.1796 | 0 | 0.0002 | 543946.3467 | 5835.1951
December | 16205.7617 | 21.3688 | 42.5817 | 0 | 0.0002 | 562409.8073 | 6321.9756
Annual Sum or Average | 178545.288 | 244.8677 | 529.4038 | 0 | 0.0022 | 6993810 | 70662.5949
Minimum of Months | 14029.2656 | 18.7635 | 38.0853 | 0 | 0.0002 | 503048.5335 | 5521.2851
Maximum of Months | 16269.7077 | 21.3887 | 50.165 | 0 | 0.0002 | 662861.4127 | 6340.0204
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 197035000000 | 122389.996 | 28-JAN-20:00 | 57040.442 | 38772.136 | 7050.629 | 71.544 | 8720.467 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 177255000000 | 128914.987 | 21-FEB-20:00 | 57185.041 | 38824.77 | 7692.955 | 0 | 14477.442 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 197081000000 | 136667.965 | 29-MAR-19:00 | 57185.041 | 38824.77 | 8392.995 | 0 | 21530.38 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 193457000000 | 137699.663 | 29-APR-19:15 | 57040.442 | 38772.136 | 8482.478 | 0 | 22669.829 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 210488000000 | 142328.735 | 04-MAY-19:30 | 57185.041 | 38824.77 | 8844.448 | 0 | 26739.698 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 210613000000 | 144962.325 | 18-JUN-20:15 | 56692.16 | 36787.756 | 9255.531 | 0 | 31492.1 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 230026000000 | 152521.988 | 24-JUL-19:00 | 57185.041 | 38824.77 | 9453.716 | 0 | 36323.683 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 233566000000 | 153504.172 | 06-AUG-19:45 | 57112.741 | 38807.225 | 9513.935 | 0 | 37335.491 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 216907000000 | 159145.183 | 02-SEP-19:15 | 57040.442 | 38772.136 | 9849.808 | 0 | 42748.018 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 208079000000 | 138736.757 | 09-OCT-19:15 | 57112.741 | 38807.225 | 8569.505 | 0 | 23512.507 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 191665000000 | 135447.366 | 04-NOV-19:15 | 57040.442 | 38772.136 | 8284.951 | 0 | 20615.059 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 198171000000 | 125372.594 | 31-DEC-20:00 | 57112.741 | 38807.225 | 7332.314 | 0 | 11385.535 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2464340000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 177255000000 | 122389.996 |  | 56692.16 | 36787.756 | 7050.629 | 0 | 8720.467 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 233566000000 | 159145.183 |  | 57185.041 | 38824.77 | 9849.808 | 71.544 | 42748.018 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 49177.2 | 9582.97 | 0 | 58760.18
Cost per Total Building Area ($/m2) | 9.63 | 1.88 | 0 | 11.51
Cost per Net Conditioned Building Area ($/m2) | 12.44 | 2.42 | 0 | 14.86

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4058.29 | 794.78 | 1026.53
Net Site Energy | 4058.29 | 794.78 | 1026.53
Total Source Energy | 11077.89 | 2169.49 | 2802.13
Net Source Energy | 11077.89 | 2169.49 | 2802.13
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 109.87 | 499.54 | 0 | 0 | 0 | 0
Cooling | 405.93 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.14 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 230.15 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 660.94 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2708.33 | 1349.96 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.296 | 0.319 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.296 | 0.319 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.296 | 0.319 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.296 | 0.319 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 3.354 | 0.385 | 0.305 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 3.354 | 0.385 | 0.305 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 3.354 | 0.385 | 0.305 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.354 | 0.385 | 0.305 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.354 | 0.385 | 0.305 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.354 | 0.385 | 0.305 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.354 | 0.385 | 0.305 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.354 | 0.385 | 0.305 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.354 | 0.385 | 0.305 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 3.354 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 72.38 | 3.35 | 0.385 | 0.305
Non-North Total or Average |  |  | 111.83 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2149.47 | 1602.45 | 547.01 | 0.75 | 2.83
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2200.11 | 1647.01 | 553.1 | 0.75 | 2.82
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2255.56 | 1695.88 | 559.69 | 0.75 | 2.82
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2146.57 | 1599.92 | 546.65 | 0.75 | 2.83
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2188.14 | 1633.96 | 554.19 | 0.75 | 2.83
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3016.12 | 2318.57 | 697.55 | 0.77 | 2.68
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9602.72 | 7350.05 | 2252.67 | 0.77 | 2.42
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7677.87 | 5910.04 | 1767.83 | 0.77 | 2.42
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9443.61 | 7208.39 | 2235.22 | 0.76 | 2.42
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2524.69 | 1951.19 | 573.51 | 0.77 | 2.78
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2462.21 | 1895.3 | 566.9 | 0.77 | 2.79
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9576.9 | 7327.07 | 2249.83 | 0.77 | 2.42
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2815.48 | 2202.32 | 613.16 | 0.78 | 2.73
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9076.55 | 6882.23 | 2194.32 | 0.76 | 2.41
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2429.18 | 1865.81 | 563.37 | 0.77 | 2.8
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3002.85 | 2306.74 | 696.11 | 0.77 | 2.69
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9651.28 | 7393.34 | 2257.94 | 0.77 | 2.42
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7797.98 | 6017.31 | 1780.67 | 0.77 | 2.42
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9638.6 | 7382.05 | 2256.55 | 0.77 | 2.42
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2570.11 | 1988.78 | 581.33 | 0.77 | 2.78
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2505.5 | 1934 | 571.5 | 0.77 | 2.79
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9328.12 | 7105.67 | 2222.45 | 0.76 | 2.42
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2431.98 | 1865.39 | 566.58 | 0.77 | 2.8
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9224.84 | 7013.88 | 2210.96 | 0.76 | 2.42
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2453.23 | 1887.28 | 565.95 | 0.77 | 2.79
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3059.71 | 2362.58 | 697.14 | 0.77 | 2.68
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9601.43 | 7433.07 | 2168.35 | 0.77 | 2.42
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7782.91 | 6058.61 | 1724.31 | 0.78 | 2.43
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9597.6 | 7429.64 | 2167.96 | 0.77 | 2.42
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2561.29 | 2003.2 | 558.09 | 0.78 | 2.78
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2512.62 | 2001.07 | 511.55 | 0.8 | 2.81
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9239.29 | 7242.54 | 1996.75 | 0.78 | 2.43
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2363.96 | 1860.02 | 503.94 | 0.79 | 2.83
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9173.23 | 7182.37 | 1990.86 | 0.78 | 2.43
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2453.43 | 1946.72 | 506.71 | 0.79 | 2.82
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9113.18 | 7278.29 | 1834.89 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5431.61 | 4180.93 | 1250.68 | 0.77 | 3.94
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5120.5 | 3911.03 | 1209.47 | 0.76 | 3.92
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5447.11 | 4224.17 | 1222.94 | 0.78 | 3.96
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 20361.73 | 13766.22 | 6595.51 | 0.68 | 3.45
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1471.31 | 1168.23 | 303.08 | 0.79 | 4.02
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11711.04 | 7917.64 | 3793.4 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1189.84 | 844.17 | 345.67 | 0.71 | 3.75
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8039.06 | 5479.55 | 2559.51 | 0.68 | 3.67
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30881.4 | 23569.36 | 7312.04 | 0.76 | 3.67
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3468.76 | 2345.17 | 1123.59 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10252.74 | 7046.81 | 3205.92 | 0.69 | 3.68
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 2508.85 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 2183.07 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 2215.83 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2423.4 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 33.57 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 159.61 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1686.3 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1709.31 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1941.03 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1930.26 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1714.52 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 2846.33 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 6183.75 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 4827.94 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 6095.71 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1780.78 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1746.06 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 5858.69 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1290.36 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 5991.25 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1716.97 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 2894.83 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 6298.58 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 5025.97 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 6276.05 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1819.56 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1792.77 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 6238.87 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1591.86 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 6216.44 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1766.3 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 3269.39 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 7748.96 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 6215.28 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 7733.82 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2181.33 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2177.68 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 7732.89 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2076.24 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 7687.5 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2151.35 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 2363.26 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 2024.41 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 2051.14 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2249.85 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1288.15 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1181.72 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1199.04 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1221.6 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 14228.69 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 8339.48 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 7837.87 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 8474.55 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 39279.2 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1972.94 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 31729.98 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1625.27 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 11773.44 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 44938.26 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 8554.26 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 14629.1 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 7.95 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.92 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.02 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.68 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.11 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.51 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 70.71 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 73.08 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75.7 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 70.57 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 72.26 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 106.54 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 335.87 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 272.03 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 328.23 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.27 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 87.24 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 334.63 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.42 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 310.66 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 85.64 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 105.9 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 338.21 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 277.83 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 337.6 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 92.15 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 89.33 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 322.69 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 85.47 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 317.74 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 86.8 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 109.18 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 344.61 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 282.83 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 344.42 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.06 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.03 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 341.01 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 87.98 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 337.69 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 93.01 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.49 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.41 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.5 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.13 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 4.08 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.75 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.8 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.87 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 638.56 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.3 | 350.66 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.28 | 324.78 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 357.63 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.82 | 951.08 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 101.79 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.47 | 547.02 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.05 | 63.15 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.33 | 383.98 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.69 | 1920.4 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.14 | 162.02 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 500.84 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.34 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 89123.791 | 153.0668 | 433.0026 | 0 | 0.0013 | 99670.1452 | 37745.9887
February | 75180.0346 | 129.2498 | 366.0422 | 0 | 0.0011 | 84257.1496 | 31852.9977
March | 76904.273 | 132.8537 | 378.2717 | 0 | 0.0012 | 87073.118 | 32644.6945
April | 73160.8192 | 128.0378 | 369.7556 | 0 | 0.0011 | 85115.2187 | 31213.5036
May | 81585.0378 | 144.4795 | 422.5141 | 0 | 0.0013 | 97262.2449 | 34970.0317
June | 87745.6791 | 156.576 | 461.5324 | 0 | 0.0014 | 106245.8332 | 37724.1382
July | 96334.7162 | 172.3748 | 509.5409 | 0 | 0.0015 | 117298.1346 | 41461.9412
August | 93793.022 | 167.7883 | 495.8659 | 0 | 0.0015 | 114150.0548 | 40364.3215
September | 84419.1301 | 150.5631 | 443.5744 | 0 | 0.0013 | 102111.7468 | 36286.6199
October | 79169.9323 | 139.8816 | 408.0829 | 0 | 0.0012 | 93939.7633 | 33904.1553
November | 74098.0619 | 129.047 | 370.7097 | 0 | 0.0011 | 85333.9377 | 31553.0383
December | 84253.8291 | 145.0557 | 411.4576 | 0 | 0.0013 | 94711.3592 | 35717.1865
Annual Sum or Average | 995768.3263 | 1748.9742 | 5070.35 | 0 | 0.0154 | 1167170 | 425438.6169
Minimum of Months | 73160.8192 | 128.0378 | 366.0422 | 0 | 0.0011 | 84257.1496 | 31213.5036
Maximum of Months | 96334.7162 | 172.3748 | 509.5409 | 0 | 0.0015 | 117298.1346 | 41461.9412
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 231277000000 | 153480.575 | 07-JAN-07:15 | 30350.287 | 41065.016 | 8374.822 | 62955.671 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 195512000000 | 128437.13 | 11-FEB-08:15 | 41071.521 | 57998.833 | 6764.086 | 22517.911 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 202047000000 | 136210.779 | 14-MAR-19:00 | 57185.041 | 38824.77 | 8196.7 | 0 | 21269.49 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 197503000000 | 135321.728 | 28-APR-19:00 | 57185.041 | 38824.77 | 8240.816 | 0 | 20336.323 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 225690000000 | 151890.168 | 30-MAY-19:15 | 57185.041 | 38824.77 | 9224.642 | 0 | 35920.936 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 246535000000 | 164924.314 | 16-JUN-19:30 | 57185.041 | 38824.77 | 9870.714 | 0 | 48309.01 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 272181000000 | 174372.035 | 02-JUL-19:30 | 57112.741 | 38807.225 | 10364.257 | 0 | 57353.033 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 264877000000 | 180964.9 | 04-AUG-19:15 | 57185.041 | 38824.77 | 10621.004 | 0 | 63599.307 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 236943000000 | 156864.06 | 06-SEP-19:15 | 57185.041 | 38824.77 | 9514.993 | 0 | 40604.478 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 217980000000 | 146173.018 | 30-OCT-19:30 | 57185.041 | 38824.77 | 8912.033 | 0 | 30516.395 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 198011000000 | 145829.363 | 02-NOV-19:30 | 57185.041 | 38824.77 | 8867.468 | 0 | 30217.306 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 219771000000 | 143499.6 | 31-DEC-20:00 | 57112.741 | 38807.225 | 6874.54 | 29970.315 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2708330000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 195512000000 | 128437.13 |  | 30350.287 | 38807.225 | 6764.086 | 0 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 272181000000 | 180964.9 |  | 57185.041 | 57998.833 | 10621.004 | 62955.671 | 63599.307 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 73320.77 | 11849.58 | 0 | 85170.36
Cost per Total Building Area ($/m2) | 14.36 | 2.32 | 0 | 16.68
Cost per Net Conditioned Building Area ($/m2) | 18.55 | 3 | 0 | 21.54

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3825.99 | 749.28 | 967.77
Net Site Energy | 3825.99 | 749.28 | 967.77
Total Source Energy | 10011.22 | 1960.6 | 2532.32
Net Source Energy | 10011.22 | 1960.6 | 2532.32
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 56.23 | 357.82 | 0 | 0 | 0 | 0
Cooling | 353.04 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.17 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 248.83 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 658.18 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2620.5 | 1205.48 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.466 | 0.5 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.285 | 0.306 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.285 | 0.306 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.285 | 0.306 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.285 | 0.306 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 3.354 | 0.385 | 0.305 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 3.354 | 0.385 | 0.305 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 3.354 | 0.385 | 0.305 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.354 | 0.385 | 0.305 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.354 | 0.385 | 0.305 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.354 | 0.385 | 0.305 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.354 | 0.385 | 0.305 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.354 | 0.385 | 0.305 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 3.354 | 0.385 | 0.305 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 3.354 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 3.354 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 3.354 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 3.354 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 72.38 | 3.35 | 0.385 | 0.305
Non-North Total or Average |  |  | 111.83 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1929.5 | 1541 | 388.49 | 0.8 | 2.9
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1992.82 | 1591.57 | 401.24 | 0.8 | 2.9
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1952.76 | 1559.58 | 393.18 | 0.8 | 2.9
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1785.92 | 1426.33 | 359.59 | 0.8 | 2.9
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1989.33 | 1588.79 | 400.54 | 0.8 | 2.9
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2906.16 | 2321.02 | 585.14 | 0.8 | 2.73
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9695.56 | 7743.41 | 1952.15 | 0.8 | 2.44
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7851 | 6270.24 | 1580.76 | 0.8 | 2.44
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9479.28 | 7570.68 | 1908.6 | 0.8 | 2.44
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2476.25 | 1977.67 | 498.58 | 0.8 | 2.82
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2355.28 | 1881.06 | 474.22 | 0.8 | 2.84
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9738.22 | 7777.48 | 1960.74 | 0.8 | 2.44
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3025.47 | 2416.31 | 609.16 | 0.8 | 2.71
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8983.09 | 7174.39 | 1808.7 | 0.8 | 2.44
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2375.49 | 1897.19 | 478.29 | 0.8 | 2.84
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2884.47 | 2303.7 | 580.77 | 0.8 | 2.73
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9788.62 | 7817.73 | 1970.89 | 0.8 | 2.44
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8027.05 | 6410.84 | 1616.2 | 0.8 | 2.44
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9767.96 | 7801.23 | 1966.73 | 0.8 | 2.44
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2529.56 | 2020.24 | 509.31 | 0.8 | 2.8
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2410.9 | 1925.48 | 485.42 | 0.8 | 2.83
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9353.49 | 7470.21 | 1883.28 | 0.8 | 2.44
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2466.14 | 1969.6 | 496.54 | 0.8 | 2.82
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9203.48 | 7350.41 | 1853.07 | 0.8 | 2.44
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2396.52 | 1914 | 482.53 | 0.8 | 2.83
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2893.55 | 2310.95 | 582.6 | 0.8 | 2.73
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9623.51 | 7685.86 | 1937.64 | 0.8 | 2.44
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7881.58 | 6294.66 | 1586.91 | 0.8 | 2.44
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9610.51 | 7675.48 | 1935.03 | 0.8 | 2.44
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2501.95 | 1998.2 | 503.76 | 0.8 | 2.81
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2515.3 | 2008.85 | 506.44 | 0.8 | 2.81
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9532.31 | 7613.03 | 1919.28 | 0.8 | 2.44
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2433.89 | 1943.84 | 490.05 | 0.8 | 2.82
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9435.39 | 7535.63 | 1899.77 | 0.8 | 2.44
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2477.08 | 1978.33 | 498.75 | 0.8 | 2.82
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9673.91 | 7726.12 | 1947.79 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5383.86 | 4299.85 | 1084.01 | 0.8 | 4.04
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4934.29 | 3940.8 | 993.49 | 0.8 | 4.04
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5103.89 | 4076.24 | 1027.64 | 0.8 | 4.04
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 17037.64 | 12686 | 4351.65 | 0.74 | 3.86
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1491.26 | 1191 | 300.26 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11783.14 | 8254.13 | 3529.01 | 0.7 | 3.72
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 845 | 674.86 | 170.14 | 0.8 | 4.04
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6273.91 | 5010.69 | 1263.22 | 0.8 | 4.04
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 32298.02 | 25794.99 | 6503.04 | 0.8 | 3.73
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3102.91 | 2260.82 | 842.09 | 0.73 | 3.81
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7455.44 | 5954.33 | 1501.11 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1965.81 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1726.25 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1761.56 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1958.36 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 114.26 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1429.27 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1451.88 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 1681.84 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 1672.43 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1457.82 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 2387.26 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 5154.12 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 4015.37 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 5069.68 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1521.6 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1488.15 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 4828.06 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1019.38 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 4963.58 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1450.99 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 2430.76 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 5253.64 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 4200.59 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 5232.49 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1556.32 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1530.44 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 5199.72 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1315.71 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 5178.7 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1501.07 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 2782.57 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 6619.47 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 5320.88 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 6605.53 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 1897.12 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 1893.76 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 6609.97 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 1777.12 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 6566.14 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 1868.61 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1831.31 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1576.6 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1602.11 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1786.1 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1014.56 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 944.83 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 960.8 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 981.12 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 12511.25 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 7372.27 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 6859.7 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 7053.05 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 33230.95 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1700.46 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 26735.29 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1284.24 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 10615.69 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 42455.87 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 7191.17 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 12435.03 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.42 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.51 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.65 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.39 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.43 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 74.2 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.63 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 75.09 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 68.67 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.5 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 111.75 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 372.83 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 301.9 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 364.51 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 95.22 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.57 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 374.47 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.18 | 116.34 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 345.43 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.35 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 110.92 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 376.4 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 308.67 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.59 | 375.61 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 97.27 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 92.71 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 359.67 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.83 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 353.9 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 92.15 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 111.27 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 370.06 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 303.07 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 369.56 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.21 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 96.72 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 366.55 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 93.59 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 362.82 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 95.25 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.91 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.95 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.05 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.74 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.83 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.57 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.63 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.7 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.58 | 677.85 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.33 | 377.25 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.3 | 345.75 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 357.63 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.88 | 1018.26 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 104.49 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.52 | 605.23 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.05 | 59.21 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.38 | 439.61 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.95 | 2133.8 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.15 | 176 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 522.4 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.34 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 64149.3348 | 106.0124 | 258.9024 | 0 | 0.001 | 269177.2937 | 26889.2398
February | 56055.2627 | 92.7716 | 226.9682 | 0 | 0.0009 | 235976.6955 | 23509.7599
March | 60479.5206 | 100.5378 | 247.2855 | 0 | 0.001 | 257103.5652 | 25408.8648
April | 58578.308 | 98.3972 | 245.0319 | 0 | 0.001 | 254767.696 | 24710.1575
May | 62390.0974 | 105.6472 | 265.5615 | 0 | 0.001 | 276118.8904 | 26401.1817
June | 63936.8264 | 109.0796 | 276.5469 | 0 | 0.0011 | 287546.5171 | 27135.4722
July | 72057.6515 | 123.5845 | 315.1919 | 0 | 0.0012 | 327732.9882 | 30645.8271
August | 70002.717 | 119.9934 | 305.8421 | 0 | 0.0012 | 318010.7914 | 29765.3272
September | 63623.6666 | 108.5533 | 275.2356 | 0 | 0.0011 | 286183.2017 | 27003.3485
October | 62256.7757 | 105.285 | 264.2557 | 0 | 0.001 | 274760.25 | 26331.3845
November | 58377.5826 | 97.4064 | 240.6544 | 0 | 0.0009 | 250211.7364 | 24561.3694
December | 63759.1664 | 105.4028 | 257.5183 | 0 | 0.001 | 267738.4853 | 26729.1479
Annual Sum or Average | 755666.9097 | 1272.6711 | 3178.9944 | 0 | 0.0125 | 3305330 | 319091.0804
Minimum of Months | 56055.2627 | 92.7716 | 226.9682 | 0 | 0.0009 | 235976.6955 | 23509.7599
Maximum of Months | 72057.6515 | 123.5845 | 315.1919 | 0 | 0.0012 | 327732.9882 | 30645.8271
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 213407000000 | 139541.713 | 06-JAN-07:15 | 37896.934 | 51279.599 | 7712.54 | 31917.861 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 187085000000 | 131383.098 | 12-FEB-20:00 | 57112.741 | 38807.225 | 8666.976 | 0 | 16061.377 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 203835000000 | 136881.959 | 26-MAR-19:15 | 57112.741 | 38807.225 | 9161.661 | 0 | 21065.553 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 201983000000 | 142604.846 | 25-APR-19:00 | 57185.041 | 38824.77 | 9610.594 | 0 | 26249.663 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 218910000000 | 150139.742 | 23-MAY-19:15 | 57185.041 | 38824.77 | 9982.886 | 0 | 33412.266 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 227970000000 | 153942.742 | 27-JUN-19:30 | 57185.041 | 38824.77 | 10245.967 | 0 | 36952.185 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 259831000000 | 162112.746 | 17-JUL-19:30 | 57185.041 | 38824.77 | 10694.696 | 0 | 44673.461 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 252123000000 | 158308.109 | 29-AUG-19:15 | 57185.041 | 38824.77 | 10471.249 | 0 | 41092.271 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 226889000000 | 151569.2 | 01-SEP-19:30 | 57185.041 | 38824.77 | 10100.768 | 0 | 34723.843 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 217833000000 | 144362.566 | 01-OCT-19:15 | 57112.741 | 38807.225 | 9811.605 | 0 | 27896.215 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 198371000000 | 131878.118 | 04-NOV-19:15 | 57040.442 | 38772.136 | 8733.845 | 0 | 16596.917 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 212266000000 | 135398.947 | 12-DEC-07:15 | 37896.934 | 51279.599 | 7606.407 | 27881.229 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2620500000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 187085000000 | 131383.098 |  | 37896.934 | 38772.136 | 7606.407 | 0 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 259831000000 | 162112.746 |  | 57185.041 | 51279.599 | 10694.696 | 31917.861 | 44673.461 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 27072.96 | 8617.43 | 0 | 35690.4
Cost per Total Building Area ($/m2) | 5.3 | 1.69 | 0 | 6.99
Cost per Net Conditioned Building Area ($/m2) | 6.85 | 2.18 | 0 | 9.03

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4298.18 | 841.76 | 1087.21
Net Site Energy | 4298.18 | 841.76 | 1087.21
Total Source Energy | 11158.49 | 2185.28 | 2822.52
Net Source Energy | 11158.49 | 2185.28 | 2822.52
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 182.56 | 644.99 | 0 | 0 | 0 | 0
Cooling | 382.59 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.28 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 229.22 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 706.83 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2756.88 | 1541.3 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.369 | 0.391 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.252 | 0.268 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.252 | 0.268 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.252 | 0.268 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.252 | 0.268 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 2.956 | 0.385 | 0.305 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 2.956 | 0.385 | 0.305 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 2.956 | 0.385 | 0.305 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.385 | 0.305 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.385 | 0.305 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.385 | 0.305 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.385 | 0.305 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.385 | 0.305 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.385 | 0.305 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 2.956 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 72.38 | 2.96 | 0.385 | 0.305
Non-North Total or Average |  |  | 111.83 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2028.6 | 1530.33 | 498.27 | 0.75 | 2.86
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2078.46 | 1574.56 | 503.89 | 0.76 | 2.86
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2106.19 | 1602.45 | 503.74 | 0.76 | 2.85
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2027.32 | 1526.75 | 500.56 | 0.75 | 2.86
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2086.51 | 1576.86 | 509.65 | 0.76 | 2.85
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2755.79 | 2130.55 | 625.24 | 0.77 | 2.74
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9204.72 | 7142.06 | 2062.66 | 0.78 | 2.43
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7454.26 | 5791.34 | 1662.92 | 0.78 | 2.43
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9045.14 | 6998.66 | 2046.48 | 0.77 | 2.42
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2400.82 | 1878.9 | 521.92 | 0.78 | 2.82
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2356.63 | 1835.39 | 521.24 | 0.78 | 2.82
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9261.23 | 7171.18 | 2090.05 | 0.77 | 2.42
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2731.42 | 2161.65 | 569.78 | 0.79 | 2.76
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8762.69 | 6724.6 | 2038.09 | 0.77 | 2.42
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2340.02 | 1817.66 | 522.36 | 0.78 | 2.82
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2741.92 | 2118.12 | 623.8 | 0.77 | 2.74
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9257.38 | 7189.4 | 2067.97 | 0.78 | 2.43
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7586.06 | 5909.66 | 1676.4 | 0.78 | 2.43
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9246.07 | 7179.24 | 2066.83 | 0.78 | 2.43
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2449.19 | 1918.84 | 530.35 | 0.78 | 2.81
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2407.29 | 1878.18 | 529.11 | 0.78 | 2.81
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9017.54 | 6952.67 | 2064.87 | 0.77 | 2.42
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2350.93 | 1824.75 | 526.17 | 0.78 | 2.82
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8915.06 | 6860.9 | 2054.16 | 0.77 | 2.42
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2364.7 | 1839.85 | 524.85 | 0.78 | 2.82
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2737.89 | 2127.12 | 610.77 | 0.78 | 2.75
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9091.83 | 7124.92 | 1966.91 | 0.78 | 2.43
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7427.74 | 5836.63 | 1591.1 | 0.79 | 2.43
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9091.13 | 7124.27 | 1966.86 | 0.78 | 2.43
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2412.56 | 1907.95 | 504.61 | 0.79 | 2.82
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2397.64 | 1914.89 | 482.75 | 0.8 | 2.83
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8721.52 | 6914.71 | 1806.81 | 0.79 | 2.44
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2224.3 | 1768.97 | 455.33 | 0.8 | 2.86
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8656.31 | 6854.92 | 1801.39 | 0.79 | 2.44
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2325.39 | 1857.19 | 468.21 | 0.8 | 2.85
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9109.34 | 7275.22 | 1834.12 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5202.18 | 4049.59 | 1152.58 | 0.78 | 3.97
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4881.04 | 3775.68 | 1105.36 | 0.77 | 3.95
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5029.41 | 3920.05 | 1109.37 | 0.78 | 3.97
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19910.32 | 13461.03 | 6449.29 | 0.68 | 3.45
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1394.09 | 1113.4 | 280.69 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11570.15 | 7822.38 | 3747.76 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1086.21 | 776.09 | 310.12 | 0.71 | 3.76
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7746.6 | 5351.02 | 2395.58 | 0.69 | 3.69
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30647.99 | 23521.73 | 7126.25 | 0.77 | 3.68
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3460.09 | 2339.31 | 1120.78 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9760.34 | 6784.44 | 2975.91 | 0.7 | 3.71
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 2876.85 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 2469.15 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 2500.46 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2705.8 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 46.04 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 171.54 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1840.4 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1863.47 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 2091.16 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 2080.35 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1868.79 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 3062.27 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 6698.75 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 5232.01 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 6613.99 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1905.73 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1869.29 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 6377.14 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1424.8 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 6509.89 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1844.8 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 3105.6 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 6802.5 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 5418.37 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 6782.56 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1941.82 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1913.25 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 6742.49 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1722.99 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 6720.76 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1891.21 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 3471.29 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 8212.68 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 6574.68 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 8199.9 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2293.92 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2289.52 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 8197.77 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2197.09 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 8152.66 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2266.55 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 2723.85 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 2309.56 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 2336.74 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2531.4 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1448.89 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1302.29 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1319.11 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1342.42 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 14352.31 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 8355.01 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 7858.39 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 8153.1 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 41255.69 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1878.75 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 34080.06 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1578.58 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 12231.44 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 45692.63 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 9177.85 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 14966.4 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.19 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.88 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 7.98 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.64 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.15 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.55 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 68.61 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 70.99 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 72.66 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 68.3 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 70.87 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 98.61 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 332.06 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.42 | 269.69 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 324.25 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.29 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 85.73 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 332.55 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 102.96 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 308.32 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.63 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 97.93 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 334.64 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 276.13 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 334.08 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.29 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 87.92 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 320.69 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.88 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 315.71 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 85.83 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 99.06 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 335.35 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 275.63 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 335.32 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.8 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 92.2 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 330.06 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 84.75 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 326.75 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 89.42 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.7 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.37 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.46 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.08 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.63 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 4.16 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.21 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.29 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.55 | 638.29 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.3 | 344.48 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.27 | 318.65 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.29 | 333.98 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.8 | 930 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.08 | 97.68 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.47 | 540.44 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.05 | 58.69 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.33 | 383.5 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.69 | 1930.31 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.14 | 161.62 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.42 | 491.28 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.34 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 69761.9176 | 115.6489 | 170.7023 | 0 | 0.0013 | 112167.4 | 29146.3518
February | 56396.3971 | 93.5434 | 138.1653 | 0 | 0.001 | 90787.7891 | 23567.1875
March | 53855.1893 | 90.4936 | 135.7339 | 0 | 0.001 | 89195.3541 | 22616.6389
April | 49793.7822 | 85.4702 | 131.3619 | 0 | 0.001 | 86330.2642 | 21083.1866
May | 55116.1251 | 96.3534 | 151.0932 | 0 | 0.0011 | 99304.8504 | 23503.7626
June | 57218.6439 | 101.0068 | 160.0408 | 0 | 0.0012 | 105189.4941 | 24493.8244
July | 61540.5519 | 109.0555 | 173.4945 | 0 | 0.0013 | 114033.8263 | 26384.0015
August | 60933.6213 | 108.0395 | 171.9774 | 0 | 0.0013 | 113036.9298 | 26129.4895
September | 53583.3241 | 94.3662 | 149.1459 | 0 | 0.0011 | 98027.7943 | 22916.301
October | 51731.0231 | 89.4966 | 138.7557 | 0 | 0.001 | 91192.3303 | 21970.4554
November | 51557.6929 | 87.1932 | 131.7672 | 0 | 0.001 | 86591.13 | 21705.3365
December | 63121.3288 | 104.9879 | 155.585 | 0 | 0.0012 | 102235.448 | 26405.1518
Annual Sum or Average | 684609.5973 | 1175.6552 | 1807.8232 | 0 | 0.0133 | 1188090 | 289921.6875
Minimum of Months | 49793.7822 | 85.4702 | 131.3619 | 0 | 0.001 | 86330.2642 | 21083.1866
Maximum of Months | 69761.9176 | 115.6489 | 173.4945 | 0 | 0.0013 | 114033.8263 | 29146.3518
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 260276000000 | 166142.553 | 06-JAN-07:15 | 37896.934 | 51279.599 | 7811.376 | 58419.865 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 210666000000 | 151869.353 | 04-FEB-06:15 | 29080.703 | 25635.382 | 8764.878 | 77653.611 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 206971000000 | 135224.298 | 19-MAR-19:00 | 57112.741 | 38807.225 | 8185.182 | 0 | 20384.371 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 200323000000 | 145478.683 | 02-APR-19:00 | 57112.741 | 38807.225 | 8916.579 | 0 | 29907.358 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 230429000000 | 170110.73 | 27-MAY-19:45 | 57040.442 | 38772.136 | 10191.298 | 0 | 53372.076 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 244084000000 | 167736.669 | 29-JUN-19:00 | 57185.041 | 38824.77 | 10086.382 | 0 | 50905.698 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 264607000000 | 175986.287 | 13-JUL-19:00 | 57185.041 | 38824.77 | 10402.734 | 0 | 58838.964 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 262294000000 | 175308.066 | 27-AUG-19:15 | 57112.741 | 38807.225 | 10471.329 | 0 | 58181.992 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 227466000000 | 152385.907 | 14-SEP-19:15 | 57185.041 | 38824.77 | 9277.274 | 0 | 36364.043 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 211605000000 | 147068.644 | 08-OCT-19:15 | 57112.741 | 38807.225 | 9085.225 | 0 | 31328.674 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 200928000000 | 133281.334 | 02-NOV-19:00 | 57185.041 | 38824.77 | 8049.892 | 0 | 18486.853 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 237230000000 | 165564.625 | 31-DEC-06:15 | 29080.703 | 25635.382 | 9248.609 | 90865.153 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2756880000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 200323000000 | 133281.334 |  | 29080.703 | 25635.382 | 7811.376 | 0 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 264607000000 | 175986.287 |  | 57185.041 | 51279.599 | 10471.329 | 90865.153 | 58838.964 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 42100.33 | 12257.56 | 0 | 54357.9
Cost per Total Building Area ($/m2) | 8.24 | 2.4 | 0 | 10.65
Cost per Net Conditioned Building Area ($/m2) | 10.65 | 3.1 | 0 | 13.75

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4013.56 | 786.02 | 1015.22
Net Site Energy | 4013.56 | 786.02 | 1015.22
Total Source Energy | 10548.67 | 2065.85 | 2668.26
Net Source Energy | 10548.67 | 2065.85 | 2668.26
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 120.33 | 522.56 | 0 | 0 | 0 | 0
Cooling | 269.92 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.08 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 233.79 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 715.17 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2586.35 | 1427.21 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.409 | 0.435 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.274 | 0.294 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.274 | 0.294 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.274 | 0.294 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.274 | 0.294 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 2.956 | 0.385 | 0.305 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 2.956 | 0.385 | 0.305 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 2.956 | 0.385 | 0.305 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.385 | 0.305 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.385 | 0.305 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.385 | 0.305 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.385 | 0.305 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.385 | 0.305 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.385 | 0.305 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 2.956 | 0.385 | 0.305 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 2.956 | 0.385 | 0.305 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 72.38 | 2.96 | 0.385 | 0.305
Non-North Total or Average |  |  | 111.83 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1854.82 | 1481.36 | 373.46 | 0.8 | 2.9
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1918.83 | 1532.49 | 386.35 | 0.8 | 2.9
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1878.63 | 1500.38 | 378.25 | 0.8 | 2.9
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1692.38 | 1351.63 | 340.75 | 0.8 | 2.9
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1876.06 | 1498.32 | 377.73 | 0.8 | 2.9
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2708.73 | 2163.34 | 545.39 | 0.8 | 2.77
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9421.56 | 7524.58 | 1896.98 | 0.8 | 2.44
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7678.13 | 6132.18 | 1545.95 | 0.8 | 2.44
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9208.97 | 7354.8 | 1854.18 | 0.8 | 2.44
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2408.21 | 1923.33 | 484.88 | 0.8 | 2.83
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2259.77 | 1804.78 | 454.99 | 0.8 | 2.86
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9287.19 | 7417.27 | 1869.93 | 0.8 | 2.44
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2882.3 | 2301.97 | 580.34 | 0.8 | 2.74
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8570.98 | 6845.26 | 1725.72 | 0.8 | 2.44
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2272.99 | 1815.34 | 457.66 | 0.8 | 2.86
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2689.97 | 2148.36 | 541.61 | 0.8 | 2.77
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9526.77 | 7608.6 | 1918.16 | 0.8 | 2.44
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7868.92 | 6284.55 | 1584.37 | 0.8 | 2.44
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9509.35 | 7594.69 | 1914.66 | 0.8 | 2.44
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2469.45 | 1972.24 | 497.21 | 0.8 | 2.82
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2320.21 | 1853.05 | 467.16 | 0.8 | 2.85
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8939.09 | 7139.25 | 1799.84 | 0.8 | 2.44
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2356.95 | 1882.39 | 474.56 | 0.8 | 2.84
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8796.16 | 7025.1 | 1771.06 | 0.8 | 2.44
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2299.71 | 1836.68 | 463.03 | 0.8 | 2.85
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2680.06 | 2140.44 | 539.62 | 0.8 | 2.78
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9318.64 | 7442.38 | 1876.26 | 0.8 | 2.44
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7645.35 | 6106 | 1539.35 | 0.8 | 2.44
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9312.55 | 7437.52 | 1875.03 | 0.8 | 2.44
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2439.69 | 1948.47 | 491.22 | 0.8 | 2.82
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2411.45 | 1925.92 | 485.53 | 0.8 | 2.83
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9059.84 | 7235.69 | 1824.15 | 0.8 | 2.44
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2314.93 | 1848.83 | 466.1 | 0.8 | 2.85
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8966.78 | 7161.36 | 1805.41 | 0.8 | 2.44
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2366.99 | 1890.41 | 476.58 | 0.8 | 2.84
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9235.36 | 7375.87 | 1859.49 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5136.85 | 4102.57 | 1034.28 | 0.8 | 4.04
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4725.3 | 3773.89 | 951.41 | 0.8 | 4.04
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4872.51 | 3891.46 | 981.05 | 0.8 | 4.04
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 15383.02 | 11790.47 | 3592.55 | 0.77 | 3.93
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1427.13 | 1139.79 | 287.35 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9960.84 | 7339.53 | 2621.31 | 0.74 | 3.83
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 813.91 | 650.04 | 163.88 | 0.8 | 4.04
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5932.16 | 4737.75 | 1194.41 | 0.8 | 4.04
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30569.93 | 24414.83 | 6155.09 | 0.8 | 3.73
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2561 | 1976.24 | 584.76 | 0.77 | 3.94
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7048.85 | 5629.6 | 1419.25 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 2744.96 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 2362.61 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 2395.64 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2632.47 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 29.49 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 51.03 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 193.08 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1771.53 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1794.8 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 2029.71 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 2018.51 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1800.25 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 2957.66 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 6391.01 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 4988.98 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 6300.46 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1834.31 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1798.3 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 6060.59 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1343.95 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 6193.35 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1768.5 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 3004.91 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 6501.26 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 5181.58 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 6478.05 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 1871.89 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1843.86 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 6433.31 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1647.08 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 6410.36 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1815.81 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 3422.91 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 8120.35 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 6506.86 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 8104.68 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2275.66 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2272.95 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 8096.19 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2180.86 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 8049.81 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2245.21 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 2594.83 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 2200.58 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 2228.23 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2456.05 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1424.32 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1281.41 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1297.77 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1321.61 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 13028.91 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 7774.88 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 7279.32 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 7456.56 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 38364.9 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1718.72 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 31731.17 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1393.33 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 11603.31 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 44063.72 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 8431.79 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 13556.23 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.11 | 9.81 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.44 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.56 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.41 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.11 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.18 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.69 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 71.32 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 73.79 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 72.24 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 65.08 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 72.14 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 104.16 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 362.29 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 295.25 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 354.12 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 92.6 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 86.9 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 357.12 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.17 | 110.83 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 329.58 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 87.4 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.44 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 366.34 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 302.59 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.57 | 365.67 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.96 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 89.22 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 343.74 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 90.63 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 338.24 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.43 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 103.06 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 358.33 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 293.99 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.56 | 358.1 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 93.81 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 92.73 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.55 | 348.38 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 89.02 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 344.8 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.02 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.27 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.86 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 7.96 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.78 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 5.09 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.58 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.64 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.72 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.56 | 647.12 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 359.94 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.29 | 331.1 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.29 | 341.42 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.85 | 983.5 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.09 | 100 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.5 | 580.6 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.05 | 57.03 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.36 | 415.67 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.85 | 2019.63 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.14 | 166.28 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.43 | 493.91 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.34 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 65077.7992 | 106.7274 | 172.6439 | 0 | 0.0012 | 4094450 | 27130.1283
February | 55208.0986 | 90.6892 | 146.996 | 0 | 0.001 | 3486210 | 23029.881
March | 55909.2459 | 92.8101 | 152.3678 | 0 | 0.0011 | 3613770 | 23416.0433
April | 51670.386 | 86.4158 | 143.1385 | 0 | 0.001 | 3394980 | 21702.7971
May | 54535.9776 | 92.3388 | 155.1653 | 0 | 0.0011 | 3680410 | 23015.6938
June | 56063.13 | 95.9183 | 163.1043 | 0 | 0.0011 | 3868870 | 23756.2541
July | 61309.6018 | 105.5977 | 180.9108 | 0 | 0.0013 | 4291350 | 26047.3711
August | 60159.8982 | 103.5529 | 177.2849 | 0 | 0.0012 | 4205330 | 25552.6806
September | 55391.7656 | 94.7931 | 161.2358 | 0 | 0.0011 | 3824550 | 23474.033
October | 54334.3188 | 91.836 | 154.0079 | 0 | 0.0011 | 3652930 | 22914.986
November | 52906.7313 | 88.0514 | 145.0006 | 0 | 0.001 | 3439070 | 22180.3199
December | 62427.9614 | 102.716 | 166.823 | 0 | 0.0012 | 3956460 | 26057.7538
Annual Sum or Average | 684994.9145 | 1151.4465 | 1918.6789 | 0 | 0.0134 | 45508400 | 288277.9421
Minimum of Months | 51670.386 | 86.4158 | 143.1385 | 0 | 0.001 | 3394980 | 21702.7971
Maximum of Months | 65077.7992 | 106.7274 | 180.9108 | 0 | 0.0013 | 4291350 | 27130.1283
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 232698000000 | 167379.617 | 07-JAN-08:15 | 41071.521 | 57998.833 | 7919.756 | 49654.729 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 198130000000 | 144507.68 | 26-FEB-07:15 | 30422.587 | 41100.106 | 8180.267 | 54069.943 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 205379000000 | 133933.641 | 30-MAR-19:30 | 57185.041 | 38824.77 | 8571.869 | 0 | 18617.182 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 192945000000 | 134164.689 | 30-APR-19:30 | 57112.741 | 38807.225 | 8619.672 | 0 | 18890.272 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 209167000000 | 140881.976 | 25-MAY-19:00 | 57185.041 | 38824.77 | 9149.825 | 0 | 24987.561 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 219877000000 | 155371.456 | 25-JUN-20:30 | 56692.16 | 36787.756 | 10255.31 | 0 | 40901.451 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 243888000000 | 150501.422 | 21-JUL-20:15 | 51619.637 | 36857.935 | 10167.437 | 0 | 41121.633 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 238999000000 | 155669.33 | 11-AUG-19:45 | 57185.041 | 38824.77 | 9988.689 | 0 | 38936.051 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 217359000000 | 152065.744 | 02-SEP-19:15 | 57040.442 | 38772.136 | 9807.963 | 0 | 35710.425 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 207605000000 | 137625.289 | 06-OCT-19:15 | 57185.041 | 38824.77 | 8897.132 | 0 | 21983.567 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 195451000000 | 129526.455 | 21-NOV-20:00 | 57185.041 | 38824.77 | 8133.885 | 0 | 14647.98 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 224855000000 | 159147.539 | 11-DEC-07:15 | 37896.934 | 51279.599 | 7912.656 | 51323.571 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2586350000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 192945000000 | 129526.455 |  | 30422.587 | 36787.756 | 7912.656 | 0 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 243888000000 | 167379.617 |  | 57185.041 | 57998.833 | 10255.31 | 54069.943 | 41121.633 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 51132.15 | 12307.78 | 0 | 63439.94
Cost per Total Building Area ($/m2) | 10.01 | 2.41 | 0 | 12.42
Cost per Net Conditioned Building Area ($/m2) | 12.93 | 3.11 | 0 | 16.05

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4442.59 | 870.04 | 1123.74
Net Site Energy | 4442.59 | 870.04 | 1123.74
Total Source Energy | 11098.8 | 2173.59 | 2807.42
Net Source Energy | 11098.8 | 2173.59 | 2807.42
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 224.93 | 806.39 | 0 | 0 | 0 | 0
Cooling | 259.88 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 167.03 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 217.1 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 782.55 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2664.17 | 1778.42 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.329 | 0.346 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.227 | 0.24 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.227 | 0.24 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.227 | 0.24 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.227 | 0.24 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 2.956 | 0.487 | 0.409 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 2.956 | 0.487 | 0.409 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 2.956 | 0.487 | 0.409 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.487 | 0.409 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.487 | 0.409 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.487 | 0.409 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.487 | 0.409 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.487 | 0.409 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.487 | 0.409 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.487 | 0.409 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.487 | 0.409 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.487 | 0.409 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.487 | 0.409 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 2.956 | 0.487 | 0.409 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.487 | 0.409 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 2.956 | 0.487 | 0.409 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 2.96 | 0.487 | 0.409
North Total or Average |  |  | 72.38 | 2.96 | 0.487 | 0.409
Non-North Total or Average |  |  | 111.83 | 2.96 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1728.65 | 1362.51 | 366.14 | 0.79 | 2.89
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1778.1 | 1407.76 | 370.35 | 0.79 | 2.89
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1733.63 | 1367.18 | 366.45 | 0.79 | 2.89
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1577.33 | 1231.74 | 345.59 | 0.78 | 2.88
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1718.07 | 1355.52 | 362.55 | 0.79 | 2.89
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2412.98 | 1916.94 | 496.04 | 0.79 | 2.82
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8834.42 | 7055.66 | 1778.76 | 0.8 | 2.44
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7271.52 | 5807.44 | 1464.08 | 0.8 | 2.44
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8618.53 | 6883.24 | 1735.3 | 0.8 | 2.44
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2247.65 | 1795.1 | 452.55 | 0.8 | 2.86
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2091.72 | 1670.56 | 421.16 | 0.8 | 2.89
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8510.41 | 6796.88 | 1713.53 | 0.8 | 2.44
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2642.74 | 2110.63 | 532.1 | 0.8 | 2.78
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7856.47 | 6274.61 | 1581.86 | 0.8 | 2.44
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2096.66 | 1674.5 | 422.15 | 0.8 | 2.89
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2407.09 | 1911.62 | 495.48 | 0.79 | 2.82
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8940.76 | 7140.59 | 1800.18 | 0.8 | 2.44
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7470.52 | 5966.37 | 1504.15 | 0.8 | 2.44
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8923.47 | 7126.77 | 1796.69 | 0.8 | 2.44
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2313.77 | 1847.9 | 465.87 | 0.8 | 2.85
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2159.63 | 1724.8 | 434.83 | 0.8 | 2.88
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8224.78 | 6568.76 | 1656.02 | 0.8 | 2.44
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2170.21 | 1733.25 | 436.96 | 0.8 | 2.88
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8094.37 | 6464.61 | 1629.76 | 0.8 | 2.44
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2133.51 | 1703.94 | 429.57 | 0.8 | 2.88
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2335.59 | 1865.33 | 470.26 | 0.8 | 2.84
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8585.75 | 6857.06 | 1728.7 | 0.8 | 2.44
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7153.39 | 5713.09 | 1440.3 | 0.8 | 2.44
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8585.34 | 6856.73 | 1728.61 | 0.8 | 2.44
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2228.5 | 1779.8 | 448.7 | 0.8 | 2.86
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2227.48 | 1778.98 | 448.49 | 0.8 | 2.86
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8317.45 | 6642.78 | 1674.68 | 0.8 | 2.44
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2117.7 | 1691.31 | 426.39 | 0.8 | 2.89
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8231.9 | 6574.45 | 1657.45 | 0.8 | 2.44
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2178.34 | 1739.74 | 438.6 | 0.8 | 2.87
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8433.49 | 6735.45 | 1698.04 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4812.36 | 3843.42 | 968.94 | 0.8 | 4.04
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4459.17 | 3561.34 | 897.83 | 0.8 | 4.04
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4442.22 | 3547.8 | 894.42 | 0.8 | 4.04
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19657.75 | 13290.27 | 6367.47 | 0.68 | 3.45
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1233.35 | 985.02 | 248.33 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11359.75 | 7680.13 | 3679.61 | 0.68 | 3.65
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 877.81 | 646.22 | 231.59 | 0.74 | 3.83
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 6672.89 | 4851.35 | 1821.54 | 0.73 | 3.8
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 28423.26 | 22533.75 | 5889.51 | 0.79 | 3.75
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 3248.87 | 2196.51 | 1052.37 | 0.68 | 3.65
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7913.3 | 5722.39 | 2190.91 | 0.72 | 3.79
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 3043.09 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 2595.37 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 2624.98 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2822.65 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 0 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 30.68 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 51.74 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 172.95 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 1917.89 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 1941.33 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 2166.76 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 2155.71 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 1946.68 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 3163.57 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 6957.06 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 5445.04 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 6871.56 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 1967.75 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 1931.45 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 6638.66 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 1491.85 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 6771.8 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 1909.21 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 3203.54 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 7051.42 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 5624.6 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 7032.45 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 2002.02 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 1973.4 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 6994.16 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 1788.1 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 6972.24 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 1953.29 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 3554.06 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 8400.3 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 6731.43 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 8388.58 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2339.01 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2334.18 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 8388.13 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2244.88 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 8342.78 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2312.81 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 2886.31 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 2435.49 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 2462.09 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 2648.8 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 1523.25 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1355.89 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1372.12 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1395.16 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 13289.98 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 8151.32 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 7685.38 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 7662.97 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 41630.65 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1627.34 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 34662.09 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1429.94 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 12146.5 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 45125.15 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 9179.33 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 14043.52 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.11 | 9.92 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.46 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.56 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.21 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.1 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.17 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.56 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 64.58 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 67.08 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 64.84 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 57.72 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 64.33 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.72 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 339.71 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.44 | 279.61 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 331.41 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 86.43 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 80.43 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 327.25 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 101.62 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 302.11 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 80.62 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 91.43 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 343.8 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.45 | 287.27 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.54 | 343.14 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 88.97 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 83.04 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 316.27 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 83.45 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 311.25 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 82.04 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.14 | 89.81 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 330.15 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.43 | 275.07 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.52 | 330.13 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 85.69 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 85.65 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 319.83 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 81.43 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.5 | 316.54 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 83.76 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.41 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 7.94 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.03 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.09 | 8.64 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.97 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.42 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.48 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.55 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.51 | 590.93 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.29 | 337.2 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.27 | 312.45 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.27 | 311.27 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.79 | 918.2 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.07 | 86.42 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.46 | 530.61 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.04 | 51.06 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.32 | 376.47 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.69 | 1924.86 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.13 | 151.75 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.38 | 440.59 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.34 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 69362.3805 | 114.607 | 168.4888 | 0 | 0.0013 | 110711.2269 | 28943.1473
February | 60079.0703 | 99.3475 | 146.1968 | 0 | 0.0011 | 96063.8522 | 25077.0371
March | 57151.2076 | 94.8891 | 140.3196 | 0 | 0.001 | 92203.7768 | 23891.5668
April | 49648.4191 | 83.7922 | 126.3273 | 0 | 0.0009 | 83015.5568 | 20885.1008
May | 51233.1741 | 88.0303 | 135.4504 | 0 | 0.001 | 89017.5439 | 21701.1869
June | 52494.0556 | 91.6292 | 143.4483 | 0 | 0.0011 | 94279.7259 | 22372.1935
July | 57959.8696 | 101.9337 | 160.8716 | 0 | 0.0012 | 105734.0484 | 24774.6523
August | 56246.3662 | 98.7047 | 155.4139 | 0 | 0.0011 | 102146.0835 | 24021.6238
September | 51218.6922 | 89.078 | 138.9046 | 0 | 0.001 | 91292.0929 | 21797.5762
October | 51437.5489 | 88.1166 | 135.1283 | 0 | 0.001 | 88804.7755 | 21762.4391
November | 54179.0952 | 90.9668 | 136.3187 | 0 | 0.001 | 89579.3357 | 22745.8667
December | 65632.6451 | 108.6937 | 160.2408 | 0 | 0.0012 | 105292.6923 | 27410.6572
Annual Sum or Average | 676642.5244 | 1149.7888 | 1747.1091 | 0 | 0.0129 | 1148140 | 285383.0478
Minimum of Months | 49648.4191 | 83.7922 | 126.3273 | 0 | 0.0009 | 83015.5568 | 20885.1008
Maximum of Months | 69362.3805 | 114.607 | 168.4888 | 0 | 0.0013 | 110711.2269 | 28943.1473
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 256897000000 | 166526.126 | 09-JAN-07:15 | 37896.934 | 51279.599 | 7520.747 | 59094.068 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 222909000000 | 168284.209 | 02-FEB-07:15 | 37896.934 | 51279.599 | 7600.425 | 60772.472 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 213952000000 | 136871.028 | 09-MAR-06:15 | 30863.644 | 37264.076 | 7337.982 | 50670.547 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 192631000000 | 130408.547 | 15-APR-19:15 | 57040.442 | 38772.136 | 7757.359 | 0 | 16103.832 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 206559000000 | 138750.366 | 27-MAY-19:45 | 57040.442 | 38772.136 | 8464.29 | 0 | 23738.72 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 218769000000 | 157281.567 | 14-JUN-19:00 | 57185.041 | 38824.77 | 9530.362 | 0 | 41006.616 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 245348000000 | 162648.503 | 06-JUL-19:00 | 57185.041 | 38824.77 | 9851.587 | 0 | 46052.327 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 237022000000 | 165574.801 | 13-AUG-19:30 | 57112.741 | 38807.225 | 10031.068 | 0 | 48888.988 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 211836000000 | 148962.651 | 08-SEP-19:15 | 57185.041 | 38824.77 | 9077.326 | 0 | 33140.736 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 206065000000 | 141785.288 | 07-OCT-19:30 | 57040.442 | 38772.136 | 8701.737 | 0 | 26536.195 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 207862000000 | 135724.557 | 25-NOV-08:15 | 41071.521 | 57998.833 | 6570.517 | 29998.907 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 244324000000 | 160256.492 | 31-DEC-08:15 | 41071.521 | 57998.833 | 7318.986 | 53782.374 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2664170000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 192631000000 | 130408.547 |  | 30863.644 | 37264.076 | 6570.517 | 0 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 256897000000 | 168284.209 |  | 57185.041 | 57998.833 | 10031.068 | 60772.472 | 48888.988 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 40558.89 | 14140.71 | 0 | 54699.6
Cost per Total Building Area ($/m2) | 7.94 | 2.77 | 0 | 10.71
Cost per Net Conditioned Building Area ($/m2) | 10.26 | 3.58 | 0 | 13.84

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 5330.05 | 1043.84 | 1348.22
Net Site Energy | 5330.05 | 1043.84 | 1348.22
Total Source Energy | 13114.27 | 2568.3 | 3317.23
Net Source Energy | 13114.27 | 2568.3 | 3317.23
Area [m2]
Total Building Area | 5106.21
Net Conditioned Building Area | 3953.39
Unconditioned Building Area | 1152.82
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 557.94 | 1325.34 | 0 | 0 | 0 | 0
Cooling | 205.88 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 980.34 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 166.03 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 812.22 | 189.48 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 215.99 | 0 | 0 | 0 | 0 | 0
Pumps | 2.67 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 874.16 | 0 | 0 | 0 | 3470.09
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2941.07 | 2388.97 | 0 | 0 | 0 | 3470.09
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
CORRIDORFLR1 | 150.51 | Yes | 504.62 | 1 | 32.7 | 9.82 | 9.25 |  | 0
CORRIDORFLR2 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR3 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
CORRIDORFLR4 | 125.42 | Yes | 344.05 | 1 | 18.39 | 2.62 | 9.25 |  | 0
ELEVATORCOREFLR1 | 15.05 | No | 50.46 | 1 | 6.13 | 0 | 0 |  | 2133.5061
ELEVATORCOREFLR2 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR3 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
ELEVATORCOREFLR4 | 15.05 | No | 41.29 | 1 | 5.02 | 0 | 0 |  | 0
EMPLOYEELOUNGEFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 17.75 | 2.96 | 77.16
EXERCISECENTERFLR1 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 14.74 | 2.96 | 11.5
FRONTLOUNGEFLR1 | 163.06 | Yes | 546.7 | 1 | 94.02 | 14.83 | 14.1 | 3.08 | 15.4
FRONTOFFICEFLR1 | 130.44 | Yes | 437.33 | 1 | 53.14 | 6.58 | 21.63 | 13.04 | 12.9
FRONTSTAIRSFLR1 | 20.07 | Yes | 67.28 | 1 | 35.77 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR2 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR3 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTAIRSFLR4 | 20.07 | Yes | 55.05 | 1 | 29.26 | 0 | 8.82 |  | 0
FRONTSTORAGEFLR1 | 12.54 | Yes | 42.05 | 1 | 5.11 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR2 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR3 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
FRONTSTORAGEFLR4 | 12.54 | Yes | 34.41 | 1 | 4.18 | 0 | 4.84 |  | 0
GUESTROOM101 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM102 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM103 | 32.61 | Yes | 109.34 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM104 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM105 | 32.61 | Yes | 109.33 | 1 | 13.29 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM201 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM202_205 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM206_208 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM209_212 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM213 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM214 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM215_218 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM219 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM220_223 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM224 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM301 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM302_305 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM306_308 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM309_312 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM313 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM314 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM315_318 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM319 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM320_323 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM324 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM401 | 32.61 | Yes | 89.46 | 1 | 33.45 | 1.64 | 18.72 | 23.41 | 14.3
GUESTROOM402_405 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM406_408 | 105.36 | Yes | 289.02 | 1 | 35.12 | 6.7 | 18.72 | 21.74 | 14.3
GUESTROOM409_412 | 130.45 | Yes | 357.84 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM413 | 32.61 | Yes | 89.46 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM414 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM415_418 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM419 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.65 | 18.72 | 23.41 | 14.3
GUESTROOM420_423 | 130.44 | Yes | 357.81 | 1 | 43.48 | 6.58 | 18.72 | 23.41 | 14.3
GUESTROOM424 | 32.61 | Yes | 89.45 | 1 | 10.87 | 1.64 | 18.72 | 23.41 | 14.3
LAUNDRYROOMFLR1 | 97.83 | Yes | 327.99 | 1 | 39.86 | 4.94 | 11.19 | 8.89 | 206.1294
MECHANICALROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 10.33 |  | 0
MEETINGROOMFLR1 | 80.27 | Yes | 269.14 | 1 | 32.7 | 4.94 | 22.92 | 1.87 | 12.9
REARSTAIRSFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 8.82 |  | 0
REARSTAIRSFLR2 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR3 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTAIRSFLR4 | 20.07 | Yes | 55.06 | 1 | 29.27 | 0 | 8.82 |  | 0
REARSTORAGEFLR1 | 20.07 | Yes | 67.3 | 1 | 35.77 | 0 | 4.84 |  | 0
REARSTORAGEFLR2 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR3 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
REARSTORAGEFLR4 | 20.07 | Yes | 55.07 | 1 | 29.27 | 0 | 4.84 |  | 0
RESTROOMFLR1 | 32.61 | Yes | 109.34 | 1 | 13.29 | 0 | 11.84 | 32.61 | 10.76
ATTIC | 1092.62 | No | 1582.44 | 1 | 0 | 0 | 0 |  | 0
Total | 5106.21 |  | 13204.19 |  | 1694.58 | 184.21 | 12.5702 | 20.5 | 18.9918
Conditioned Total | 3953.39 |  | 11447.42 |  | 1673.4 | 184.21 | 16.2357 | 15.87 | 16.4078
Unconditioned Total | 1152.82 |  | 1756.76 |  | 21.18 | 0 | 0 |  | 27.8533
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
W_CORRIDORFLR1_10_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 10.22 | 0 | 90 | N
W_CORRIDORFLR1_16_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 6.13 | 270 | 90 | W
W_CORRIDORFLR1_20_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 10.22 | 180 | 90 | S
W_CORRIDORFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 6.13 | 90 | 90 | E
S_CORRIDORFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 150.51 | 270 | 180
W_CORRIDORFLR2_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 5.02 | 270 | 90 | W
W_CORRIDORFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 5.02 | 90 | 90 | E
W_CORRIDORFLR2_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 8.36 | 0 | 90 | N
W_CORRIDORFLR3_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 5.02 | 270 | 90 | W
W_CORRIDORFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 5.02 | 90 | 90 | E
W_CORRIDORFLR3_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 8.36 | 0 | 90 | N
W_CORRIDORFLR4_15_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 5.02 | 270 | 90 | W
W_CORRIDORFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 5.02 | 90 | 90 | E
W_CORRIDORFLR4_9_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 8.36 | 0 | 90 | N
W_ELEVATORCOREFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 6.13 | 0 | 90 | N
S_ELEVATORCOREFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 15.05 | 90 | 180
W_ELEVATORCOREFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 5.02 | 0 | 90 | N
W_ELEVATORCOREFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 5.02 | 0 | 90 | N
W_EMPLOYEELOUNGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 13.29 | 0 | 90 | N
S_EMPLOYEELOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_EXERCISECENTERFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 13.29 | 0 | 90 | N
S_EXERCISECENTERFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_FRONTLOUNGEFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 27.59 | 270 | 90 | W
W_FRONTLOUNGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 66.43 | 180 | 90 | S
S_FRONTLOUNGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 163.06 | 90 | 180
W_FRONTOFFICEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 53.14 | 0 | 90 | N
S_FRONTOFFICEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 130.44 | 90 | 180
W_FRONTSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 8.18 | 0 | 90 | N
W_FRONTSTAIRSFLR1_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 27.59 | 270 | 90 | W
S_FRONTSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_FRONTSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR2_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR3_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 22.58 | 270 | 90 | W
W_FRONTSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 6.69 | 0 | 90 | N
W_FRONTSTAIRSFLR4_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 22.58 | 270 | 90 | W
W_FRONTSTORAGEFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 5.11 | 0 | 90 | N
S_FRONTSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 12.54 | 90 | 180
W_FRONTSTORAGEFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 4.18 | 0 | 90 | N
W_FRONTSTORAGEFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 4.18 | 0 | 90 | N
W_GUESTROOM101_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 13.29 | 180 | 90 | S
S_GUESTROOM101_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM102_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 13.29 | 180 | 90 | S
S_GUESTROOM102_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM103_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 13.29 | 180 | 90 | S
S_GUESTROOM103_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM104_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 13.29 | 0 | 90 | N
S_GUESTROOM104_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM105_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 13.29 | 0 | 90 | N
S_GUESTROOM105_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_GUESTROOM201_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 22.58 | 270 | 90 | W
W_GUESTROOM201_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 10.87 | 180 | 90 | S
W_GUESTROOM202_205_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 43.48 | 180 | 90 | S
W_GUESTROOM206_208_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 35.12 | 180 | 90 | S
W_GUESTROOM209_212_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 43.48 | 180 | 90 | S
W_GUESTROOM213_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 10.87 | 180 | 90 | S
W_GUESTROOM214_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 10.87 | 0 | 90 | N
W_GUESTROOM215_218_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 43.48 | 0 | 90 | N
W_GUESTROOM219_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 10.87 | 0 | 90 | N
W_GUESTROOM220_223_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 43.48 | 0 | 90 | N
W_GUESTROOM224_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 10.87 | 0 | 90 | N
W_GUESTROOM301_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 22.58 | 270 | 90 | W
W_GUESTROOM301_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 10.87 | 180 | 90 | S
W_GUESTROOM302_305_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 43.48 | 180 | 90 | S
W_GUESTROOM306_308_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 35.12 | 180 | 90 | S
W_GUESTROOM309_312_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 43.48 | 180 | 90 | S
W_GUESTROOM313_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 10.87 | 180 | 90 | S
W_GUESTROOM314_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 10.87 | 0 | 90 | N
W_GUESTROOM315_318_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 43.48 | 0 | 90 | N
W_GUESTROOM319_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 10.87 | 0 | 90 | N
W_GUESTROOM320_323_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 43.48 | 0 | 90 | N
W_GUESTROOM324_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 10.87 | 0 | 90 | N
W_GUESTROOM401_4_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 22.58 | 270 | 90 | W
W_GUESTROOM401_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 10.87 | 180 | 90 | S
W_GUESTROOM402_405_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 43.48 | 180 | 90 | S
W_GUESTROOM406_408_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 35.12 | 180 | 90 | S
W_GUESTROOM409_412_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 43.48 | 180 | 90 | S
W_GUESTROOM413_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 10.87 | 180 | 90 | S
W_GUESTROOM414_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 10.87 | 0 | 90 | N
W_GUESTROOM415_418_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 43.48 | 0 | 90 | N
W_GUESTROOM419_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 10.87 | 0 | 90 | N
W_GUESTROOM420_423_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 43.48 | 0 | 90 | N
W_GUESTROOM424_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 10.87 | 0 | 90 | N
W_LAUNDRYROOMFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 39.86 | 0 | 90 | N
S_LAUNDRYROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 97.83 | 90 | 180
W_MECHANICALROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 13.29 | 180 | 90 | S
S_MECHANICALROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
W_MEETINGROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 32.7 | 180 | 90 | S
S_MEETINGROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 80.27 | 90 | 180
W_REARSTAIRSFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 27.59 | 90 | 90 | E
W_REARSTAIRSFLR1_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 8.18 | 0 | 90 | N
S_REARSTAIRSFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTAIRSFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR2_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR3_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 6.69 | 0 | 90 | N
W_REARSTAIRSFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 22.58 | 90 | 90 | E
W_REARSTAIRSFLR4_3_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 6.69 | 0 | 90 | N
W_REARSTORAGEFLR1_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 27.59 | 90 | 90 | E
W_REARSTORAGEFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 8.18 | 180 | 90 | S
S_REARSTORAGEFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 20.07 | 90 | 180
W_REARSTORAGEFLR2_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR2_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR3_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR3_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 6.69 | 180 | 90 | S
W_REARSTORAGEFLR4_2_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 22.58 | 90 | 90 | E
W_REARSTORAGEFLR4_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 6.69 | 180 | 90 | S
W_RESTROOMFLR1_5_0_0 | EXT-WALLS-STEELFRAME-RES | 0.22 | 0.256 | 0.266 | 13.29 | 180 | 90 | S
S_RESTROOMFLR1_0_0_0 | EXT-SLAB | 0.3 | 1.862 | 3.401 | 32.61 | 90 | 180
EASTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.174 | 0.182 | 11.33 | 270 | 180
SOUTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.174 | 0.182 | 33.28 | 135 | 180
WESTSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.174 | 0.182 | 11.33 | 225 | 180
NORTHSOFFIT | ATTIC-FLOOR-RES | 0.08 | 0.174 | 0.182 | 33.28 | 315 | 180
WESTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 270 | 18.45
EASTROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 100.98 | 90 | 18.45
SOUTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.35 | 180 | 18.6
NORTHROOF | ATTIC-ROOF-RES | 0.3 | 4.035 | 16.833 | 475.38 | 0 | 18.6
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
D_CORRIDORFLR1_16_0_0_0_0 | WINDOW-NONRES-FIXED | 4.44 | 4.44 | 2.956 | 0.616 | 0.541 | No | W_CORRIDORFLR1_16_0_0 | 270 | W
W_CORRIDORFLR1_20_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 2.956 | 0.616 | 0.541 | No | W_CORRIDORFLR1_20_0_0 | 180 | S
W_CORRIDORFLR1_2_0_0_0_0 | WINDOW-NONRES-FIXED | 2.69 | 2.69 | 2.956 | 0.616 | 0.541 | No | W_CORRIDORFLR1_2_0_0 | 90 | E
W_CORRIDORFLR2_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.616 | 0.541 | No | W_CORRIDORFLR2_15_0_0 | 270 | W
W_CORRIDORFLR2_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.616 | 0.541 | No | W_CORRIDORFLR2_2_0_0 | 90 | E
W_CORRIDORFLR3_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.616 | 0.541 | No | W_CORRIDORFLR3_15_0_0 | 270 | W
W_CORRIDORFLR3_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.616 | 0.541 | No | W_CORRIDORFLR3_2_0_0 | 90 | E
W_CORRIDORFLR4_15_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.616 | 0.541 | No | W_CORRIDORFLR4_15_0_0 | 270 | W
W_CORRIDORFLR4_2_0_0_0_0 | WINDOW-NONRES-FIXED | 1.31 | 1.31 | 2.956 | 0.616 | 0.541 | No | W_CORRIDORFLR4_2_0_0 | 90 | E
W_EMPLOYEELOUNGEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_EMPLOYEELOUNGEFLR1_3_0_0 | 0 | N
W_EXERCISECENTERFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_EXERCISECENTERFLR1_3_0_0 | 0 | N
W_FRONTLOUNGEFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.616 | 0.541 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.616 | 0.541 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.616 | 0.541 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_3 | WINDOW-NONRES-FIXED | 2.97 | 2.97 | 2.956 | 0.616 | 0.541 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTLOUNGEFLR1_5_0_0_0_4 | WINDOW-NONRES-FIXED | 2.96 | 2.96 | 2.956 | 0.616 | 0.541 | No | W_FRONTLOUNGEFLR1_5_0_0 | 180 | S
W_FRONTOFFICEFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_FRONTOFFICEFLR1_3_0_0_0_3 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_FRONTOFFICEFLR1_3_0_0 | 0 | N
W_GUESTROOM101_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM101_5_0_0 | 180 | S
W_GUESTROOM102_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM102_5_0_0 | 180 | S
W_GUESTROOM103_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM103_5_0_0 | 180 | S
W_GUESTROOM104_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM104_3_0_0 | 0 | N
W_GUESTROOM105_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM105_3_0_0 | 0 | N
W_GUESTROOM201_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM201_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM202_205_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM202_205_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM206_208_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM206_208_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM209_212_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM209_212_5_0_0 | 180 | S
W_GUESTROOM213_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM213_5_0_0 | 180 | S
W_GUESTROOM214_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM214_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM215_218_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM215_218_3_0_0 | 0 | N
W_GUESTROOM219_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM219_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM220_223_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM220_223_3_0_0 | 0 | N
W_GUESTROOM224_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM224_3_0_0 | 0 | N
W_GUESTROOM301_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM301_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM302_305_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM302_305_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_1 | WINDOW-RES-OPER | 3.41 | 3.41 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM306_308_5_0_0_0_2 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM306_308_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM309_312_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM309_312_5_0_0 | 180 | S
W_GUESTROOM313_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM313_5_0_0 | 180 | S
W_GUESTROOM314_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM314_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM315_318_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM315_318_3_0_0 | 0 | N
W_GUESTROOM319_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM319_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM320_323_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM320_323_3_0_0 | 0 | N
W_GUESTROOM324_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM324_3_0_0 | 0 | N
W_GUESTROOM401_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM401_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM402_405_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM402_405_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_1 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM406_408_5_0_0_0_2 | WINDOW-RES-OPER | 3.41 | 3.41 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM406_408_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM409_412_5_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM409_412_5_0_0 | 180 | S
W_GUESTROOM413_5_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM413_5_0_0 | 180 | S
W_GUESTROOM414_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM414_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM415_418_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM415_418_3_0_0 | 0 | N
W_GUESTROOM419_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM419_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_0 | WINDOW-RES-OPER | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_1 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_2 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM420_423_3_0_0_0_3 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM420_423_3_0_0 | 0 | N
W_GUESTROOM424_3_0_0_0_0 | WINDOW-RES-OPER | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_GUESTROOM424_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_LAUNDRYROOMFLR1_3_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_LAUNDRYROOMFLR1_3_0_0 | 0 | N
W_MEETINGROOMFLR1_5_0_0_0_0 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_1 | WINDOW-NONRES-FIXED | 1.64 | 1.64 | 2.956 | 0.616 | 0.541 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
W_MEETINGROOMFLR1_5_0_0_0_2 | WINDOW-NONRES-FIXED | 1.65 | 1.65 | 2.956 | 0.616 | 0.541 | No | W_MEETINGROOMFLR1_5_0_0 | 180 | S
Total or Average |  |  | 184.21 | 2.96 | 0.616 | 0.541
North Total or Average |  |  | 72.38 | 2.96 | 0.616 | 0.541
Non-North Total or Average |  |  | 111.83 | 2.96 | 0.616 | 0.541
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
GUESTROOM101 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1766.01 | 1410.43 | 355.58 | 0.8 | 2.9
GUESTROOM102 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1847.03 | 1475.14 | 371.89 | 0.8 | 2.9
GUESTROOM103 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1717.43 | 1371.64 | 345.8 | 0.8 | 2.9
GUESTROOM104 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1253.9 | 1001.43 | 252.47 | 0.8 | 2.9
GUESTROOM105 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1481.13 | 1182.91 | 298.22 | 0.8 | 2.9
GUESTROOM201 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2600.2 | 2076.67 | 523.54 | 0.8 | 2.79
GUESTROOM202_205 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9929.17 | 7929.98 | 1999.19 | 0.8 | 2.44
GUESTROOM206_208 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8408.96 | 6715.86 | 1693.1 | 0.8 | 2.44
GUESTROOM209_212 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9649.41 | 7706.56 | 1942.86 | 0.8 | 2.44
GUESTROOM213 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2465.17 | 1968.82 | 496.35 | 0.8 | 2.82
GUESTROOM214 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1988.75 | 1588.33 | 400.43 | 0.8 | 2.9
GUESTROOM215_218 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8182.07 | 6534.65 | 1647.42 | 0.8 | 2.44
GUESTROOM219 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2561.67 | 2045.89 | 515.78 | 0.8 | 2.8
GUESTROOM220_223 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7544.7 | 6025.62 | 1519.09 | 0.8 | 2.44
GUESTROOM224 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1979.75 | 1581.14 | 398.61 | 0.8 | 2.9
GUESTROOM301 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2605.68 | 2081.04 | 524.64 | 0.8 | 2.79
GUESTROOM302_305 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10072.25 | 8044.26 | 2028 | 0.8 | 2.44
GUESTROOM306_308 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8702.81 | 6950.55 | 1752.27 | 0.8 | 2.44
GUESTROOM309_312 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10047.58 | 8024.55 | 2023.03 | 0.8 | 2.44
GUESTROOM313 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2558.29 | 2043.19 | 515.1 | 0.8 | 2.8
GUESTROOM314 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2072.18 | 1654.96 | 417.22 | 0.8 | 2.9
GUESTROOM315_318 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7945.74 | 6345.91 | 1599.83 | 0.8 | 2.44
GUESTROOM319 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2085.47 | 1665.57 | 419.9 | 0.8 | 2.89
GUESTROOM320_323 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7817.02 | 6243.1 | 1573.92 | 0.8 | 2.44
GUESTROOM324 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2030.54 | 1621.7 | 408.84 | 0.8 | 2.9
GUESTROOM401 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2608.86 | 2083.58 | 525.28 | 0.8 | 2.79
GUESTROOM402_405 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10166.52 | 8119.55 | 2046.98 | 0.8 | 2.44
GUESTROOM406_408 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 8830 | 7052.13 | 1777.87 | 0.8 | 2.44
GUESTROOM409_412 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 10161.89 | 8115.85 | 2046.04 | 0.8 | 2.44
GUESTROOM413 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2580.25 | 2060.73 | 519.52 | 0.8 | 2.79
GUESTROOM414 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2100.66 | 1677.71 | 422.96 | 0.8 | 2.89
GUESTROOM415_418 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7979.87 | 6373.16 | 1606.7 | 0.8 | 2.44
GUESTROOM419 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2013.63 | 1608.2 | 405.43 | 0.8 | 2.9
GUESTROOM420_423 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7896.32 | 6306.44 | 1589.88 | 0.8 | 2.44
GUESTROOM424 PTAC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2048.59 | 1636.12 | 412.47 | 0.8 | 2.9
PSZ-HEATCOOL:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7421.24 | 5927.01 | 1494.23 | 0.8 | 4.04
PSZ-HEATCOOL:10_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4718.84 | 3768.73 | 950.11 | 0.8 | 4.04
PSZ-HEATCOOL:11_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4414.81 | 3525.91 | 888.9 | 0.8 | 4.04
PSZ-HEATCOOL:12_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 4269.52 | 3409.88 | 859.65 | 0.8 | 4.04
PSZ-HEATCOOL:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14591.85 | 11653.86 | 2937.99 | 0.8 | 4.01
PSZ-HEATCOOL:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 1133.1 | 904.96 | 228.14 | 0.8 | 4.04
PSZ-HEATCOOL:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 7881.45 | 6282.66 | 1598.79 | 0.8 | 4.03
PSZ-HEATCOOL:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 922.52 | 736.78 | 185.75 | 0.8 | 4.04
PSZ-HEATCOOL:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5071.43 | 4050.33 | 1021.11 | 0.8 | 4.04
PSZ-HEATCOOL:7_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26527.79 | 21186.56 | 5341.23 | 0.8 | 3.77
PSZ-HEATCOOL:8_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 2002.07 | 1598.97 | 403.11 | 0.8 | 4.04
PSZ-HEATCOOL:9_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 5400.22 | 4312.92 | 1087.31 | 0.8 | 4.04
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONTSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 4370.07 | 1
FRONTSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 3655.92 | 1
FRONTSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 3683.58 | 1
FRONTSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 3891.68 | 1
FRONTSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 99.29 | 1
FRONTSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 114.04 | 1
FRONTSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 131.17 | 1
FRONTSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 257.07 | 1
GUESTROOM101 PTAC HEAT COIL | Coil:Heating:Electric | 2516.29 | 1
GUESTROOM102 PTAC HEAT COIL | Coil:Heating:Electric | 2540.99 | 1
GUESTROOM103 PTAC HEAT COIL | Coil:Heating:Electric | 2767.77 | 1
GUESTROOM104 PTAC HEAT COIL | Coil:Heating:Electric | 2756.96 | 1
GUESTROOM105 PTAC HEAT COIL | Coil:Heating:Electric | 2548.47 | 1
GUESTROOM201 PTAC HEAT COIL | Coil:Heating:Electric | 4086.13 | 1
GUESTROOM202_205 PTAC HEAT COIL | Coil:Heating:Electric | 8990.11 | 1
GUESTROOM206_208 PTAC HEAT COIL | Coil:Heating:Electric | 7057.83 | 1
GUESTROOM209_212 PTAC HEAT COIL | Coil:Heating:Electric | 8896.87 | 1
GUESTROOM213 PTAC HEAT COIL | Coil:Heating:Electric | 2474.68 | 1
GUESTROOM214 PTAC HEAT COIL | Coil:Heating:Electric | 2438.75 | 1
GUESTROOM215_218 PTAC HEAT COIL | Coil:Heating:Electric | 8675.17 | 1
GUESTROOM219 PTAC HEAT COIL | Coil:Heating:Electric | 2024.71 | 1
GUESTROOM220_223 PTAC HEAT COIL | Coil:Heating:Electric | 8815.82 | 1
GUESTROOM224 PTAC HEAT COIL | Coil:Heating:Electric | 2418.38 | 1
GUESTROOM301 PTAC HEAT COIL | Coil:Heating:Electric | 4118.17 | 1
GUESTROOM302_305 PTAC HEAT COIL | Coil:Heating:Electric | 9056 | 1
GUESTROOM306_308 PTAC HEAT COIL | Coil:Heating:Electric | 7216.92 | 1
GUESTROOM309_312 PTAC HEAT COIL | Coil:Heating:Electric | 9036.56 | 1
GUESTROOM313 PTAC HEAT COIL | Coil:Heating:Electric | 2503.11 | 1
GUESTROOM314 PTAC HEAT COIL | Coil:Heating:Electric | 2474.07 | 1
GUESTROOM315_318 PTAC HEAT COIL | Coil:Heating:Electric | 8999.59 | 1
GUESTROOM319 PTAC HEAT COIL | Coil:Heating:Electric | 2322.6 | 1
GUESTROOM320_323 PTAC HEAT COIL | Coil:Heating:Electric | 8975.44 | 1
GUESTROOM324 PTAC HEAT COIL | Coil:Heating:Electric | 2453.98 | 1
GUESTROOM401 PTAC HEAT COIL | Coil:Heating:Electric | 4476.39 | 1
GUESTROOM402_405 PTAC HEAT COIL | Coil:Heating:Electric | 10432.91 | 1
GUESTROOM406_408 PTAC HEAT COIL | Coil:Heating:Electric | 8346.19 | 1
GUESTROOM409_412 PTAC HEAT COIL | Coil:Heating:Electric | 10421.34 | 1
GUESTROOM413 PTAC HEAT COIL | Coil:Heating:Electric | 2847.02 | 1
GUESTROOM414 PTAC HEAT COIL | Coil:Heating:Electric | 2842.08 | 1
GUESTROOM415_418 PTAC HEAT COIL | Coil:Heating:Electric | 10418.11 | 1
GUESTROOM419 PTAC HEAT COIL | Coil:Heating:Electric | 2786.77 | 1
GUESTROOM420_423 PTAC HEAT COIL | Coil:Heating:Electric | 10369.74 | 1
GUESTROOM424 PTAC HEAT COIL | Coil:Heating:Electric | 2820.33 | 1
REARSTAIRSFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 4213.04 | 1
REARSTAIRSFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 3496.3 | 1
REARSTAIRSFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 3520.65 | 1
REARSTAIRSFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 3716.82 | 1
REARSTORAGEFLR1 UNIT HEATER COIL | Coil:Heating:Electric | 2207 | 1
REARSTORAGEFLR2 UNIT HEATER COIL | Coil:Heating:Electric | 1891.7 | 1
REARSTORAGEFLR3 UNIT HEATER COIL | Coil:Heating:Electric | 1905.34 | 1
REARSTORAGEFLR4 UNIT HEATER COIL | Coil:Heating:Electric | 1927 | 1
PSZ-HEATCOOL:1_HEATC | Coil:Heating:Gas | 12985.87 | 0.8
PSZ-HEATCOOL:10_HEATC | Coil:Heating:Gas | 8818.53 | 0.8
PSZ-HEATCOOL:11_HEATC | Coil:Heating:Gas | 8403.12 | 0.8
PSZ-HEATCOOL:12_HEATC | Coil:Heating:Gas | 8204.52 | 0.8
PSZ-HEATCOOL:2_HEATC | Coil:Heating:Gas | 51957.25 | 0.8
PSZ-HEATCOOL:3_HEATC | Coil:Heating:Gas | 1548.48 | 0.8
PSZ-HEATCOOL:4_HEATC | Coil:Heating:Gas | 43176.76 | 0.8
PSZ-HEATCOOL:5_HEATC | Coil:Heating:Gas | 1877 | 0.8
PSZ-HEATCOOL:6_HEATC | Coil:Heating:Gas | 13582.77 | 0.8
PSZ-HEATCOOL:7_HEATC | Coil:Heating:Gas | 47064.34 | 0.8
PSZ-HEATCOOL:8_HEATC | Coil:Heating:Gas | 11051.31 | 0.8
PSZ-HEATCOOL:9_HEATC | Coil:Heating:Gas | 14939.23 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONTSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.15 | 13.76 | 1 | Unit Heater Fans
FRONTSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.12 | 11.51 | 1 | Unit Heater Fans
FRONTSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.12 | 11.6 | 1 | Unit Heater Fans
FRONTSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.13 | 12.25 | 1 | Unit Heater Fans
FRONTSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.31 | 1 | Unit Heater Fans
FRONTSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.36 | 1 | Unit Heater Fans
FRONTSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0 | 0.41 | 1 | Unit Heater Fans
FRONTSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.01 | 0.81 | 1 | Unit Heater Fans
GUESTROOM101 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 67.91 | 1 | PTAC Fan
GUESTROOM102 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.11 | 71.02 | 1 | PTAC Fan
GUESTROOM103 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.1 | 66.04 | 1 | PTAC Fan
GUESTROOM104 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.08 | 48.22 | 1 | PTAC Fan
GUESTROOM105 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.09 | 56.95 | 1 | PTAC Fan
GUESTROOM201 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 99.99 | 1 | PTAC Fan
GUESTROOM202_205 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.6 | 381.81 | 1 | PTAC Fan
GUESTROOM206_208 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.51 | 323.35 | 1 | PTAC Fan
GUESTROOM209_212 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.58 | 371.05 | 1 | PTAC Fan
GUESTROOM213 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 94.79 | 1 | PTAC Fan
GUESTROOM214 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.47 | 1 | PTAC Fan
GUESTROOM215_218 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.49 | 314.63 | 1 | PTAC Fan
GUESTROOM219 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 98.5 | 1 | PTAC Fan
GUESTROOM220_223 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.46 | 290.12 | 1 | PTAC Fan
GUESTROOM224 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 76.13 | 1 | PTAC Fan
GUESTROOM301 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.2 | 1 | PTAC Fan
GUESTROOM302_305 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 387.31 | 1 | PTAC Fan
GUESTROOM306_308 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 334.65 | 1 | PTAC Fan
GUESTROOM309_312 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 386.36 | 1 | PTAC Fan
GUESTROOM313 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.15 | 98.37 | 1 | PTAC Fan
GUESTROOM314 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 79.68 | 1 | PTAC Fan
GUESTROOM315_318 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 305.54 | 1 | PTAC Fan
GUESTROOM319 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 80.19 | 1 | PTAC Fan
GUESTROOM320_323 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.47 | 300.59 | 1 | PTAC Fan
GUESTROOM324 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.08 | 1 | PTAC Fan
GUESTROOM401 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 100.32 | 1 | PTAC Fan
GUESTROOM402_405 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 390.94 | 1 | PTAC Fan
GUESTROOM406_408 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.53 | 339.54 | 1 | PTAC Fan
GUESTROOM409_412 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.61 | 390.76 | 1 | PTAC Fan
GUESTROOM413 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.16 | 99.22 | 1 | PTAC Fan
GUESTROOM414 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.13 | 80.78 | 1 | PTAC Fan
GUESTROOM415_418 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 306.85 | 1 | PTAC Fan
GUESTROOM419 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 77.43 | 1 | PTAC Fan
GUESTROOM420_423 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.48 | 303.64 | 1 | PTAC Fan
GUESTROOM424 PTACFAN | Fan:OnOff | 0.52 | 331 | 0.12 | 78.78 | 1 | PTAC Fan
REARSTAIRSFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.14 | 13.27 | 1 | Unit Heater Fans
REARSTAIRSFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.12 | 11.01 | 1 | Unit Heater Fans
REARSTAIRSFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.12 | 11.08 | 1 | Unit Heater Fans
REARSTAIRSFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.13 | 11.7 | 1 | Unit Heater Fans
REARSTORAGEFLR1 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.95 | 1 | Unit Heater Fans
REARSTORAGEFLR2 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.96 | 1 | Unit Heater Fans
REARSTORAGEFLR3 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 6 | 1 | Unit Heater Fans
REARSTORAGEFLR4 UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.07 | 6.07 | 1 | Unit Heater Fans
PSZ-HEATCOOL:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.45 | 520.01 | 1 | Fan Energy
PSZ-HEATCOOL:10_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.29 | 330.65 | 1 | Fan Energy
PSZ-HEATCOOL:11_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.27 | 309.35 | 1 | Fan Energy
PSZ-HEATCOOL:12_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.26 | 299.17 | 1 | Fan Energy
PSZ-HEATCOOL:2_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.88 | 1004.19 | 1 | Fan Energy
PSZ-HEATCOOL:3_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.07 | 79.4 | 1 | Fan Energy
PSZ-HEATCOOL:4_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.47 | 549.98 | 1 | Fan Energy
PSZ-HEATCOOL:5_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.06 | 64.64 | 1 | Fan Energy
PSZ-HEATCOOL:6_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.31 | 355.36 | 1 | Fan Energy
PSZ-HEATCOOL:7_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.6 | 1825.61 | 1 | Fan Energy
PSZ-HEATCOOL:8_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.12 | 140.29 | 1 | Fan Energy
PSZ-HEATCOOL:9_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.33 | 378.39 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 179352 | 84.78 | 0.9
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 2 | 845000 | 0.78 | 0.34 | 0.65
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 85994.9736 | 101.5894 | 492.4473 | 0 | 0.0017 | 98819.3227 | 33383.3274
February | 71745.7408 | 84.5497 | 406.53 | 0 | 0.0014 | 81577.5306 | 27819.9894
March | 60475.4177 | 71.1547 | 340.2986 | 0 | 0.0012 | 68286.5825 | 23432.3921
April | 48160.9218 | 57.1476 | 281.0875 | 0 | 0.001 | 56406.7383 | 18735.0661
May | 46574.238 | 56.1368 | 290.0698 | 0 | 0.001 | 58212.4833 | 18252.0174
June | 46937.0309 | 57.0183 | 301.6214 | 0 | 0.001 | 60532.2443 | 18462.5409
July | 49907.1584 | 60.8232 | 324.8264 | 0 | 0.0011 | 65189.9075 | 19661.1271
August | 48363.8558 | 58.7808 | 311.4035 | 0 | 0.0011 | 62495.5125 | 19028.2888
September | 45435.7298 | 54.7202 | 282.0501 | 0 | 0.001 | 56602.8984 | 17799.0135
October | 51592.6882 | 61.2837 | 302.4555 | 0 | 0.001 | 60694.9611 | 20079.9038
November | 66450.0968 | 78.3649 | 377.6923 | 0 | 0.0013 | 75790.9444 | 25775.158
December | 78689.6737 | 92.8743 | 448.8347 | 0 | 0.0016 | 90067.2798 | 30534.3178
Annual Sum or Average | 700327.5256 | 834.4435 | 4159.3169 | 0 | 0.0143 | 834676.4053 | 272963.1425
Minimum of Months | 45435.7298 | 54.7202 | 281.0875 | 0 | 0.001 | 56406.7383 | 17799.0135
Maximum of Months | 85994.9736 | 101.5894 | 492.4473 | 0 | 0.0017 | 98819.3227 | 33383.3274
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 348201000000 | 223951.118 | 13-JAN-09:00 | 36531.279 | 35630.216 | 9390.161 | 131664.682 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 287447000000 | 223301.995 | 04-FEB-08:15 | 41071.521 | 57998.833 | 8438.525 | 105058.337 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 240615000000 | 172001.221 | 14-MAR-07:15 | 36531.279 | 40634.202 | 7673.892 | 76427.07 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 198755000000 | 126810.177 | 23-APR-20:45 | 56692.16 | 36787.756 | 7563.538 | 0 | 15031.945 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 205118000000 | 129681.834 | 29-MAY-19:00 | 57112.741 | 38807.225 | 8490.925 | 0 | 25186.164 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 213292000000 | 139295.807 | 23-JUN-19:00 | 57185.041 | 38824.77 | 9030.041 | 0 | 34171.176 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 229704000000 | 145927.332 | 29-JUL-19:00 | 57040.442 | 38772.136 | 9468.576 | 0 | 40561.4 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 220210000000 | 138633.499 | 19-AUG-20:00 | 56764.46 | 36822.846 | 8533.709 | 0 | 25777.707 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 199446000000 | 133730.789 | 09-SEP-19:45 | 57040.442 | 38772.136 | 7915.552 | 0 | 19267.881 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 213865000000 | 135616.429 | 22-OCT-07:15 | 41071.521 | 57998.833 | 6101.472 | 19709.825 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 267058000000 | 167664.604 | 23-NOV-08:15 | 41071.521 | 57998.833 | 6928.797 | 50930.675 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 317362000000 | 200368.007 | 29-DEC-08:00 | 36531.279 | 40634.202 | 8546.25 | 103921.498 | 0 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2941070000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 198755000000 | 126810.177 |  | 36531.279 | 35630.216 | 6101.472 | 0 | 0 | 0 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 348201000000 | 223951.118 |  | 57185.041 | 57998.833 | 9468.576 | 131664.682 | 40561.4 | 10650 | 84.778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 74301.66 | 9971.26 | 0 | 84272.92
Cost per Total Building Area ($/m2) | 14.55 | 1.95 | 0 | 16.5
Cost per Net Conditioned Building Area ($/m2) | 18.79 | 2.52 | 0 | 21.32

## Picture
DOE Commercial Building Benchmark - Small Hotel
First Floor
Upper Floors

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.5 | 0.4 | 0.4 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.8 | 0.9 | 0.8 | 0.6 | 0.3 | 8.55 | 58.7 | 3060.79
|  |  | Sat | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.4 | 0.4 | 0.3 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.6 | 0.7 | 0.7 | 0.7 | 0.6 | 0.3 | 7.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.7 | 0.8 | 0.6 | 0.5 | 0.3 | 8.1
GuestRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD | 0.22 | 0.17 | 0.11 | 0.11 | 0.11 | 0.22 | 0.44 | 0.56 | 0.44 | 0.44 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.28 | 0.67 | 0.89 | 1 | 0.89 | 0.67 | 0.33 | 9.51 | 58.28 | 3038.89
|  |  | Sat, Sun, Hol | 0.26 | 0.26 | 0.11 | 0.11 | 0.11 | 0.11 | 0.41 | 0.41 | 0.56 | 0.56 | 0.41 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.85 | 1 | 1 | 1 | 0.85 | 0.41 | 10.73
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Ltg_Sch | Fraction | Through 12/31 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5 | 19.7 | 118.2 | 6163.29
|  |  | Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.6 | 0.5 | 0.5 | 19.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.61 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.61 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 15.72 | 78.6 | 4098.43
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Ltg_Sch | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.4 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.4 | 0.15 | 0.15 | 0.05 | 0.05 | 12.6 | 71.2 | 3712.57
|  |  | Sat, Sun, Hol | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.15 | 0.3 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.3 | 0.15 | 0.15 | 0.05 | 0.05 | 8.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Ltg_Sch_Base | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.3 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.3 | 0.2 | 0.05 | 0 | 0 | 12.05 | 60.25 | 3141.61
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Storage_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MechanicalRoom_Ltg_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9 | 35.4 | 1845.86
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Ltg_Sch_Base | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 16 | 112 | 5840
LaundryRoom_Ltg_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 63 | 3285
Corridor_Ltg_Sch | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Exterior_Ltg_Sch | Fraction | Through 12/31 | All | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 12 | 84 | 4380
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.3 | 0.25 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.5 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.9 | 0.95 | 0.9 | 0.7 | 0.4 | 10.9 | 75.25 | 3923.75
|  |  | Sat | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.5 | 0.5 | 0.4 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.7 | 0.8 | 0.8 | 0.8 | 0.7 | 0.4 | 10.25
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.8 | 0.9 | 0.7 | 0.6 | 0.4 | 10.5
GuestRoom_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.62 | 0.9 | 0.43 | 0.43 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.26 | 0.51 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11 | 8.19 | 49.33 | 2572.21
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.3 | 0.62 | 0.9 | 0.62 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.29 | 0.43 | 0.51 | 0.49 | 0.66 | 0.7 | 0.35 | 0.11 | 8.38
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Eqp_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.68 | 1 | 1 | 1 | 1 | 0.32 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.21 | 9.02 | 45.1 | 2351.64
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Eqp_Sch | Fraction | Through 12/31 | WD | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.43 | 0.43 | 1 | 1 | 0.94 | 1 | 1 | 1 | 1 | 0.75 | 0.63 | 0.63 | 0.48 | 0.48 | 0.33 | 0.33 | 14.27 | 83.07 | 4331.51
|  |  | Sat, Sun, Hol | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.38 | 0.38 | 0.43 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.48 | 0.48 | 0.48 | 0.48 | 0.33 | 0.33 | 11.72
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Eqp_Sch | Fraction | Through 12/31 | WD | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08 | 66.48 | 3466.46
|  |  | Sat, Sun, Hol | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.19 | 0.19 | 0.25 | 1 | 1 | 0.86 | 0.86 | 1 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.25 | 0.19 | 0.11 | 0.11 | 0.11 | 0.11 | 11.08
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Elec_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Eqp_Gas_Sch | Fraction | Through 12/31 | WD, Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 40 | 2085.71
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.05 | 0.54 | 0.54 | 0.26 | 0.26 | 0.26 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.66 | 25.62 | 1335.9
ExerciseRoom_Eqp_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0 | 0.5 | 0.5 | 0.5 | 1 | 0.5 | 0.5 | 1 | 1 | 0.5 | 0.5 | 0 | 10.5 | 73.5 | 3832.5
Kitchen_Elec_Equip_SCH | Fraction | Through 12/31 | Weekday | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95 | 23.8 | 1241
|  |  | Sat | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
|  |  | SummerDesign | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 7.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 5.95
Kitchen_Gas_Equip_SCH | Fraction | Through 12/31 | WD, Sat | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65 | 21.9 | 1141.93
|  |  | SummerDesign | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05 | 0.1 | 0.15 | 0.2 | 0.15 | 0.25 | 0.25 | 0.25 | 0.2 | 0.15 | 0.2 | 0.3 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 | 0.1 | 0.05 | 3.65
Kitchen_Exhaust_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 0.16 | 2.72 | 19.04 | 992.8
BLDG_ELEVATORS | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.4 | 0.5 | 0.5 | 0.35 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.35 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.2 | 0.1 | 5.9 | 41.3 | 2153.5
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.8 | 0.9 | 0.9 | 13.9 | 96.4 | 5026.57
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.5 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 13.9
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.5 | 0.5 | 0.3 | 0.3 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 0.4 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 13
GuestRoom_Occ_Sch | Fraction | Through 12/31 | WD | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.43 | 0.43 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.31 | 0.54 | 0.54 | 0.54 | 0.77 | 0.77 | 0.89 | 1 | 1 | 15.19 | 90.86 | 4737.7
|  |  | Sat, Sun, Hol | 1 | 1 | 1 | 1 | 1 | 1 | 0.77 | 0.53 | 0.53 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.53 | 0.54 | 0.65 | 0.65 | 0.77 | 0.77 | 0.77 | 14.91
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Lobby_Occ_Sch | Fraction | Through 12/31 | WD | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 6.6 | 38.6 | 2012.71
|  |  | Sat, Sun, Hol | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 5.6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
Office_Occ_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.4 | 1 | 1 | 1 | 1 | 0.5 | 1 | 1 | 1 | 1 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 12.1 | 68.2 | 3556.14
|  |  | Sat, Sun, Hol | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 7.7
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
EmployeeLounge_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.7 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 3.1 | 16.85 | 878.61
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 1.35
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
MeetingRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2 | 19.2 | 1001.14
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.05 | 0.5 | 0.5 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 3.2
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
LaundryRoom_Occ_Sch | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17 | 7.02 | 366.04
|  |  | Sat, Sun, Hol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.09 | 0.18 | 0.18 | 0 | 0.18 | 0.18 | 0.18 | 0.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | SummerDesign, CustomDay1, CustomDay2 | [24 empty] | 24 | bar: 1 to 24
ExerciseRoom_Occ_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1 | 1 | 1 | 1 | 0.5 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0 | 14.5 | 101.5 | 5292.5
INFIL_SCH | fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
INFIL_HALF_ON_SCH | fraction | Through 12/31 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84 | 4380
INFIL_QUARTER_ON_SCH | fraction | Through 12/31 | All | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 6 | 42 | 2190
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.5 | 0.6 | 0.55 | 0.45 | 0.4 | 0.45 | 0.4 | 0.35 | 0.3 | 0.3 | 0.3 | 0.4 | 0.55 | 0.6 | 0.5 | 0.55 | 0.45 | 0.25 | 9 | 63.3 | 3300.64
|  |  | Sat, WinterDesign | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.4 | 0.5 | 0.5 | 0.5 | 0.45 | 0.5 | 0.5 | 0.45 | 0.4 | 0.4 | 0.35 | 0.4 | 0.55 | 0.55 | 0.5 | 0.55 | 0.4 | 0.3 | 9.3
|  |  | Sun, Hol, Other | 0.25 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.5 | 0.5 | 0.5 | 0.55 | 0.5 | 0.5 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.4 | 0.5 | 0.4 | 0.2 | 9
GuestRoom_SWH_Sch | Fraction | Through 12/31 | WD | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.55 | 0.4 | 0.4 | 0.6 | 0.45 | 0.25 | 8 | 40 | 2085.71
|  |  | Other | 0.2 | 0.15 | 0.15 | 0.15 | 0.2 | 0.25 | 0.35 | 0.6 | 0.8 | 0.55 | 0.4 | 0.3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.25 | 0.3 | 0.4 | 0.4 | 0.4 | 0.6 | 0.35 | 7.8
LaundryRoom_SWH_Sch | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 56 | 2920
Hours_of_operation | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | on/off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | All | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 3528 | 183960
HTGSETP_SCH_KEYCARD | Temperature | Through 12/31 | SummerDesign, WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504 | 0 | 0
|  |  | Other | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 486
CLGSETP_SCH | Temperature | Through 12/31 | All | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 4032 | 210240
CLGSETP_SCH_KEYCARD | Temperature | Through 12/31 | SummerDesign, WinterDesign | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 576 | 0 | 0
|  |  | Other | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 594
SemiHeated_HtgSP_Sch | Temperature | Through 12/31 | All | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 172.8 | 1209.6 | 63072
Base_OccGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
Base_OccGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
VacGuestRoom_HtgSP_Sch | Temperature | Through 12/31 | All | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 18.9 | 453.6 | 3175.2 | 165564
VacGuestRoom_ClgSP_Sch | Temperature | Through 12/31 | All | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | 559.2 | 3914.4 | 204108
CommonArea_HtgSP_Sch | Temperature | Through 12/31 | All | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 506.4 | 3544.8 | 184836
CommonArea_ClgSP_Sch | Temperature | Through 12/31 | All | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 573.6 | 4015.2 | 209364
Off During Unoccupied Period | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 70 | 3650
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SHWSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SHWSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720