## BuildingSummary
Building Summary Retail pre-1980 construction
|  | Value | Data Source
Program
| Building Name | Retail
| Available Fuel Types | gas, electricity
| Principal Building Activity | Retail
Form
| Total Floor Area (m2) | 2294 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.3
| Number of Floors | 1
Window Fraction (Window to Wall Ratio)
| South | 0.254
| East | 0
| North | 0
| West | 0
| Total | 0.071
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Back, CoreRetail, FrontRetail, PointofSale, FrontEntry
| Floor to Ceiling Height (m) | 6.1
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Steel-frame wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1177
| Net Dimensions - Total Area (m2) | 1093.1
| Wall to Skin Ratio | 0.34
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 2294
| Net Dimensions - Total Area (m2) | 2294
| Roof to Skin Ratio | 0.66
Window Dimensions (m2)
| South | 83.9
| East | 0
| North | 0
| West | 0
| Total Area (m2) | 83.9
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (m2) | 2294
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
| Internal Mass | 244.23
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 7764.95
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.27 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºC ) | N/A
| Water Consumption (L ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Back_Space | Yes | 1 | 379.89 | 2317.33 | 6.1 | 416.1704 | 0 | 27.8709 | 13.6303 | 12.558 | 8.0729 |  |  |  | 0.75 | 284.9175 |  | 1.4021
Core_Retail | Yes | 1 | 1600.48 | 9762.95 | 6.1 | 356.8603 | 0 | 6.1939 | 258.3982 | 36.2662 | 3.2292 |  |  |  | 1.5 | 2400.72 |  | 0.81826
Point_of_Sale | Yes | 1 | 150.81 | 919.94 | 6.1 | 189.8002 | 38.05 | 6.1939 | 24.3483 | 36.2662 | 21.5278 |  |  |  | 1.5 | 226.215 |  | 1.5111
Front_Retail | Yes | 1 | 150.81 | 919.94 | 6.1 | 189.8002 | 38.05 | 6.1939 | 24.3483 | 36.2662 | 3.2292 |  |  |  | 1.5 | 226.215 |  | 1.5111
Front_Entry | Yes | 1 | 12 | 73.2 | 6.1 | 24.38 | 7.83 | 6.1939 | 1.9374 | 36.2662 | 0 | [6 empty] | 1
Total Conditioned Zones |  |  | 2293.99 | 13993.36 |  | 1177.0111 | 83.9301 |  | 322.6626
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall | Steel-frame wall
| R-value (m2·K / W) | 0.7657 | 0.7657 | 0.7657 | 0.78247 | 0.7657 | 0.7657 | 0.78616 | 0.98912 | 0.95694 | 1.006 | 1.1287 | 1.0941 | 1.2151 | 1.2151 | 1.2953 | 1.4085
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 1.7575 | 2.045 | 1.9763 | 2.0704 | 2.5 | 2.3697 | 2.9851 | 2.9851 | 2.9326 | 2.9851
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 5.835 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525 | 3.525
| SHGC | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.54 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
| Visible transmittance | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.384 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316 | 0.316
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | 50.4662 | 52.0828 | 48.8604 | 57.861 | 28.6605 | 39.7574 | 26.8231 | 67.312 | 46.384 | 37.3347 | 88.8096 | 60.7477 | 100.0474 | 70.9891 | 104.4252 | 93.9989
| PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | 222.6739 | 230.0685 | 224.1857 | 227.7528 | 158.7504 | 187.5958 | 103.9332 | 201.3526 | 141.5066 | 120.111 | 191.1165 | 132.8638 | 217.4021 | 153.8242 | 230.5431 | 214.1717
| PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | 36.6687 | 39.2349 | 39.1983 | 37.7497 | 30.0162 | 34.3535 | 30.0164 | 37.6369 | 28.2856 | 30.4948 | 35.8962 | 26.2787 | 40.0017 | 31.6392 | 39.4951 | 42.1601
| PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | 32.6473 | 35.29 | 35.3487 | 34.0297 | 26.4744 | 30.4369 | 25.8977 | 34.0813 | 23.4525 | 26.6051 | 38.4444 | 26.2754 | 42.5126 | 31.6433 | 42.1174 | 42.1601
Heating (kW)
| FRONT_ENTRY UNIT HEATER COIL | 0.83541 | 1.8107 | 1.4054 | 2.236 | 1.0818 | 1.7798 | 1.3668 | 2.4367 | 2.137 | 1.8952 | 2.8123 | 2.4681 | 3.1395 | 3.0462 | 3.3089 | 4.3793
| PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 27.3281 | 55.3323 | 43.1497 | 66.3622 | 34.2136 | 53.1754 | 42.6068 | 74.2956 | 61.5197 | 57.8089 | 94.4844 | 79.4147 | 105.6709 | 99.9973 | 110.8594 | 150.1162
| PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 92.9463 | 160.091 | 121.9287 | 194.6014 | 96.6681 | 153.259 | 120.6346 | 225.3846 | 180.7251 | 172.4953 | 291.2292 | 238.7675 | 327.8318 | 306.9604 | 345.4109 | 474.2891
| PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 13.1118 | 27.2238 | 20.6242 | 33.0108 | 16.1583 | 25.7773 | 20.4834 | 37.4012 | 30.681 | 28.911 | 46.7251 | 38.8809 | 52.5833 | 49.5929 | 55.2941 | 74.766
| PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 13.1109 | 27.2238 | 20.6242 | 33.012 | 16.1598 | 25.7791 | 20.4837 | 37.4031 | 30.681 | 28.9106 | 46.7268 | 38.8772 | 52.5865 | 49.5979 | 55.2968 | 74.766
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | 3.11 | 3.11 | 3.19 | 3.15 | 3.43 | 3.27 | 3.58 | 3.11 | 3.35 | 3.52 | 3.33 | 4.13 | 3.33 | 3.93 | 3.35 | 3.89
| PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | 3.31 | 3.17 | 3.2 | 3.17 | 3.5 | 3.5 | 3.77 | 3.31 | 3.85 | 3.69 | 3.31 | 3.79 | 3.31 | 3.89 | 3.12 | 3.7
| PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | 3.33 | 3.35 | 3.4 | 3.38 | 3.53 | 3.5 | 3.56 | 3.38 | 3.6 | 3.56 | 3.35 | 3.6 | 3.16 | 3.56 | 3.39 | 3.35
| PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | 3.3 | 3.32 | 3.41 | 3.38 | 3.5 | 3.51 | 3.6 | 3.36 | 3.6 | 3.6 | 3.31 | 3.6 | 3.12 | 3.56 | 3.17 | 3.35
Heating Efficiency (%)
| FRONT_ENTRY UNIT HEATER COIL | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
HVAC Control - Economizer
| PSZ-AC:1_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:2_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:3_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb
| PSZ-AC:4_UNITARY_PACKAGE_FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| FRONT_ENTRY UNIT HEATERFAN | 0.04 | 0.08 | 0.06 | 0.1 | 0.05 | 0.08 | 0.06 | 0.1 | 0.11 | 0.08 | 0.12 | 0.13 | 0.14 | 0.15 | 0.15 | 0.19
| PSZ-AC:1_UNITARY_PACKAGE_FAN | 2.06 | 2.15 | 2.34 | 2.57 | 1.44 | 2.16 | 1.59 | 2.77 | 2.8 | 2.17 | 3.58 | 3.61 | 4.03 | 4.29 | 4.32 | 5.68
| PSZ-AC:2_UNITARY_PACKAGE_FAN | 8.97 | 9.26 | 9.31 | 9.17 | 7.62 | 8.96 | 5.91 | 8.11 | 8.38 | 6.54 | 7.7 | 7.64 | 8.75 | 9.29 | 9.49 | 12.94
| PSZ-AC:3_UNITARY_PACKAGE_FAN | 1.57 | 1.73 | 1.96 | 1.82 | 1.69 | 1.94 | 1.81 | 1.75 | 1.71 | 1.84 | 1.58 | 1.59 | 1.8 | 1.91 | 1.93 | 2.55
| PSZ-AC:4_UNITARY_PACKAGE_FAN | 1.32 | 1.48 | 1.71 | 1.57 | 1.45 | 1.67 | 1.56 | 1.52 | 1.42 | 1.61 | 1.58 | 1.59 | 1.8 | 1.91 | 1.94 | 2.55
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.08687 | 0.1219 | 0.098397 | 0.099659 | 0.13129 | 0.09926 | 0.1491 | 0.077235 | 0.037304 | 0.075563 | 0.091198 | 0.037306 | 0.061373 | 0.0752 | 0.060313 | 0.09519
| Total Cost ($/m2) | 25.69 | 33.63 | 27.28 | 24.79 | 27.41 | 24.79 | 28.53 | 17.9 | 8.33 | 14.91 | 20.95 | 8.27 | 14.39 | 17.18 | 13.65 | 23.6
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011402 | 0.0080453 | 0.0081371 | 0.0094954 | 0.0086287 | 0.0076265 | 0.008577 | 0.0096557 | 0.0068662 | 0.008418 | 0.0082965 | 0.0069006 | 0.0078766 | 0.0080645 | 0.0078639 | 0.0041218
| Total Cost ($/m2) | 0.09 | 1.12 | 0.94 | 2.8 | 0.76 | 1.53 | 2.18 | 5.08 | 2.62 | 3.99 | 5.87 | 3.67 | 7.31 | 6.02 | 9.2 | 8.13
Total Utility Costs
| Cost Intensity ($/m2) | 25.78 | 34.75 | 28.22 | 27.59 | 28.17 | 26.32 | 30.71 | 22.98 | 10.95 | 18.9 | 26.83 | 11.95 | 21.7 | 23.19 | 22.86 | 31.72
Energy - End Uses
Electricity (kWh)
| Heating | 38.8889 | 525 | 438.8889 | 1080.5556 | 350 | 633.3333 | 916.6667 | 1694.4444 | 1233.3333 | 1869.4444 | 2111.1111 | 1700 | 2675 | 2433.3333 | 3475 | 6358.3333
| Cooling | 219077.7778 | 166866.6667 | 166488.8889 | 101225 | 34505.5556 | 107272.2222 | 8375 | 69969.4444 | 49066.6667 | 10602.7778 | 47802.7778 | 29875 | 39338.8889 | 17230.5556 | 13852.7778 | 3730.5556
| Interior Lighting | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444 | 269744.4444
| Exterior Lighting | 16138.8889 | 16130.5556 | 16127.7778 | 16125 | 16113.8889 | 16111.1111 | 16119.4444 | 16108.3333 | 16113.8889 | 16083.3333 | 16111.1111 | 16102.7778 | 16100 | 16097.2222 | 16088.8889 | 15988.8889
| Interior Equipment | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225 | 55225
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 118052.7778 | 124319.4444 | 127938.8889 | 127280.5556 | 103013.8889 | 124033.3333 | 88483.3333 | 118991.6667 | 120930.5556 | 99133.3333 | 136083.3333 | 135958.3333 | 154925 | 163263.8889 | 160958.3333 | 217580.5556
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 678277.7778 | 632816.6667 | 635966.6667 | 570683.3333 | 478952.7778 | 573022.2222 | 438863.8889 | 531736.1111 | 512316.6667 | 452663.8889 | 527080.5556 | 508605.5556 | 538013.8889 | 523997.2222 | 519344.4444 | 568630.5556
Gas (MJ)
| Heating | 18230 | 318990 | 265660 | 676900 | 201580 | 459540 | 583510 | 1207410 | 874360 | 1086140 | 1623680 | 1221530 | 2128210 | 1711680 | 2684310 | 4524020
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 18230 | 318990 | 265660 | 676900 | 201580 | 459540 | 583510 | 1207410 | 874360 | 1086140 | 1623680 | 1221530 | 2128210 | 1711680 | 2684310 | 4524020
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 2460030 | 2597130 | 2555140 | 2731350 | 1925820 | 2522420 | 2163420 | 3121660 | 2718700 | 2715730 | 3521160 | 3052510 | 4065060 | 3598070 | 4553950 | 6571100
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0.061029 | 0.82389 | 0.68876 | 1.6957 | 0.54926 | 0.9939 | 1.4385 | 2.6591 | 1.9355 | 2.9338 | 3.313 | 2.6678 | 4.1979 | 3.8187 | 5.4534 | 9.9782
| Cooling (elec) | 343.8027 | 261.8669 | 261.274 | 158.8542 | 54.1502 | 168.3442 | 13.143 | 109.8043 | 77.0012 | 16.6391 | 75.0178 | 46.8834 | 61.7352 | 27.0402 | 21.7394 | 5.8544
| Interior Lighting (elec) | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148 | 423.3148
| Exterior Lighting (elec) | 25.3271 | 25.314 | 25.3096 | 25.3053 | 25.2878 | 25.2835 | 25.2965 | 25.2791 | 25.2878 | 25.2399 | 25.2835 | 25.2704 | 25.266 | 25.2617 | 25.2486 | 25.0917
| Interior Equipment (elec) | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656 | 86.6656
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 185.2624 | 195.0968 | 200.7768 | 199.7437 | 161.6616 | 194.6478 | 138.8585 | 186.7358 | 189.7785 | 155.5717 | 213.558 | 213.3619 | 243.1266 | 256.213 | 252.5948 | 341.4531
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1064.4336 | 993.0906 | 998.034 | 895.5837 | 751.6293 | 899.2541 | 688.717 | 834.4631 | 803.9878 | 710.3736 | 827.157 | 798.1639 | 844.3149 | 822.3183 | 815.0166 | 892.3622
Gas (MJ/m2)
| Heating (gas) | 7.9469 | 139.0547 | 115.807 | 295.0754 | 87.8731 | 200.3235 | 254.3647 | 526.3362 | 381.1525 | 473.472 | 707.7973 | 532.4914 | 927.7329 | 746.1584 | 1170.149 | 1972.1184
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 7.9469 | 139.0547 | 115.807 | 295.0754 | 87.8731 | 200.3235 | 254.3647 | 526.3362 | 381.1525 | 473.472 | 707.7973 | 532.4914 | 927.7329 | 746.1584 | 1170.149 | 1972.1184
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 1072.3804 | 1132.1453 | 1113.8409 | 1190.6547 | 839.5067 | 1099.5776 | 943.0817 | 1360.7993 | 1185.1403 | 1183.8456 | 1534.95 | 1330.6553 | 1772.0478 | 1568.4768 | 1985.1656 | 2864.485
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 157.1951 | 150.3208 | 133.8844 | 120.1525 | 127.9997 | 106.971 | 98.2571 | 104.4668 | 104.2423 | 100.5015 | 107.6043 | 107.1134 | 111.1519 | 112.5475 | 111.8696 | 123.1975
| Feb | 165.585 | 153.699 | 142.0783 | 126.7295 | 123.5247 | 115.5477 | 108.3691 | 104.017 | 112.4259 | 100.6058 | 107.1208 | 107.2096 | 110.6795 | 112.2337 | 111.8099 | 123.0273
| Mar | 167.6083 | 157.5558 | 163.0655 | 138.0029 | 124.2806 | 128.7855 | 97.8568 | 130.2045 | 113.6327 | 102.167 | 115.2703 | 119.2917 | 110.317 | 113.077 | 111.164 | 120.3695
| Apr | 176.0006 | 180.5439 | 169.0665 | 157.5152 | 134.0754 | 156.9604 | 116.9545 | 132.4531 | 134.794 | 109.1199 | 117.8373 | 126.2579 | 127.0701 | 108.3817 | 108.021 | 117.6116
| May | 187.125 | 192.8067 | 192.4003 | 171.2452 | 130.2576 | 169.4181 | 118.8837 | 153.888 | 141.4345 | 120.2664 | 151.5374 | 134.3682 | 181.384 | 130.546 | 129.7861 | 116.4364
| Jun | 193.4264 | 194.459 | 216.4848 | 185.2957 | 132.4702 | 191.2684 | 120.7088 | 184.7214 | 154.439 | 125.9389 | 179.383 | 145.9814 | 180.5117 | 154.1747 | 155.9846 | 146.4591
| Jul | 188.249 | 200.3936 | 213.7948 | 201.1762 | 139.6693 | 189.9639 | 129.992 | 191.0114 | 158.8005 | 136.9369 | 182.566 | 152.4988 | 187.669 | 155.0601 | 173.1332 | 153.7875
| Aug | 193.9499 | 199.5525 | 214.1443 | 190.8252 | 149.1612 | 187.8595 | 126.5312 | 192.6052 | 157.2726 | 132.5467 | 180.3204 | 154.2453 | 179.246 | 149.7381 | 171.5418 | 145.2803
| Sep | 186.3999 | 196.6071 | 202.1796 | 178.968 | 145.9903 | 183.6094 | 141.444 | 168.3713 | 144.4027 | 149.9061 | 156.3106 | 144.5723 | 155.7997 | 142.3805 | 144.4763 | 116.8768
| Oct | 182.6316 | 175.625 | 169.4602 | 163.5941 | 137.0259 | 157.5191 | 117.7959 | 145.9299 | 130.3897 | 108.0747 | 131.3452 | 133.2411 | 139.1318 | 125.1562 | 135.466 | 121.4804
| Nov | 169.1167 | 157.5833 | 154.2386 | 128.466 | 129.8052 | 118.8011 | 98.4452 | 134.846 | 108.6565 | 100.5636 | 130.9825 | 111.8766 | 110.3614 | 111.6555 | 111.5129 | 122.1418
| Dec | 158.64 | 153.6888 | 132.2975 | 116.641 | 129.4215 | 116.7894 | 98.1964 | 104.3543 | 104.4645 | 100.8102 | 107.1759 | 107.4401 | 110.8904 | 112.5605 | 111.7336 | 122.8292
Time of Peak Electrical Demand
| Jan | 24-JAN-13:00 | 03-JAN-13:00 | 28-JAN-14:00 | 23-JAN-15:00 | 26-JAN-13:00 | 18-JAN-16:49 | 04-JAN-17:00 | 17-JAN-17:00 | 12-JAN-17:00 | 31-JAN-17:00 | 26-JAN-17:00 | 05-JAN-17:00 | 04-JAN-17:00 | 06-JAN-17:00 | 11-JAN-17:00 | 13-JAN-09:09
| Feb | 25-FEB-13:00 | 23-FEB-15:09 | 28-FEB-15:00 | 18-FEB-15:09 | 13-FEB-11:00 | 08-FEB-15:50 | 15-FEB-15:00 | 23-FEB-17:00 | 14-FEB-15:00 | 11-FEB-17:00 | 03-FEB-17:00 | 14-FEB-17:00 | 01-FEB-17:00 | 22-FEB-17:00 | 01-FEB-17:00 | 03-FEB-09:09
| Mar | 13-MAR-14:00 | 25-MAR-12:50 | 17-MAR-14:00 | 28-MAR-14:00 | 31-MAR-14:09 | 31-MAR-14:00 | 01-MAR-17:00 | 09-MAR-15:00 | 02-MAR-15:09 | 29-MAR-16:00 | 31-MAR-14:00 | 30-MAR-15:00 | 01-MAR-17:00 | 30-MAR-16:00 | 08-MAR-17:00 | 02-MAR-17:00
| Apr | 01-APR-15:20 | 29-APR-14:30 | 01-APR-15:00 | 15-APR-15:00 | 11-APR-15:00 | 21-APR-14:00 | 29-APR-13:00 | 04-APR-15:00 | 22-APR-13:00 | 29-APR-14:00 | 07-APR-14:00 | 25-APR-14:00 | 01-APR-16:00 | 04-APR-08:09 | 04-APR-14:00 | 10-APR-08:09
| May | 24-MAY-14:00 | 26-MAY-14:00 | 27-MAY-15:30 | 15-MAY-14:00 | 30-MAY-12:00 | 31-MAY-15:00 | 17-MAY-13:00 | 31-MAY-15:00 | 31-MAY-15:00 | 04-MAY-14:00 | 30-MAY-15:00 | 23-MAY-15:00 | 27-MAY-14:00 | 16-MAY-16:00 | 31-MAY-15:00 | 18-MAY-08:09
| Jun | 27-JUN-14:00 | 13-JUN-14:00 | 28-JUN-15:00 | 19-JUN-14:00 | 28-JUN-12:00 | 27-JUN-15:00 | 15-JUN-12:00 | 30-JUN-14:00 | 29-JUN-14:09 | 28-JUN-14:00 | 08-JUN-12:00 | 27-JUN-15:00 | 29-JUN-14:00 | 30-JUN-14:00 | 14-JUN-15:00 | 20-JUN-16:00
| Jul | 13-JUL-14:00 | 18-JUL-12:00 | 11-JUL-15:00 | 03-JUL-14:00 | 24-JUL-14:30 | 24-JUL-15:00 | 03-JUL-12:00 | 25-JUL-12:00 | 31-JUL-14:00 | 24-JUL-14:00 | 13-JUL-14:00 | 17-JUL-15:00 | 15-JUL-14:00 | 21-JUL-16:00 | 08-JUL-15:00 | 29-JUL-16:00
| Aug | 21-AUG-14:39 | 31-AUG-14:09 | 01-AUG-15:00 | 17-AUG-13:00 | 08-AUG-12:00 | 05-AUG-12:00 | 15-AUG-11:00 | 17-AUG-14:00 | 01-AUG-14:20 | 07-AUG-14:00 | 04-AUG-15:00 | 30-AUG-13:00 | 25-AUG-15:00 | 09-AUG-16:00 | 12-AUG-14:00 | 15-AUG-16:00
| Sep | 07-SEP-13:00 | 16-SEP-13:00 | 09-SEP-15:20 | 11-SEP-13:00 | 25-SEP-14:00 | 01-SEP-14:00 | 28-SEP-14:00 | 09-SEP-14:30 | 02-SEP-14:00 | 02-SEP-15:39 | 05-SEP-14:00 | 02-SEP-14:00 | 14-SEP-14:00 | 01-SEP-16:00 | 07-SEP-14:00 | 29-SEP-08:09
| Oct | 06-OCT-14:39 | 06-OCT-15:00 | 14-OCT-13:00 | 12-OCT-15:00 | 05-OCT-14:09 | 03-OCT-14:00 | 13-OCT-14:00 | 20-OCT-14:00 | 13-OCT-14:00 | 17-OCT-15:30 | 31-OCT-14:09 | 05-OCT-14:00 | 07-OCT-14:00 | 06-OCT-15:00 | 07-OCT-14:00 | 27-OCT-08:09
| Nov | 07-NOV-15:09 | 03-NOV-14:39 | 13-NOV-15:20 | 22-NOV-15:09 | 20-NOV-12:00 | 10-NOV-15:09 | 14-NOV-16:00 | 04-NOV-13:00 | 08-NOV-17:10 | 16-NOV-17:00 | 02-NOV-14:00 | 10-NOV-13:00 | 27-NOV-17:00 | 27-NOV-17:00 | 24-NOV-17:00 | 02-NOV-08:09
| Dec | 16-DEC-12:00 | 02-DEC-12:00 | 09-DEC-15:30 | 01-DEC-15:30 | 19-DEC-12:00 | 05-DEC-14:50 | 02-DEC-17:00 | 14-DEC-17:00 | 28-DEC-17:00 | 13-DEC-17:00 | 13-DEC-17:00 | 01-DEC-17:00 | 30-DEC-17:00 | 11-DEC-17:00 | 30-DEC-17:00 | 29-DEC-09:09
Source Energy
| Total Source Energy (GJ) | 8119.36 | 8622.54 | 7531.74 | 7650.37 | 5556.63 | 7880.74 | 5527.01 | 8163.85 | 7074.33 | 4024.8 | 8501.55 | 7409.09 | 8980.95 | 8426.24 | 9357.23 | 12252.38
| Total Source Energy (MJ/m2) | 3539.4 | 3758.75 | 3283.24 | 3334.96 | 2422.25 | 3435.38 | 2409.34 | 3558.79 | 3083.85 | 1754.5 | 3706 | 3229.78 | 3914.99 | 3673.18 | 4079.01 | 5341.07
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emissions
| Carbon Equivalent (kg) | 186346.2286 | 216835.0071 | 196773.6261 | 187997.5323 | 59608.385 | 201552.798 | 61810.3647 | 165264.6955 | 225047.5239 | 52555.3341 | 310291.6938 | 229791.4072 | 222535.5488 | 222354.3964 | 226173.614 | 241586.1383
| CO2 (kg) | 431683.2426 | 546286.5246 | 465327.0932 | 434242.1259 | 159941.736 | 481695.0507 | 167331.436 | 384691.3225 | 533197.9188 | 134905.7605 | 732965.3836 | 547751.8331 | 535436.7861 | 534555.0582 | 549678.2148 | 636518.6561
| NOX (kg) | 760.5064 | 711.2872 | 775.6508 | 802.4391 | 137.4212 | 772.4181 | 144.7817 | 700.4896 | 896.9469 | 177.2111 | 1257.4173 | 907.168 | 875.4032 | 871.5483 | 874.8251 | 716.1335
| SO2 (kg) | 2903.3063 | 3018.6175 | 2557.4253 | 2003.2784 | 1393.7517 | 3152.2022 | 1277.1956 | 1941.3722 | 2237.4196 | 350.1636 | 3552.5341 | 2221.3004 | 1270.3671 | 1399.5939 | 1226.4576 | 2895.775
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0132 | 0.0085 | 0.007 | 0.0074 | 0.0006 | 0.006 | 0.0006 | 0.0079 | 0.0088 | 0.0015 | 0.0109 | 0.0088 | 0.0095 | 0.0099 | 0.0092 | 0.0103
| Water Environmental Factors (m3) | 359.3232 | 1029.67 | 18891 | 3563.12 | 8409.35 | 15720.3 | 7705.45 | 120.724 | 2326.33 | 4624.77 | 817.7334 | 2309.47 | 834.6949 | 33192.2 | 805.7333 | 580.9596

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2460.03 | 1072.38 | 1072.38
Net Site Energy | 2460.03 | 1072.38 | 1072.38
Total Source Energy | 8119.36 | 3539.4 | 3539.4
Net Source Energy | 8119.36 | 3539.4 | 3539.4
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0.14 | 18.23 | 0 | 0 | 0 | 0
Cooling | 788.68 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 971.08 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.1 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 424.99 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2441.8 | 18.23 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 12.55 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 36.25 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 36.25 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 7.83 | 7.83 | 5.835 | 0.54 | 0.384 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 50466.19 | 34278.4 | 16187.79 | 0.68 | 3.11
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 222673.91 | 150546.09 | 72127.82 | 0.68 | 3.31
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 36668.71 | 25382.01 | 11286.7 | 0.69 | 3.33
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 32647.3 | 22085.68 | 10561.62 | 0.68 | 3.3
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 835.41 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27328.11 | 0.78
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 92946.29 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13111.83 | 0.78
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 13110.94 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.04 | 3.33 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.06 | 2251.13 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 8.97 | 16822.15 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.57 | 1792.8 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.32 | 1500.21 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 31623.5568 | 55.4263 | 210.4377 | 0 | 0.001 | 26044.2858 | 13622.4331
February | 29167.2298 | 51.2864 | 195.3925 | 0 | 0.0009 | 24182.3823 | 12580.8793
March | 33633.5932 | 59.1384 | 225.3021 | 0 | 0.001 | 27884.0775 | 14507.2452
April | 34645.7083 | 61.0845 | 233.3922 | 0 | 0.0011 | 28885.4644 | 14960.4837
May | 38610.764 | 68.0942 | 260.2506 | 0 | 0.0012 | 32209.5634 | 16674.527
June | 39664.6871 | 69.9529 | 267.3544 | 0 | 0.0012 | 33088.7587 | 17129.6765
July | 41490.1306 | 73.1722 | 279.6585 | 0 | 0.0013 | 34611.5655 | 17918.0164
August | 42137.6637 | 74.3142 | 284.0231 | 0 | 0.0013 | 35151.7455 | 18197.6615
September | 38968.8443 | 68.7257 | 262.6641 | 0 | 0.0012 | 32508.2783 | 16829.1684
October | 37264.0799 | 65.7189 | 251.1716 | 0 | 0.0011 | 31085.9143 | 16092.9216
November | 33178.8414 | 58.5027 | 223.5455 | 0 | 0.001 | 27666.799 | 14327.5147
December | 31298.1435 | 55.09 | 210.1139 | 0 | 0.001 | 26004.3894 | 13505.7011
Annual Sum or Average | 431683.2426 | 760.5064 | 2903.3063 | 0 | 0.0132 | 359323.2239 | 186346.2286
Minimum of Months | 29167.2298 | 51.2864 | 195.3925 | 0 | 0.0009 | 24182.3823 | 12580.8793
Maximum of Months | 42137.6637 | 74.3142 | 284.0231 | 0 | 0.0013 | 35151.7455 | 18197.6615
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 176985000000 | 157195.088 | 24-JAN-13:00 | 66738.465 | 10771.038 | 22366.288 | 0 | 57319.298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 164333000000 | 165585.025 | 25-FEB-13:00 | 66738.465 | 10771.038 | 22366.288 | 0 | 65709.235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 189488000000 | 167608.255 | 13-MAR-14:00 | 66738.465 | 10771.038 | 22366.288 | 0 | 67732.465 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 196293000000 | 176000.608 | 01-APR-15:20 | 66738.465 | 10771.038 | 22366.288 | 0 | 76124.817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 218882000000 | 187124.96 | 24-MAY-14:00 | 66738.465 | 10771.038 | 22366.288 | 0 | 87249.169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 224857000000 | 193426.371 | 27-JUN-14:00 | 66738.465 | 10771.038 | 22366.288 | 0 | 93550.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 235205000000 | 188248.962 | 13-JUL-14:00 | 66738.465 | 10771.038 | 22366.288 | 0 | 88373.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 238876000000 | 193949.941 | 21-AUG-14:39 | 66738.465 | 10771.038 | 22366.288 | 0 | 94074.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 220912000000 | 186399.87 | 07-SEP-13:00 | 66738.465 | 10771.038 | 22366.288 | 0 | 86524.08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 211246000000 | 182631.551 | 06-OCT-14:39 | 66738.465 | 10771.038 | 22366.288 | 0 | 82755.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 188011000000 | 169116.748 | 07-NOV-15:09 | 66738.465 | 10771.038 | 22366.288 | 0 | 69240.957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 176714000000 | 158639.962 | 16-DEC-12:00 | 66738.465 | 10771.038 | 22366.288 | 0 | 58764.172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2441800000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 164333000000 | 157195.088 |  | 66738.465 | 10771.038 | 22366.288 | 0 | 57319.298 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 238876000000 | 193949.941 |  | 66738.465 | 10771.038 | 22366.288 | 0 | 94074.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 58922.08 | 207.86 | 0 | 59129.94
Cost per Total Building Area ($/m2) | 25.69 | 0.09 | 0 | 25.78
Cost per Net Conditioned Building Area ($/m2) | 25.69 | 0.09 | 0 | 25.78

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2597.13 | 1132.14 | 1132.14
Net Site Energy | 2597.13 | 1132.14 | 1132.14
Total Source Energy | 8622.54 | 3758.75 | 3758.75
Net Source Energy | 8622.54 | 3758.75 | 3758.75
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 1.89 | 318.99 | 0 | 0 | 0 | 0
Cooling | 600.72 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 971.08 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.07 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 447.55 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2278.14 | 318.99 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 12.55 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 36.25 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 36.25 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 7.83 | 7.83 | 5.835 | 0.54 | 0.384 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 52082.82 | 35555.9 | 16526.92 | 0.68 | 3.11
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 230068.52 | 155545.47 | 74523.05 | 0.68 | 3.17
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 39234.85 | 27466.07 | 11768.78 | 0.7 | 3.35
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 35289.99 | 24234.64 | 11055.35 | 0.69 | 3.32
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1810.67 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 55332.31 | 0.78
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 160090.96 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27223.79 | 0.78
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 27223.79 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.23 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.15 | 2355.48 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 9.26 | 17380.78 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.73 | 1975.87 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.48 | 1689.26 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 40774.2683 | 51.6351 | 204.9327 | 0 | 0.0006 | 69897.1197 | 15996.835
February | 36306.377 | 45.9891 | 182.6451 | 0 | 0.0005 | 62295.44 | 14245.5087
March | 39750.8182 | 51.6122 | 217.6213 | 0 | 0.0006 | 74231.0762 | 15759.4275
April | 41463.3403 | 54.3748 | 234.5456 | 0 | 0.0007 | 80006.4265 | 16507.842
May | 48724.5969 | 64.0165 | 277.2922 | 0 | 0.0008 | 94588.319 | 19414.1597
June | 53322.3695 | 70.0874 | 303.88 | 0 | 0.0009 | 103657.956 | 21250.0105
July | 56566.0899 | 74.351 | 322.3659 | 0 | 0.0009 | 109963.7489 | 22542.6979
August | 56453.0462 | 74.202 | 321.7165 | 0 | 0.0009 | 109742.2269 | 22497.6002
September | 49606.9129 | 65.2027 | 282.6911 | 0 | 0.0008 | 96430.0772 | 19769.1911
October | 45133.2082 | 59.2153 | 255.6954 | 0 | 0.0007 | 87221.0113 | 17972.5239
November | 38564.6175 | 50.287 | 214.1368 | 0 | 0.0006 | 73043.4611 | 15316.8494
December | 39620.8796 | 50.3143 | 201.095 | 0 | 0.0006 | 68588.8458 | 15562.3612
Annual Sum or Average | 546286.5246 | 711.2872 | 3018.6175 | 0 | 0.0085 | 1029670 | 216835.0071
Minimum of Months | 36306.377 | 45.9891 | 182.6451 | 0 | 0.0005 | 62295.44 | 14245.5087
Maximum of Months | 56566.0899 | 74.351 | 322.3659 | 0 | 0.0009 | 109963.7489 | 22542.6979
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 154648000000 | 150320.752 | 03-JAN-13:00 | 66738.465 | 10771.038 | 23401.398 | 0 | 49409.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 137829000000 | 153699.043 | 23-FEB-15:09 | 66738.465 | 10771.038 | 23401.398 | 0 | 52788.143 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 164236000000 | 157555.811 | 25-MAR-12:50 | 66738.465 | 10771.038 | 23401.398 | 0 | 56644.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 177014000000 | 180543.88 | 29-APR-14:30 | 66738.465 | 10771.038 | 23401.398 | 0 | 79632.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 209277000000 | 192806.713 | 26-MAY-14:00 | 66738.465 | 10771.038 | 23401.398 | 0 | 91895.813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 229343000000 | 194459.022 | 13-JUN-14:00 | 66738.465 | 10771.038 | 23401.398 | 0 | 93548.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 243295000000 | 200393.55 | 18-JUL-12:00 | 66738.465 | 10771.038 | 23401.398 | 0 | 99482.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 242805000000 | 199552.512 | 31-AUG-14:09 | 66738.465 | 10771.038 | 23401.398 | 0 | 98641.613 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 213352000000 | 196607.148 | 16-SEP-13:00 | 66738.465 | 10771.038 | 23401.398 | 0 | 95696.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 192977000000 | 175625.045 | 06-OCT-15:00 | 66738.465 | 10771.038 | 23401.398 | 0 | 74714.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 161609000000 | 157583.261 | 03-NOV-14:39 | 66738.465 | 10771.038 | 23401.398 | 0 | 56672.361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 151753000000 | 153688.796 | 02-DEC-12:00 | 66738.465 | 10771.038 | 23401.398 | 0 | 52777.896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2278140000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 137829000000 | 150320.752 |  | 66738.465 | 10771.038 | 23401.398 | 0 | 49409.852 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 243295000000 | 200393.55 |  | 66738.465 | 10771.038 | 23401.398 | 0 | 99482.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 77141.82 | 2566.37 | 0 | 79708.19
Cost per Total Building Area ($/m2) | 33.63 | 1.12 | 0 | 34.75
Cost per Net Conditioned Building Area ($/m2) | 33.63 | 1.12 | 0 | 34.75

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2555.14 | 1113.84 | 1113.84
Net Site Energy | 2555.14 | 1113.84 | 1113.84
Total Source Energy | 7531.74 | 3283.24 | 3283.24
Net Source Energy | 7531.74 | 3283.24 | 3283.24
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 1.58 | 265.66 | 0 | 0 | 0 | 0
Cooling | 599.36 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 971.08 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.06 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 460.58 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2289.48 | 265.66 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 12.55 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 36.25 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 36.25 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 7.83 | 7.83 | 5.835 | 0.54 | 0.384 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 48860.4 | 35303.65 | 13556.75 | 0.72 | 3.19
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 224185.73 | 153291.3 | 70894.42 | 0.68 | 3.2
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 39198.35 | 28831.9 | 10366.45 | 0.74 | 3.4
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 35348.67 | 25624.06 | 9724.61 | 0.72 | 3.41
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1405.36 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 43149.69 | 0.78
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 121928.74 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20624.15 | 0.78
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20624.16 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.82 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.34 | 2559.73 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 9.31 | 17467.5 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.96 | 2145.1 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.71 | 1944.6 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 32658.3313 | 52.5223 | 165.6311 | 0 | 0.0005 | 1223380 | 13616.5634
February | 29890.2068 | 48.1046 | 151.8387 | 0 | 0.0004 | 1121510 | 12465.8669
March | 34729.317 | 57.7907 | 190.1523 | 0 | 0.0005 | 1404600 | 14675.9915
April | 35921.579 | 60.3473 | 200.8229 | 0 | 0.0005 | 1483450 | 15237.7281
May | 40460.5403 | 68.3204 | 228.7139 | 0 | 0.0006 | 1689490 | 17198.2926
June | 46269.8006 | 78.2021 | 262.0759 | 0 | 0.0007 | 1935940 | 19674.9164
July | 49419.6474 | 83.5272 | 279.9277 | 0 | 0.0008 | 2067810 | 21014.4502
August | 49113.664 | 83.0101 | 278.1945 | 0 | 0.0008 | 2055010 | 20884.3386
September | 43804.665 | 74.036 | 248.1154 | 0 | 0.0007 | 1832820 | 18626.7181
October | 37526.6183 | 63.19 | 210.8545 | 0 | 0.0006 | 1557560 | 15933.372
November | 32067.5771 | 53.3032 | 175.1573 | 0 | 0.0005 | 1293830 | 13545.2988
December | 33465.1465 | 53.297 | 165.941 | 0 | 0.0005 | 1225640 | 13900.0894
Annual Sum or Average | 465327.0932 | 775.6508 | 2557.4253 | 0 | 0.007 | 18891000 | 196773.6261
Minimum of Months | 29890.2068 | 48.1046 | 151.8387 | 0 | 0.0004 | 1121510 | 12465.8669
Maximum of Months | 49419.6474 | 83.5272 | 279.9277 | 0 | 0.0008 | 2067810 | 21014.4502
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 148266000000 | 133884.389 | 28-JAN-14:00 | 66738.465 | 10771.038 | 24116.926 | 0 | 32257.961 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 135920000000 | 142078.308 | 28-FEB-15:00 | 66738.465 | 10771.038 | 24116.926 | 0 | 40451.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 170230000000 | 163065.518 | 17-MAR-14:00 | 66738.465 | 10771.038 | 24116.926 | 0 | 61439.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 179786000000 | 169066.528 | 01-APR-15:00 | 66738.465 | 10771.038 | 24116.926 | 0 | 67440.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 204757000000 | 192400.348 | 27-MAY-15:30 | 66738.465 | 10771.038 | 24116.926 | 0 | 90773.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 234625000000 | 216484.834 | 28-JUN-15:00 | 66738.465 | 10771.038 | 24116.926 | 0 | 114858.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 250607000000 | 213794.777 | 11-JUL-15:00 | 66738.465 | 10771.038 | 24116.926 | 0 | 112168.349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 249055000000 | 214144.321 | 01-AUG-15:00 | 66738.465 | 10771.038 | 24116.926 | 0 | 112517.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 222127000000 | 202179.641 | 09-SEP-15:20 | 66738.465 | 10771.038 | 24116.926 | 0 | 100553.213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 188767000000 | 169460.175 | 14-OCT-13:00 | 66738.465 | 10771.038 | 24116.926 | 0 | 67833.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 156805000000 | 154238.584 | 13-NOV-15:20 | 66738.465 | 10771.038 | 24116.926 | 0 | 52612.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 148540000000 | 132297.52 | 09-DEC-15:30 | 66738.465 | 10771.038 | 24116.926 | 0 | 30671.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2289480000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 135920000000 | 132297.52 |  | 66738.465 | 10771.038 | 24116.926 | 0 | 30671.092 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 250607000000 | 216484.834 |  | 66738.465 | 10771.038 | 24116.926 | 0 | 114858.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 62577.1 | 2161.71 | 0 | 64738.81
Cost per Total Building Area ($/m2) | 27.28 | 0.94 | 0 | 28.22
Cost per Net Conditioned Building Area ($/m2) | 27.28 | 0.94 | 0 | 28.22

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2731.35 | 1190.66 | 1190.66
Net Site Energy | 2731.35 | 1190.66 | 1190.66
Total Source Energy | 7650.37 | 3334.96 | 3334.96
Net Source Energy | 7650.37 | 3334.96 | 3334.96
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 3.89 | 676.9 | 0 | 0 | 0 | 0
Cooling | 364.41 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 971.08 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.05 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 458.21 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2054.46 | 676.9 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 12.55 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 36.25 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 36.25 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.278 | 1.58 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 7.83 | 7.83 | 5.835 | 0.54 | 0.384 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 57860.96 | 40582.94 | 17278.03 | 0.7 | 3.15
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 227752.79 | 153979.84 | 73772.95 | 0.68 | 3.17
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 37749.68 | 27337.75 | 10411.93 | 0.72 | 3.38
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 34029.75 | 24214.2 | 9815.55 | 0.71 | 3.38
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 2236.03 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 66362.18 | 0.78
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 194601.44 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 33010.79 | 0.78
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 33012.04 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.24 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.57 | 2811.31 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 9.17 | 17205.84 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.82 | 1988.8 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.57 | 1787.1 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 37967.0255 | 63.5042 | 142.5275 | 0 | 0.0005 | 253440.6246 | 15822.5224
February | 33329.5139 | 56.7653 | 130.1081 | 0 | 0.0005 | 231368.7877 | 13983.8726
March | 33181.83 | 60.4493 | 148.8235 | 0 | 0.0006 | 264695.2941 | 14285.3607
April | 32263.9178 | 60.651 | 153.8926 | 0 | 0.0006 | 273729.8565 | 14063.2436
May | 35843.9725 | 69.0593 | 179.1966 | 0 | 0.0007 | 318754.0006 | 15778.7312
June | 39197.7755 | 75.6873 | 196.7789 | 0 | 0.0007 | 350030.8215 | 17270.4585
July | 42116.7004 | 81.3234 | 211.4321 | 0 | 0.0008 | 376096.0175 | 18556.5264
August | 42411.5686 | 81.8955 | 212.9257 | 0 | 0.0008 | 378752.8334 | 18686.6953
September | 37565.3273 | 72.5259 | 188.538 | 0 | 0.0007 | 335371.8888 | 16550.344
October | 32653.6091 | 61.8565 | 158.0699 | 0 | 0.0006 | 281164.5929 | 14276.7842
November | 31583.5906 | 57.0032 | 139.0352 | 0 | 0.0005 | 247280.6016 | 13547.9298
December | 36127.2948 | 61.7182 | 141.9503 | 0 | 0.0005 | 252429.6944 | 15175.0637
Annual Sum or Average | 434242.1259 | 802.4391 | 2003.2784 | 0 | 0.0074 | 3563120 | 187997.5323
Minimum of Months | 31583.5906 | 56.7653 | 130.1081 | 0 | 0.0005 | 231368.7877 | 13547.9298
Maximum of Months | 42411.5686 | 81.8955 | 212.9257 | 0 | 0.0008 | 378752.8334 | 18686.6953
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 146131000000 | 120152.45 | 23-JAN-15:00 | 66738.465 | 10771.038 | 23793.055 | 0 | 18849.893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 133405000000 | 126729.508 | 18-FEB-15:09 | 66738.465 | 10771.038 | 23793.055 | 0 | 25426.951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 152621000000 | 138002.873 | 28-MAR-14:00 | 66738.465 | 10771.038 | 23793.055 | 0 | 36700.317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 157830000000 | 157515.232 | 15-APR-15:00 | 66738.465 | 10771.038 | 23793.055 | 0 | 56212.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 183791000000 | 171245.178 | 15-MAY-14:00 | 66738.465 | 10771.038 | 23793.055 | 0 | 69942.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 201824000000 | 185295.728 | 19-JUN-14:00 | 66738.465 | 10771.038 | 23793.055 | 0 | 83993.171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 216853000000 | 201176.239 | 03-JUL-14:00 | 66738.465 | 10771.038 | 23793.055 | 0 | 99873.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 218385000000 | 190825.183 | 17-AUG-13:00 | 66738.465 | 10771.038 | 23793.055 | 0 | 89522.626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 193372000000 | 178968.03 | 11-SEP-13:00 | 66738.465 | 10771.038 | 23793.055 | 0 | 77665.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 162117000000 | 163594.119 | 12-OCT-15:00 | 66738.465 | 10771.038 | 23793.055 | 0 | 62291.562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 142580000000 | 128465.964 | 22-NOV-15:09 | 66738.465 | 10771.038 | 23793.055 | 0 | 27163.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 145549000000 | 116641.033 | 01-DEC-15:30 | 66738.465 | 10771.038 | 23793.055 | 0 | 15338.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2054460000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 133405000000 | 116641.033 |  | 66738.465 | 10771.038 | 23793.055 | 0 | 15338.476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 218385000000 | 201176.239 |  | 66738.465 | 10771.038 | 23793.055 | 0 | 99873.682 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 56873.91 | 6427.47 | 0 | 63301.38
Cost per Total Building Area ($/m2) | 24.79 | 2.8 | 0 | 27.59
Cost per Net Conditioned Building Area ($/m2) | 24.79 | 2.8 | 0 | 27.59

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 1925.82 | 839.5 | 839.5
Net Site Energy | 1925.82 | 839.5 | 839.5
Total Source Energy | 5556.63 | 2422.25 | 2422.25
Net Source Energy | 5556.63 | 2422.25 | 2422.25
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 1.26 | 201.58 | 0 | 0 | 0 | 0
Cooling | 124.22 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 971.08 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.01 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 370.85 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1724.23 | 201.58 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 12.55 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 36.25 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 36.25 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 7.83 | 7.83 | 5.835 | 0.54 | 0.384 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28660.49 | 21088.43 | 7572.07 | 0.74 | 3.43
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 158750.4 | 114776.14 | 43974.26 | 0.72 | 3.5
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30016.18 | 23248.12 | 6768.06 | 0.77 | 3.53
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26474.44 | 20223.22 | 6251.23 | 0.76 | 3.5
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1081.79 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 34213.55 | 0.78
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 96668.12 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16158.34 | 0.78
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 16159.8 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.05 | 4.32 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.44 | 1635.18 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 7.62 | 14288.69 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.69 | 1930.07 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.45 | 1649.59 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 14137.7909 | 12.2121 | 111.5795 | 0 | 0.0001 | 673185.6949 | 5233.5379
February | 12601.4529 | 10.8776 | 100.7812 | 0 | 0 | 608042.0092 | 4668.8634
March | 13767.336 | 11.8595 | 114.4744 | 0 | 0.0001 | 690674.3983 | 5114.1551
April | 12742.799 | 10.9612 | 108.7751 | 0 | 0.0001 | 656298.1871 | 4742.1726
May | 12881.5449 | 11.053 | 114.8854 | 0 | 0.0001 | 693183.1276 | 4808.8352
June | 12587.8455 | 10.7876 | 114.6728 | 0 | 0.0001 | 691908.847 | 4706.5368
July | 13593.7696 | 11.6345 | 126.5546 | 0 | 0.0001 | 763609.9414 | 5090.9397
August | 14716.8336 | 12.5954 | 137.0557 | 0 | 0.0001 | 826972.0604 | 5511.6725
September | 13408.2972 | 11.4764 | 124.7081 | 0 | 0.0001 | 752467.8283 | 5021.1136
October | 12990.4561 | 11.1321 | 118.4301 | 0 | 0.0001 | 714579.7379 | 4857.3444
November | 12714.0988 | 10.9308 | 109.5606 | 0 | 0.0001 | 661041.4397 | 4734.636
December | 13799.5115 | 11.9011 | 112.274 | 0 | 0.0001 | 677389.231 | 5118.5778
Annual Sum or Average | 159941.736 | 137.4212 | 1393.7517 | 0 | 0.0006 | 8409350 | 59608.385
Minimum of Months | 12587.8455 | 10.7876 | 100.7812 | 0 | 0 | 608042.0092 | 4668.8634
Maximum of Months | 14716.8336 | 12.5954 | 137.0557 | 0 | 0.0001 | 826972.0604 | 5511.6725
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 138028000000 | 127999.659 | 26-JAN-13:00 | 66738.465 | 10771.038 | 19503.533 | 0 | 30986.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 124671000000 | 123524.748 | 13-FEB-11:00 | 66738.465 | 10771.038 | 19503.533 | 0 | 26511.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 141614000000 | 124280.608 | 31-MAR-14:09 | 66738.465 | 10771.038 | 19503.533 | 0 | 27267.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 134566000000 | 134075.405 | 11-APR-15:00 | 66738.465 | 10771.038 | 19503.533 | 0 | 37062.369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 142129000000 | 130257.608 | 30-MAY-12:00 | 66738.465 | 10771.038 | 19503.533 | 0 | 33244.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 141867000000 | 132470.229 | 28-JUN-12:00 | 66738.465 | 10771.038 | 19503.533 | 0 | 35457.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 156569000000 | 139669.326 | 24-JUL-14:30 | 66738.465 | 10771.038 | 19503.533 | 0 | 42656.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 169560000000 | 149161.202 | 08-AUG-12:00 | 66738.465 | 10771.038 | 19503.533 | 0 | 52148.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 154284000000 | 145990.328 | 25-SEP-14:00 | 66738.465 | 10771.038 | 19503.533 | 0 | 48977.293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 146516000000 | 137025.86 | 05-OCT-14:09 | 66738.465 | 10771.038 | 19503.533 | 0 | 40012.824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 135538000000 | 129805.163 | 20-NOV-12:00 | 66738.465 | 10771.038 | 19503.533 | 0 | 32792.128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 138890000000 | 129421.54 | 19-DEC-12:00 | 66738.465 | 10771.038 | 19503.533 | 0 | 32408.505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1724230000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 124671000000 | 123524.748 |  | 66738.465 | 10771.038 | 19503.533 | 0 | 26511.713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 169560000000 | 149161.202 |  | 66738.465 | 10771.038 | 19503.533 | 0 | 52148.166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 62883.13 | 1739.37 | 0 | 64622.51
Cost per Total Building Area ($/m2) | 27.41 | 0.76 | 0 | 28.17
Cost per Net Conditioned Building Area ($/m2) | 27.41 | 0.76 | 0 | 28.17

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2522.42 | 1099.58 | 1099.58
Net Site Energy | 2522.42 | 1099.58 | 1099.58
Total Source Energy | 7880.74 | 3435.38 | 3435.38
Net Source Energy | 7880.74 | 3435.38 | 3435.38
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 2.28 | 459.54 | 0 | 0 | 0 | 0
Cooling | 386.18 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 971.08 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 446.52 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2062.88 | 459.54 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 12.55 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 36.25 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 36.25 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.306 | 1.623 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 7.83 | 7.83 | 5.835 | 0.54 | 0.384 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 39757.4 | 30295.77 | 9461.63 | 0.76 | 3.27
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 187595.79 | 135367.8 | 52227.99 | 0.72 | 3.5
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 34353.47 | 26624.18 | 7729.29 | 0.78 | 3.5
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30436.94 | 23284.85 | 7152.09 | 0.77 | 3.51
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1779.83 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 53175.43 | 0.78
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 153258.95 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25777.3 | 0.78
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 25779.08 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.67 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.16 | 2364.85 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 8.96 | 16803.77 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.94 | 2123.61 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.67 | 1903 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 39218.6907 | 59.0393 | 220.4638 | 0 | 0.0004 | 1099330 | 16009.9369
February | 31949.8869 | 50.0741 | 198.1871 | 0 | 0.0004 | 988331.9405 | 13248.1538
March | 36264.0186 | 56.9513 | 226.0358 | 0 | 0.0004 | 1127210 | 15049.0566
April | 35666.3133 | 58.0176 | 241.1561 | 0 | 0.0005 | 1202690 | 15009.415
May | 40028.1105 | 65.479 | 274.0898 | 0 | 0.0005 | 1366960 | 16883.0431
June | 46603.47 | 76.4203 | 320.8543 | 0 | 0.0006 | 1600190 | 19675.6387
July | 49690.4571 | 81.4888 | 342.1677 | 0 | 0.0006 | 1706480 | 20979.6077
August | 50309.0719 | 82.5032 | 346.4271 | 0 | 0.0006 | 1727730 | 21240.7863
September | 43514.193 | 71.3552 | 299.5921 | 0 | 0.0006 | 1494150 | 18371.4438
October | 37193.7308 | 60.5644 | 252.0674 | 0 | 0.0005 | 1257110 | 15658.6519
November | 33251.2119 | 52.6724 | 211.511 | 0 | 0.0004 | 1054800 | 13845.8278
December | 38005.896 | 57.8523 | 219.6499 | 0 | 0.0004 | 1095300 | 15581.2363
Annual Sum or Average | 481695.0507 | 772.4181 | 3152.2022 | 0 | 0.006 | 15720300 | 201552.798
Minimum of Months | 31949.8869 | 50.0741 | 198.1871 | 0 | 0.0004 | 988331.9405 | 13248.1538
Maximum of Months | 50309.0719 | 82.5032 | 346.4271 | 0 | 0.0006 | 1727730 | 21240.7863
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 144258000000 | 106970.965 | 18-JAN-16:49 | 66738.465 | 10771.038 | 23195.231 | 0 | 2574.232 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 129693000000 | 115547.687 | 08-FEB-15:50 | 66738.465 | 10771.038 | 23195.231 | 0 | 14842.955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 147918000000 | 128785.517 | 31-MAR-14:00 | 66738.465 | 10771.038 | 23195.231 | 0 | 28080.784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 157822000000 | 156960.441 | 21-APR-14:00 | 66738.465 | 10771.038 | 23195.231 | 0 | 56255.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 179377000000 | 169418.1 | 31-MAY-15:00 | 66738.465 | 10771.038 | 23195.231 | 0 | 68713.367 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 209983000000 | 191268.428 | 27-JUN-15:00 | 66738.465 | 10771.038 | 23195.231 | 0 | 90563.695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 223932000000 | 189963.934 | 24-JUL-15:00 | 66738.465 | 10771.038 | 23195.231 | 0 | 89259.201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 226719000000 | 187859.52 | 05-AUG-12:00 | 66738.465 | 10771.038 | 23195.231 | 0 | 87154.787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 196068000000 | 183609.389 | 01-SEP-14:00 | 66738.465 | 10771.038 | 23195.231 | 0 | 82904.656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 164964000000 | 157519.113 | 03-OCT-14:00 | 66738.465 | 10771.038 | 23195.231 | 0 | 56814.38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 138415000000 | 118801.143 | 10-NOV-15:09 | 66738.465 | 10771.038 | 23195.231 | 0 | 18096.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 143729000000 | 116789.434 | 05-DEC-14:50 | 66738.465 | 10771.038 | 23195.231 | 0 | 16084.702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2062880000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 129693000000 | 106970.965 |  | 66738.465 | 10771.038 | 23195.231 | 0 | 2574.232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 226719000000 | 191268.428 |  | 66738.465 | 10771.038 | 23195.231 | 0 | 90563.695 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 56878.02 | 3504.67 | 0 | 60382.69
Cost per Total Building Area ($/m2) | 24.79 | 1.53 | 0 | 26.32
Cost per Net Conditioned Building Area ($/m2) | 24.79 | 1.53 | 0 | 26.32

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2163.42 | 943.08 | 943.08
Net Site Energy | 2163.42 | 943.08 | 943.08
Total Source Energy | 5527.01 | 2409.34 | 2409.34
Net Source Energy | 5527.01 | 2409.34 | 2409.34
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 3.3 | 583.51 | 0 | 0 | 0 | 0
Cooling | 30.15 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 971.08 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.03 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 318.54 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1579.91 | 583.51 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 12.55 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 36.25 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 36.25 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.272 | 1.571 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 7.83 | 7.83 | 5.835 | 0.54 | 0.384 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26823.07 | 21218.27 | 5604.8 | 0.79 | 3.58
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 103933.18 | 80747.87 | 23185.31 | 0.78 | 3.77
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30016.44 | 23972.79 | 6043.65 | 0.8 | 3.56
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 25897.67 | 20683.31 | 5214.36 | 0.8 | 3.6
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1366.79 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 42606.82 | 0.78
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 120634.63 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20483.39 | 0.78
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 20483.71 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.06 | 5.44 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.59 | 1807.72 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.91 | 11082.29 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.81 | 1983.07 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.56 | 1782.24 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 17305.5905 | 15.1147 | 106.8195 | 0 | 0.0001 | 644350.1543 | 6315.396
February | 13458.3224 | 11.6794 | 96.5126 | 0 | 0 | 582245.5163 | 4952.4043
March | 15287.9922 | 13.2718 | 108.8191 | 0 | 0.0001 | 656484.9932 | 5623.2026
April | 13686.6505 | 11.8469 | 103.6389 | 0 | 0.0001 | 625261.0229 | 5053.171
May | 13279.6177 | 11.452 | 108.1682 | 0 | 0.0001 | 652617.4577 | 4926.1148
June | 12585.0094 | 10.8335 | 105.9887 | 0 | 0 | 639481.3653 | 4679.0603
July | 12574.7301 | 10.8105 | 108.4444 | 0 | 0.0001 | 654307.0652 | 4682.9948
August | 13127.1722 | 11.2903 | 112.3399 | 0 | 0.0001 | 677807.76 | 4886.081
September | 12685.0675 | 10.9061 | 109.2656 | 0 | 0.0001 | 659261.4541 | 4723.6883
October | 13146.3175 | 11.3297 | 108.3979 | 0 | 0.0001 | 654008.3865 | 4880.6802
November | 13508.4484 | 11.6918 | 102.4381 | 0 | 0.0001 | 618017.2523 | 4987.8314
December | 16686.5177 | 14.5552 | 106.3626 | 0 | 0.0001 | 641611.2916 | 6099.74
Annual Sum or Average | 167331.436 | 144.7817 | 1277.1956 | 0 | 0.0006 | 7705450 | 61810.3647
Minimum of Months | 12574.7301 | 10.8105 | 96.5126 | 0 | 0 | 582245.5163 | 4679.0603
Maximum of Months | 17305.5905 | 15.1147 | 112.3399 | 0 | 0.0001 | 677807.76 | 6315.396
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 132116000000 | 98257.096 | 04-JAN-17:00 | 66738.465 | 10771.038 | 16660.769 | 394.825 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 119382000000 | 108369.094 | 15-FEB-15:00 | 66738.465 | 10771.038 | 16655.326 | 0 | 14204.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 134604000000 | 97856.829 | 01-MAR-17:00 | 66738.465 | 10771.038 | 16655.326 | 0 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 128202000000 | 116954.487 | 29-APR-13:00 | 66738.465 | 10771.038 | 16655.326 | 0 | 22789.658 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 133811000000 | 118883.667 | 17-MAY-13:00 | 66738.465 | 10771.038 | 16655.326 | 0 | 24718.838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 131118000000 | 120708.793 | 15-JUN-12:00 | 66738.465 | 10771.038 | 16655.326 | 0 | 26543.964 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 134158000000 | 129992.046 | 03-JUL-12:00 | 66738.465 | 10771.038 | 16655.326 | 0 | 35827.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 138976000000 | 126531.25 | 15-AUG-11:00 | 66738.465 | 10771.038 | 16655.326 | 0 | 32366.421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 135173000000 | 141444.044 | 28-SEP-14:00 | 66738.465 | 10771.038 | 16655.326 | 0 | 47279.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 134096000000 | 117795.862 | 13-OCT-14:00 | 66738.465 | 10771.038 | 16655.326 | 0 | 23631.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 126717000000 | 98445.178 | 14-NOV-16:00 | 66738.465 | 10771.038 | 16655.326 | 0 | 588.35 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 131554000000 | 98196.362 | 02-DEC-17:00 | 66738.465 | 10771.038 | 16660.769 | 334.091 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1579910000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 119382000000 | 97856.829 |  | 66738.465 | 10771.038 | 16655.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 138976000000 | 141444.044 |  | 66738.465 | 10771.038 | 16660.769 | 394.825 | 47279.215 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 65436.48 | 5004.75 | 0 | 70441.24
Cost per Total Building Area ($/m2) | 28.53 | 2.18 | 0 | 30.71
Cost per Net Conditioned Building Area ($/m2) | 28.53 | 2.18 | 0 | 30.71

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3121.66 | 1360.8 | 1360.8
Net Site Energy | 3121.66 | 1360.8 | 1360.8
Total Source Energy | 8163.85 | 3558.79 | 3558.79
Net Source Energy | 8163.85 | 3558.79 | 3558.79
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 6.1 | 1207.41 | 0 | 0 | 0 | 0
Cooling | 251.89 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 971.08 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 57.99 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 428.37 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1914.25 | 1207.41 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 12.55 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 36.25 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 36.25 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.011 | 1.191 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.489 | 0.539 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 7.83 | 7.83 | 5.835 | 0.54 | 0.384 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 67312 | 45855.41 | 21456.59 | 0.68 | 3.11
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 201352.61 | 136131.12 | 65221.49 | 0.68 | 3.31
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 37636.85 | 26897.51 | 10739.34 | 0.71 | 3.38
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 34081.31 | 23948.84 | 10132.47 | 0.7 | 3.36
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 2436.74 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 74295.62 | 0.78
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 225384.62 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37401.23 | 0.78
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 37403.14 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.1 | 9.75 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.77 | 3026.78 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 8.11 | 15211.41 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.75 | 1998.37 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.52 | 1733.27 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 40676.2549 | 63.4014 | 146.3794 | 0 | 0.0006 | 9098.8539 | 16499.3365
February | 34410.3059 | 55.0638 | 131.7212 | 0 | 0.0006 | 8188.4082 | 14088.3758
March | 32094.924 | 56.0065 | 148.5212 | 0 | 0.0006 | 9234.922 | 13565.3871
April | 26581.4049 | 49.5184 | 140.3068 | 0 | 0.0006 | 8725.358 | 11521.5024
May | 27413.7781 | 53.7263 | 159.3728 | 0 | 0.0006 | 9911.9158 | 12125.2625
June | 31562.7051 | 63.0162 | 189.8909 | 0 | 0.0008 | 11810.2885 | 14066.3043
July | 34135.1003 | 68.2333 | 205.8153 | 0 | 0.0008 | 12800.7303 | 15220.1432
August | 34957.54 | 69.8493 | 210.6198 | 0 | 0.0008 | 13099.5387 | 15584.2962
September | 28366.0833 | 56.4096 | 169.4197 | 0 | 0.0007 | 10537.0108 | 12621.1665
October | 27856.2256 | 53.0642 | 153.5013 | 0 | 0.0006 | 9546.2833 | 12181.1316
November | 29164.7061 | 51.9554 | 140.8265 | 0 | 0.0006 | 8756.8803 | 12424.0138
December | 37472.2943 | 60.2453 | 144.9973 | 0 | 0.0006 | 9013.8469 | 15367.7755
Annual Sum or Average | 384691.3225 | 700.4896 | 1941.3722 | 0 | 0.0079 | 120724.0366 | 165264.6955
Minimum of Months | 26581.4049 | 49.5184 | 131.7212 | 0 | 0.0006 | 8188.4082 | 11521.5024
Maximum of Months | 40676.2549 | 69.8493 | 210.6198 | 0 | 0.0008 | 13099.5387 | 16499.3365
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 144275000000 | 104466.763 | 17-JAN-17:00 | 66738.465 | 10771.038 | 21979.576 | 1285.685 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 129839000000 | 104017.024 | 23-FEB-17:00 | 66738.465 | 10771.038 | 21979.576 | 835.945 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 146433000000 | 130204.524 | 09-MAR-15:00 | 66738.465 | 10771.038 | 21969.827 | 0 | 30725.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 138353000000 | 132453.071 | 04-APR-15:00 | 66738.465 | 10771.038 | 21969.827 | 0 | 32973.742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 157167000000 | 153887.957 | 31-MAY-15:00 | 66738.465 | 10771.038 | 21969.827 | 0 | 54408.628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 187269000000 | 184721.403 | 30-JUN-14:00 | 66738.465 | 10771.038 | 21969.827 | 0 | 85242.074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 202974000000 | 191011.43 | 25-JUL-12:00 | 66738.465 | 10771.038 | 21969.827 | 0 | 91532.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 207712000000 | 192605.22 | 17-AUG-14:00 | 66738.465 | 10771.038 | 21969.827 | 0 | 93125.891 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 167079000000 | 168371.303 | 09-SEP-14:30 | 66738.465 | 10771.038 | 21969.827 | 0 | 68891.974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 151370000000 | 145929.886 | 20-OCT-14:00 | 66738.465 | 10771.038 | 21969.827 | 0 | 46450.557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 138853000000 | 134845.996 | 04-NOV-13:00 | 66738.465 | 10771.038 | 21969.827 | 0 | 35366.666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 142927000000 | 104354.272 | 14-DEC-17:00 | 66738.465 | 10771.038 | 21979.576 | 1173.194 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1914250000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 129839000000 | 104017.024 |  | 66738.465 | 10771.038 | 21969.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 207712000000 | 192605.22 |  | 66738.465 | 10771.038 | 21979.576 | 1285.685 | 93125.891 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 41068.5 | 11658.39 | 0 | 52726.9
Cost per Total Building Area ($/m2) | 17.9 | 5.08 | 0 | 22.98
Cost per Net Conditioned Building Area ($/m2) | 17.9 | 5.08 | 0 | 22.98

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2718.7 | 1185.14 | 1185.14
Net Site Energy | 2718.7 | 1185.14 | 1185.14
Total Source Energy | 7074.33 | 3083.85 | 3083.85
Net Source Energy | 7074.33 | 3083.85 | 3083.85
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 4.44 | 874.36 | 0 | 0 | 0 | 0
Cooling | 176.64 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 971.08 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58.01 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 435.35 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1844.34 | 874.36 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 12.55 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 36.25 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 36.25 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 1.045 | 1.238 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.506 | 0.56 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 7.83 | 7.83 | 5.835 | 0.54 | 0.384 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 46384.02 | 37044.84 | 9339.18 | 0.8 | 3.35
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 141506.56 | 111970.02 | 29536.55 | 0.79 | 3.85
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 28285.6 | 22590.44 | 5695.16 | 0.8 | 3.6
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 23452.54 | 18730.5 | 4722.05 | 0.8 | 3.6
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 2137.01 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 61519.73 | 0.78
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 180725.06 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 30680.95 | 0.78
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 30680.95 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.11 | 10.34 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.8 | 3064.41 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 8.38 | 15714.63 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.71 | 1946.58 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.42 | 1613.97 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 48126.0012 | 75.819 | 174.1346 | 0 | 0.0007 | 181018.7184 | 19808.555
February | 41370.2935 | 66.5662 | 157.2153 | 0 | 0.0006 | 163441.595 | 17164.2914
March | 44344.4145 | 72.8862 | 176.8234 | 0 | 0.0007 | 183838.0231 | 18548.7627
April | 39720.824 | 67.6063 | 170.9417 | 0 | 0.0007 | 177739.8754 | 16842.2965
May | 43280.3397 | 75.3223 | 195.2318 | 0 | 0.0008 | 203007.0828 | 18514.1772
June | 45317.306 | 79.43 | 207.466 | 0 | 0.0008 | 215732.177 | 19440.7347
July | 48242.1448 | 84.6398 | 221.3069 | 0 | 0.0009 | 230125.0296 | 20703.6338
August | 48101.2465 | 84.3748 | 220.5645 | 0 | 0.0009 | 229352.9618 | 20641.4257
September | 42896.1236 | 75.1155 | 195.9988 | 0 | 0.0008 | 203807.5721 | 18395.1289
October | 40835.9132 | 69.7585 | 177.1166 | 0 | 0.0007 | 184162.0445 | 17340.0502
November | 42338.1783 | 69.1613 | 166.5105 | 0 | 0.0007 | 173112.8589 | 17667.6578
December | 48625.1334 | 76.267 | 174.1094 | 0 | 0.0007 | 180989.8093 | 19980.8101
Annual Sum or Average | 533197.9188 | 896.9469 | 2237.4196 | 0 | 0.0088 | 2326330 | 225047.5239
Minimum of Months | 39720.824 | 66.5662 | 157.2153 | 0 | 0.0006 | 163441.595 | 16842.2965
Maximum of Months | 48625.1334 | 84.6398 | 221.3069 | 0 | 0.0009 | 230125.0296 | 20703.6338
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 143514000000 | 104242.334 | 12-JAN-17:00 | 66738.465 | 10771.038 | 22349.93 | 690.902 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 129578000000 | 112425.867 | 14-FEB-15:00 | 66738.465 | 10771.038 | 22339.59 | 0 | 12576.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 145749000000 | 113632.66 | 02-MAR-15:09 | 66738.465 | 10771.038 | 22339.59 | 0 | 13783.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 140914000000 | 134794.016 | 22-APR-13:00 | 66738.465 | 10771.038 | 22339.59 | 0 | 34944.923 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 160946000000 | 141434.495 | 31-MAY-15:00 | 66738.465 | 10771.038 | 22339.59 | 0 | 41585.403 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 171035000000 | 154438.977 | 29-JUN-14:09 | 66738.465 | 10771.038 | 22339.59 | 0 | 54589.885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 182446000000 | 158800.451 | 31-JUL-14:00 | 66738.465 | 10771.038 | 22339.59 | 0 | 58951.358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 181834000000 | 157272.56 | 01-AUG-14:20 | 66738.465 | 10771.038 | 22339.59 | 0 | 57423.467 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 161581000000 | 144402.731 | 02-SEP-14:00 | 66738.465 | 10771.038 | 22339.59 | 0 | 44553.638 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 146006000000 | 130389.685 | 13-OCT-14:00 | 66738.465 | 10771.038 | 22339.59 | 0 | 30540.592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 137246000000 | 108656.506 | 08-NOV-17:10 | 66738.465 | 10771.038 | 22339.59 | 0 | 5115.414 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 143491000000 | 104464.527 | 28-DEC-17:00 | 66738.465 | 10771.038 | 22349.93 | 913.095 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1844340000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 129578000000 | 104242.334 |  | 66738.465 | 10771.038 | 22339.59 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 182446000000 | 158800.451 |  | 66738.465 | 10771.038 | 22349.93 | 913.095 | 58951.358 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 19111.31 | 6003.52 | 0 | 25114.83
Cost per Total Building Area ($/m2) | 8.33 | 2.62 | 0 | 10.95
Cost per Net Conditioned Building Area ($/m2) | 8.33 | 2.62 | 0 | 10.95

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 2715.73 | 1183.84 | 1183.84
Net Site Energy | 2715.73 | 1183.84 | 1183.84
Total Source Energy | 4024.8 | 1754.5 | 1754.5
Net Source Energy | 4024.8 | 1754.5 | 1754.5
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 6.73 | 1086.14 | 0 | 0 | 0 | 0
Cooling | 38.17 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 971.08 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 57.9 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 356.88 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1629.59 | 1086.14 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 12.55 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 36.25 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 36.25 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.994 | 1.167 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.483 | 0.532 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 7.83 | 7.83 | 5.835 | 0.54 | 0.384 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 5.835 | 0.54 | 0.384 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 5.83 | 0.54 | 0.384
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 37334.68 | 29282.48 | 8052.2 | 0.78 | 3.52
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 120110.98 | 91593.52 | 28517.46 | 0.76 | 3.69
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 30494.83 | 24354.85 | 6139.97 | 0.8 | 3.56
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26605.08 | 21248.29 | 5356.79 | 0.8 | 3.6
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 1895.19 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 57808.92 | 0.78
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 172495.27 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 28911.03 | 0.78
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 28910.62 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.08 | 7.65 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.17 | 2370.4 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 6.54 | 12276.14 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.84 | 2014.67 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.61 | 1830.93 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 16997.4662 | 20.0222 | 29.3984 | 0 | 0.0001 | 387892.3788 | 6374.7896
February | 12944.3282 | 15.8787 | 26.4164 | 0 | 0.0001 | 348704.7723 | 4922.256
March | 13907.3406 | 17.2847 | 29.8163 | 0 | 0.0001 | 393633.3434 | 5312.5203
April | 10863.9745 | 14.2386 | 27.9933 | 0 | 0.0001 | 369714.3956 | 4228.8401
May | 8875.9439 | 12.6428 | 29.3173 | 0 | 0.0001 | 387371.9659 | 3563.1299
June | 7761.0823 | 11.5825 | 29.0044 | 0 | 0.0001 | 383306.7981 | 3172.1041
July | 7519.6548 | 11.6259 | 30.6799 | 0 | 0.0001 | 405496.6812 | 3116.6686
August | 7629.4794 | 11.8823 | 31.6807 | 0 | 0.0001 | 418732.3021 | 3171.4575
September | 8119.9778 | 11.9858 | 29.5011 | 0 | 0.0001 | 389855.6816 | 3304.6251
October | 9812.0729 | 13.4162 | 28.8339 | 0 | 0.0001 | 380911.1387 | 3878.951
November | 13550.9985 | 16.7046 | 28.1761 | 0 | 0.0001 | 371951.537 | 5161.7015
December | 16923.4416 | 19.9468 | 29.3457 | 0 | 0.0001 | 387199.7422 | 6348.2904
Annual Sum or Average | 134905.7605 | 177.2111 | 350.1636 | 0 | 0.0015 | 4624770 | 52555.3341
Minimum of Months | 7519.6548 | 11.5825 | 26.4164 | 0 | 0.0001 | 348704.7723 | 3116.6686
Maximum of Months | 16997.4662 | 20.0222 | 31.6807 | 0 | 0.0001 | 418732.3021 | 6374.7896
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 136678000000 | 100501.514 | 31-JAN-17:00 | 66738.465 | 10771.038 | 18499.793 | 800.218 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 122870000000 | 100605.761 | 11-FEB-17:00 | 66738.465 | 10771.038 | 18499.793 | 904.466 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 138701000000 | 102166.96 | 29-MAR-16:00 | 66738.465 | 10771.038 | 18492.142 | 0 | 6165.315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 130273000000 | 109119.854 | 29-APR-14:00 | 66738.465 | 10771.038 | 18492.142 | 0 | 13118.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 136495000000 | 120266.401 | 04-MAY-14:00 | 66738.465 | 10771.038 | 18492.142 | 0 | 24264.757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 135062000000 | 125938.862 | 28-JUN-14:00 | 66738.465 | 10771.038 | 18492.142 | 0 | 29937.217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 142881000000 | 136936.866 | 24-JUL-14:00 | 66738.465 | 10771.038 | 18492.142 | 0 | 40935.221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 147545000000 | 132546.654 | 07-AUG-14:00 | 66738.465 | 10771.038 | 18492.142 | 0 | 36545.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 137370000000 | 149906.128 | 02-SEP-15:39 | 66738.465 | 10771.038 | 18492.142 | 0 | 53904.483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 134218000000 | 108074.728 | 17-OCT-15:30 | 66738.465 | 10771.038 | 18492.142 | 0 | 12073.083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 131061000000 | 100563.577 | 16-NOV-17:00 | 66738.465 | 10771.038 | 18499.793 | 862.282 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 136434000000 | 100810.176 | 13-DEC-17:00 | 66738.465 | 10771.038 | 18499.793 | 1108.88 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1629590000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 122870000000 | 100501.514 |  | 66738.465 | 10771.038 | 18492.142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 147545000000 | 149906.128 |  | 66738.465 | 10771.038 | 18499.793 | 1108.88 | 53904.483 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 34204.68 | 9143.13 | 0 | 43347.81
Cost per Total Building Area ($/m2) | 14.91 | 3.99 | 0 | 18.9
Cost per Net Conditioned Building Area ($/m2) | 14.91 | 3.99 | 0 | 18.9

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3521.16 | 1534.95 | 1534.95
Net Site Energy | 3521.16 | 1534.95 | 1534.95
Total Source Energy | 8501.55 | 3706 | 3706
Net Source Energy | 8501.55 | 3706 | 3706
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 7.6 | 1623.68 | 0 | 0 | 0 | 0
Cooling | 172.09 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 971.08 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 58 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 489.9 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1897.49 | 1623.68 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 12.55 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 36.25 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 36.25 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.886 | 1.021 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.4 | 0.433 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 7.83 | 7.83 | 3.525 | 0.407 | 0.316 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 3.525 | 0.407 | 0.316 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 3.525 | 0.407 | 0.316 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 88809.6 | 60042.68 | 28766.92 | 0.68 | 3.33
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 191116.51 | 129210.66 | 61905.84 | 0.68 | 3.31
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 35896.24 | 25099.91 | 10796.32 | 0.7 | 3.35
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 38444.43 | 26198.65 | 12245.78 | 0.68 | 3.31
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 2812.27 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 94484.45 | 0.78
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 291229.25 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 46725.09 | 0.78
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 46726.8 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.12 | 11.44 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.58 | 6821.67 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 7.7 | 14438.11 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.58 | 1802.31 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.58 | 1802.4 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 71903.6861 | 112.3043 | 282.273 | 0 | 0.0009 | 64958.2925 | 29383.221
February | 61381.7545 | 97.8932 | 253.0932 | 0 | 0.0008 | 58246.919 | 25276.8681
March | 63661.397 | 104.8808 | 282.5869 | 0 | 0.0009 | 65040.3887 | 26536.1038
April | 53061.4009 | 92.18 | 264.0841 | 0 | 0.0008 | 60789.3877 | 22573.0267
May | 54880.1932 | 98.6501 | 292.9811 | 0 | 0.0009 | 67445.9068 | 23663.2751
June | 60850.4459 | 110.6667 | 332.5558 | 0 | 0.001 | 76557.93 | 26360.3744
July | 66898.9638 | 121.7896 | 366.3472 | 0 | 0.0011 | 84337.2352 | 28992.3183
August | 65455.1431 | 119.1351 | 358.2842 | 0 | 0.0011 | 82481.01 | 28364.1077
September | 54748.5825 | 99.2811 | 297.4795 | 0 | 0.0009 | 68482.6148 | 23689.4784
October | 53688.396 | 94.867 | 276.7827 | 0 | 0.0008 | 63714.7694 | 22992.5217
November | 57662.4794 | 96.7132 | 266.2423 | 0 | 0.0008 | 61281.2508 | 24199.5844
December | 68772.9411 | 109.0562 | 279.8241 | 0 | 0.0009 | 64397.7025 | 28260.8143
Annual Sum or Average | 732965.3836 | 1257.4173 | 3552.5341 | 0 | 0.0109 | 817733.4074 | 310291.6938
Minimum of Months | 53061.4009 | 92.18 | 253.0932 | 0 | 0.0008 | 58246.919 | 22573.0267
Maximum of Months | 71903.6861 | 121.7896 | 366.3472 | 0 | 0.0011 | 84337.2352 | 29383.221
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 150731000000 | 107604.316 | 26-JAN-17:00 | 66738.465 | 10771.038 | 24875.933 | 1526.881 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 135158000000 | 107120.835 | 03-FEB-17:00 | 66738.465 | 10771.038 | 24875.933 | 1043.4 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 150921000000 | 115270.282 | 31-MAR-14:00 | 66738.465 | 10771.038 | 24864.49 | 0 | 12896.291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 141057000000 | 117837.339 | 07-APR-14:00 | 66738.465 | 10771.038 | 24864.49 | 0 | 15463.347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 156503000000 | 151537.446 | 30-MAY-15:00 | 66738.465 | 10771.038 | 24864.49 | 0 | 49163.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 177647000000 | 179382.993 | 08-JUN-12:00 | 66738.465 | 10771.038 | 24864.49 | 0 | 77009.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 195698000000 | 182565.975 | 13-JUL-14:00 | 66738.465 | 10771.038 | 24864.49 | 0 | 80191.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 191391000000 | 180320.441 | 04-AUG-15:00 | 66738.465 | 10771.038 | 24864.49 | 0 | 77946.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 158909000000 | 156310.551 | 05-SEP-14:00 | 66738.465 | 10771.038 | 24864.49 | 0 | 53936.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 147845000000 | 131345.222 | 31-OCT-14:09 | 66738.465 | 10771.038 | 24864.49 | 0 | 28971.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 142199000000 | 130982.503 | 02-NOV-14:00 | 66738.465 | 10771.038 | 24864.49 | 0 | 28608.511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 149430000000 | 107175.946 | 13-DEC-17:00 | 66738.465 | 10771.038 | 24875.933 | 1098.511 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1897490000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 135158000000 | 107120.835 |  | 66738.465 | 10771.038 | 24864.49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 195698000000 | 182565.975 |  | 66738.465 | 10771.038 | 24875.933 | 1526.881 | 80191.983 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 48068.58 | 13470.81 | 0 | 61539.39
Cost per Total Building Area ($/m2) | 20.95 | 5.87 | 0 | 26.83
Cost per Net Conditioned Building Area ($/m2) | 20.95 | 5.87 | 0 | 26.83

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3052.51 | 1330.65 | 1330.65
Net Site Energy | 3052.51 | 1330.65 | 1330.65
Total Source Energy | 7409.09 | 3229.78 | 3229.78
Net Source Energy | 7409.09 | 3229.78 | 3229.78
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 6.12 | 1221.53 | 0 | 0 | 0 | 0
Cooling | 107.55 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 971.08 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 57.97 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 489.45 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1830.98 | 1221.53 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 12.55 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 36.25 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 36.25 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.914 | 1.059 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.422 | 0.459 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 7.83 | 7.83 | 3.525 | 0.407 | 0.316 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 3.525 | 0.407 | 0.316 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 3.525 | 0.407 | 0.316 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 60747.68 | 48159.33 | 12588.35 | 0.79 | 4.13
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 132863.83 | 103789.19 | 29074.64 | 0.78 | 3.79
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26278.66 | 20987.59 | 5291.07 | 0.8 | 3.6
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 26275.41 | 20985 | 5290.42 | 0.8 | 3.6
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 2468.08 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 79414.71 | 0.78
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 238767.53 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 38880.88 | 0.78
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 38877.18 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.13 | 11.96 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 3.61 | 6887.9 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 7.64 | 14341.14 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.59 | 1808.46 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.55 | 622 | 1.59 | 1808.24 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 52409.5897 | 80.9851 | 181.0689 | 0 | 0.0007 | 188214.4115 | 21416.4475
February | 45529.5098 | 71.4003 | 162.9638 | 0 | 0.0007 | 169403.5978 | 18707.6595
March | 48056.0393 | 77.4663 | 183.3938 | 0 | 0.0007 | 190657.9737 | 19952.1474
April | 41579.9829 | 69.6302 | 172.7702 | 0 | 0.0007 | 179633.3448 | 17518.7467
May | 42098.3782 | 72.1255 | 183.7312 | 0 | 0.0007 | 191041.1464 | 17896.7678
June | 42459.9886 | 73.9779 | 191.9825 | 0 | 0.0007 | 199628.9013 | 18171.4296
July | 46049.1694 | 80.7709 | 211.1314 | 0 | 0.0008 | 219543.9407 | 19760.4033
August | 46602.0633 | 81.6739 | 213.3049 | 0 | 0.0008 | 221803.6697 | 19991.1086
September | 41844.9122 | 72.5116 | 187.0653 | 0 | 0.0007 | 194513.3022 | 17869.4848
October | 42759.0748 | 72.1462 | 180.6 | 0 | 0.0007 | 187778.0158 | 18068.6394
November | 45526.5975 | 73.1649 | 172.5287 | 0 | 0.0007 | 179360.8444 | 18879.9947
December | 52836.5273 | 81.3152 | 180.7599 | 0 | 0.0007 | 187890.4402 | 21558.578
Annual Sum or Average | 547751.8331 | 907.168 | 2221.3004 | 0 | 0.0088 | 2309470 | 229791.4072
Minimum of Months | 41579.9829 | 69.6302 | 162.9638 | 0 | 0.0007 | 169403.5978 | 17518.7467
Maximum of Months | 52836.5273 | 81.6739 | 213.3049 | 0 | 0.0008 | 221803.6697 | 21558.578
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 149219000000 | 107113.394 | 05-JAN-17:00 | 66738.465 | 10771.038 | 24857.71 | 1054.182 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 134305000000 | 107209.617 | 14-FEB-17:00 | 66738.465 | 10771.038 | 24857.71 | 1150.405 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 151156000000 | 119291.659 | 30-MAR-15:00 | 66738.465 | 10771.038 | 24845.748 | 0 | 16936.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 142415000000 | 126257.884 | 25-APR-14:00 | 66738.465 | 10771.038 | 24845.748 | 0 | 23902.634 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 151460000000 | 134368.166 | 23-MAY-15:00 | 66738.465 | 10771.038 | 24845.748 | 0 | 32012.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 158268000000 | 145981.352 | 27-JUN-15:00 | 66738.465 | 10771.038 | 24845.748 | 0 | 43626.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 174057000000 | 152498.774 | 17-JUL-15:00 | 66738.465 | 10771.038 | 24845.748 | 0 | 50143.524 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 175849000000 | 154245.314 | 30-AUG-13:00 | 66738.465 | 10771.038 | 24845.748 | 0 | 51890.064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 154212000000 | 144572.261 | 02-SEP-14:00 | 66738.465 | 10771.038 | 24845.748 | 0 | 42217.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 148873000000 | 133241.122 | 05-OCT-14:00 | 66738.465 | 10771.038 | 24845.748 | 0 | 30885.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 142199000000 | 111876.638 | 10-NOV-13:00 | 66738.465 | 10771.038 | 24845.748 | 0 | 9521.388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 148962000000 | 107440.112 | 01-DEC-17:00 | 66738.465 | 10771.038 | 24857.71 | 1380.9 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1830980000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 134305000000 | 107113.394 |  | 66738.465 | 10771.038 | 24845.748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 175849000000 | 154245.314 |  | 66738.465 | 10771.038 | 24857.71 | 1380.9 | 51890.064 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 18974.21 | 8429.31 | 0 | 27403.52
Cost per Total Building Area ($/m2) | 8.27 | 3.67 | 0 | 11.95
Cost per Net Conditioned Building Area ($/m2) | 8.27 | 3.67 | 0 | 11.95

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4065.06 | 1772.05 | 1772.05
Net Site Energy | 4065.06 | 1772.05 | 1772.05
Total Source Energy | 8980.95 | 3914.99 | 3914.99
Net Source Energy | 8980.95 | 3914.99 | 3914.99
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 9.63 | 2128.21 | 0 | 0 | 0 | 0
Cooling | 141.62 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 971.08 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 57.96 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 557.73 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1936.85 | 2128.21 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 12.55 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 36.25 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 36.25 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 7.83 | 7.83 | 3.525 | 0.407 | 0.316 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 3.525 | 0.407 | 0.316 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 3.525 | 0.407 | 0.316 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 100047.35 | 67640.33 | 32407.01 | 0.68 | 3.33
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 217402.08 | 146981.9 | 70420.18 | 0.68 | 3.31
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 40001.71 | 28173.02 | 11828.69 | 0.7 | 3.16
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 42512.57 | 29256.09 | 13256.49 | 0.69 | 3.12
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 3139.48 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 105670.92 | 0.78
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 327831.85 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 52583.26 | 0.78
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 52586.5 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.14 | 12.87 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 4.03 | 7684.86 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 8.75 | 16423.88 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.8 | 1964.48 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.8 | 1964.64 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 63615.6127 | 89.7556 | 104.5276 | 0 | 0.0008 | 68613.6215 | 25077.336
February | 52117.1442 | 75.8405 | 93.1498 | 0 | 0.0007 | 61160.5384 | 20765.25
March | 47470.173 | 74.5509 | 102.664 | 0 | 0.0008 | 67441.182 | 19436.8502
April | 36908.2953 | 62.9026 | 95.9037 | 0 | 0.0007 | 63025.4164 | 15584.3412
May | 36918.6779 | 66.2227 | 106.6839 | 0 | 0.0008 | 70123.9458 | 15904.3947
June | 39150.6663 | 71.2846 | 116.5797 | 0 | 0.0008 | 76632.51 | 16967.0832
July | 41813.3126 | 76.254 | 124.9031 | 0 | 0.0009 | 82104.3002 | 18132.6095
August | 42507.2534 | 77.5387 | 127.0385 | 0 | 0.0009 | 83508.0468 | 18435.375
September | 34264.3103 | 61.7816 | 100.0559 | 0 | 0.0007 | 65768.5453 | 14791.5036
October | 37834.6234 | 64.7172 | 99.0787 | 0 | 0.0007 | 65112.9677 | 15998.0247
November | 44694.7103 | 70.2532 | 96.8607 | 0 | 0.0007 | 63629.2149 | 18306.2728
December | 58142.0067 | 84.3018 | 102.9216 | 0 | 0.0008 | 67574.6588 | 23136.5078
Annual Sum or Average | 535436.7861 | 875.4032 | 1270.3671 | 0 | 0.0095 | 834694.9478 | 222535.5488
Minimum of Months | 34264.3103 | 61.7816 | 93.1498 | 0 | 0.0007 | 61160.5384 | 14791.5036
Maximum of Months | 63615.6127 | 89.7556 | 127.0385 | 0 | 0.0009 | 83508.0468 | 25077.336
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 159213000000 | 111151.877 | 04-JAN-17:00 | 66738.465 | 10771.038 | 28050.738 | 1899.636 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 141918000000 | 110679.523 | 01-FEB-17:00 | 66738.465 | 10771.038 | 28050.738 | 1427.282 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 156492000000 | 110316.977 | 01-MAR-17:00 | 66738.465 | 10771.038 | 28050.738 | 1064.736 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 146246000000 | 127070.142 | 01-APR-16:00 | 66738.465 | 10771.038 | 28037.865 | 0 | 21522.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 162717000000 | 181383.973 | 27-MAY-14:00 | 66738.465 | 10771.038 | 28037.865 | 0 | 75836.606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 177820000000 | 180511.722 | 29-JUN-14:00 | 66738.465 | 10771.038 | 28037.865 | 0 | 74964.354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 190517000000 | 187668.988 | 15-JUL-14:00 | 66738.465 | 10771.038 | 28037.865 | 0 | 82121.621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 193774000000 | 179245.971 | 25-AUG-15:00 | 66738.465 | 10771.038 | 28037.865 | 0 | 73698.604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 152611000000 | 155799.693 | 14-SEP-14:00 | 66738.465 | 10771.038 | 28037.865 | 0 | 50252.326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 151090000000 | 139131.835 | 07-OCT-14:00 | 66738.465 | 10771.038 | 28037.865 | 0 | 33584.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 147647000000 | 110361.431 | 27-NOV-17:00 | 66738.465 | 10771.038 | 28050.738 | 1109.191 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 156802000000 | 110890.388 | 30-DEC-17:00 | 66738.465 | 10771.038 | 28050.738 | 1638.148 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1936850000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 141918000000 | 110316.977 |  | 66738.465 | 10771.038 | 28037.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 193774000000 | 187668.988 |  | 66738.465 | 10771.038 | 28050.738 | 1899.636 | 82121.621 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 33019.43 | 16763.13 | 0 | 49782.55
Cost per Total Building Area ($/m2) | 14.39 | 7.31 | 0 | 21.7
Cost per Net Conditioned Building Area ($/m2) | 14.39 | 7.31 | 0 | 21.7

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 3598.07 | 1568.47 | 1568.47
Net Site Energy | 3598.07 | 1568.47 | 1568.47
Total Source Energy | 8426.24 | 3673.18 | 3673.18
Net Source Energy | 8426.24 | 3673.18 | 3673.18
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 8.76 | 1711.68 | 0 | 0 | 0 | 0
Cooling | 62.03 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 971.08 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 57.95 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 587.75 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1886.39 | 1711.68 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 12.55 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 36.25 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 36.25 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.823 | 0.939 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 7.83 | 7.83 | 3.525 | 0.407 | 0.316 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 3.525 | 0.407 | 0.316 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 3.525 | 0.407 | 0.316 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 70989.11 | 56695.82 | 14293.28 | 0.8 | 3.93
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 153824.15 | 122852.47 | 30971.68 | 0.8 | 3.89
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 31639.17 | 25268.79 | 6370.38 | 0.8 | 3.56
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 31643.26 | 25272.06 | 6371.2 | 0.8 | 3.56
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 3046.17 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 99997.25 | 0.78
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 306960.35 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 49592.94 | 0.78
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 49597.87 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.15 | 13.98 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 4.29 | 8179.93 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 9.29 | 17432.67 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.91 | 2090.27 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.91 | 2090.54 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 58051.4622 | 85.4302 | 118.6559 | 0 | 0.0009 | 2812440 | 23256.1378
February | 49144.2918 | 73.9628 | 106.3833 | 0 | 0.0008 | 2521900 | 19846.4069
March | 47127.3754 | 75.3042 | 117.8464 | 0 | 0.0008 | 2794540 | 19454.9862
April | 40802.7708 | 67.4726 | 110.2565 | 0 | 0.0008 | 2614950 | 17063.9321
May | 39129.2416 | 67.124 | 114.4819 | 0 | 0.0008 | 2715570 | 16597.8655
June | 39043.555 | 68.484 | 119.6811 | 0 | 0.0008 | 2839120 | 16707.1861
July | 41026.2559 | 72.6781 | 128.3493 | 0 | 0.0009 | 3044850 | 17624.8494
August | 40855.0173 | 72.1992 | 127.1787 | 0 | 0.0009 | 3017060 | 17534.3159
September | 37910.5145 | 65.949 | 114.2275 | 0 | 0.0008 | 2709670 | 16169.4092
October | 40763.8864 | 68.3389 | 113.5169 | 0 | 0.0008 | 2692430 | 17137.6254
November | 45247.9236 | 71.819 | 111.4032 | 0 | 0.0008 | 2641660 | 18632.5161
December | 55452.7638 | 82.7862 | 117.6131 | 0 | 0.0009 | 2787970 | 22329.1659
Annual Sum or Average | 534555.0582 | 871.5483 | 1399.5939 | 0 | 0.0099 | 33192200 | 222354.3964
Minimum of Months | 37910.5145 | 65.949 | 106.3833 | 0 | 0.0008 | 2521900 | 16169.4092
Maximum of Months | 58051.4622 | 85.4302 | 128.3493 | 0 | 0.0009 | 3044850 | 23256.1378
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 159837000000 | 112547.504 | 06-JAN-17:00 | 66738.465 | 10771.038 | 29807.387 | 1538.614 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 143326000000 | 112233.714 | 22-FEB-17:00 | 66738.465 | 10771.038 | 29807.387 | 1224.825 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 158820000000 | 113076.965 | 30-MAR-16:00 | 66738.465 | 10771.038 | 29793.409 | 0 | 5774.053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 148614000000 | 108381.691 | 04-APR-08:09 | 66738.465 | 10771.038 | 29807.387 | 1064.802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 154332000000 | 130546.037 | 16-MAY-16:00 | 66738.465 | 10771.038 | 29793.409 | 0 | 23243.125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 161354000000 | 154174.687 | 30-JUN-14:00 | 66738.465 | 10771.038 | 29793.409 | 0 | 46871.775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 173046000000 | 155060.098 | 21-JUL-16:00 | 66738.465 | 10771.038 | 29793.409 | 0 | 47757.187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 171467000000 | 149738.148 | 09-AUG-16:00 | 66738.465 | 10771.038 | 29793.409 | 0 | 42435.236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 153997000000 | 142380.478 | 01-SEP-16:00 | 66738.465 | 10771.038 | 29793.409 | 0 | 35077.567 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 153017000000 | 125156.248 | 06-OCT-15:00 | 66738.465 | 10771.038 | 29793.409 | 0 | 17853.336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 150132000000 | 111655.492 | 27-NOV-17:00 | 66738.465 | 10771.038 | 29807.387 | 646.603 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 158447000000 | 112560.452 | 11-DEC-17:00 | 66738.465 | 10771.038 | 29807.387 | 1551.562 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1886390000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 143326000000 | 108381.691 |  | 66738.465 | 10771.038 | 29793.409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 173046000000 | 155060.098 |  | 66738.465 | 10771.038 | 29807.387 | 1551.562 | 47757.187 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 39404.78 | 13803.89 | 0 | 53208.67
Cost per Total Building Area ($/m2) | 17.18 | 6.02 | 0 | 23.19
Cost per Net Conditioned Building Area ($/m2) | 17.18 | 6.02 | 0 | 23.19

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 4553.95 | 1985.16 | 1985.16
Net Site Energy | 4553.95 | 1985.16 | 1985.16
Total Source Energy | 9357.23 | 4079.01 | 4079.01
Net Source Energy | 9357.23 | 4079.01 | 4079.01
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 12.51 | 2684.31 | 0 | 0 | 0 | 0
Cooling | 49.87 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 971.08 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 57.92 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 579.45 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 1869.64 | 2684.31 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 12.55 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 36.25 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 36.25 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.772 | 0.873 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.341 | 0.365 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 7.83 | 7.83 | 3.525 | 0.407 | 0.316 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 3.525 | 0.407 | 0.316 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 3.525 | 0.407 | 0.316 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 104425.22 | 71313.17 | 33112.05 | 0.68 | 3.35
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 230543.12 | 157146.15 | 73396.98 | 0.68 | 3.12
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 39495.06 | 28798.33 | 10696.73 | 0.73 | 3.39
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 42117.37 | 29929.29 | 12188.08 | 0.71 | 3.17
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 3308.93 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 110859.36 | 0.78
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 345410.93 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 55294.11 | 0.78
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 55296.8 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.15 | 13.86 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.58 | 1109.65 | 4.32 | 8244.61 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1017.59 | 9.49 | 16333.53 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.93 | 2116.09 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 1.94 | 2116.22 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 65003.3615 | 91.3298 | 105.5581 | 0 | 0.0008 | 69287.5017 | 25587.7023
February | 56034.9348 | 79.9576 | 94.9944 | 0 | 0.0007 | 62361.9272 | 22174.8246
March | 54094.773 | 81.2386 | 104.8909 | 0 | 0.0008 | 68885.1275 | 21794.112
April | 41689.8795 | 67.5838 | 97.036 | 0 | 0.0007 | 63754.839 | 17271.8491
May | 37334.9921 | 64.4901 | 99.8136 | 0 | 0.0007 | 65598.5893 | 15846.7432
June | 34933.5009 | 62.9109 | 101.7585 | 0 | 0.0007 | 66887.3835 | 15073.0011
July | 37721.1115 | 68.5238 | 111.8085 | 0 | 0.0008 | 73495.6812 | 16332.4464
August | 37671.9943 | 68.0387 | 110.3741 | 0 | 0.0008 | 72551.297 | 16273.3444
September | 34930.1651 | 61.5121 | 97.2135 | 0 | 0.0007 | 63894.6347 | 14938.4267
October | 40116.0431 | 66.9736 | 99.6933 | 0 | 0.0007 | 65509.9333 | 16805.3609
November | 48376.5715 | 74.121 | 98.5894 | 0 | 0.0008 | 64755.0618 | 19630.8204
December | 61770.8874 | 88.1451 | 104.7272 | 0 | 0.0008 | 68751.3156 | 24444.9831
Annual Sum or Average | 549678.2148 | 874.8251 | 1226.4576 | 0 | 0.0092 | 805733.2919 | 226173.614
Minimum of Months | 34930.1651 | 61.5121 | 94.9944 | 0 | 0.0007 | 62361.9272 | 14938.4267
Maximum of Months | 65003.3615 | 91.3298 | 111.8085 | 0 | 0.0008 | 73495.6812 | 25587.7023
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 160776000000 | 111869.63 | 11-JAN-17:00 | 66738.465 | 10771.038 | 28824.304 | 1843.825 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 144706000000 | 111809.875 | 01-FEB-17:00 | 66738.465 | 10771.038 | 28824.304 | 1784.069 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 159843000000 | 111163.968 | 08-MAR-17:00 | 66738.465 | 10771.038 | 28824.304 | 1138.162 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 147938000000 | 108020.99 | 04-APR-14:00 | 66738.465 | 10771.038 | 28810.446 | 0 | 1701.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 152217000000 | 129786.083 | 31-MAY-15:00 | 66738.465 | 10771.038 | 28810.446 | 0 | 23466.136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 155207000000 | 155984.554 | 14-JUN-15:00 | 66738.465 | 10771.038 | 28810.446 | 0 | 49664.607 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 170541000000 | 173133.162 | 08-JUL-15:00 | 66738.465 | 10771.038 | 28810.446 | 0 | 66813.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 168350000000 | 171541.766 | 12-AUG-14:00 | 66738.465 | 10771.038 | 28810.446 | 0 | 65221.818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 148263000000 | 144476.286 | 07-SEP-14:00 | 66738.465 | 10771.038 | 28810.446 | 0 | 38156.339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 152011000000 | 135466.043 | 07-OCT-14:00 | 66738.465 | 10771.038 | 28810.446 | 0 | 29146.095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 150259000000 | 111512.897 | 24-NOV-17:00 | 66738.465 | 10771.038 | 28824.304 | 1487.091 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 159532000000 | 111733.614 | 30-DEC-17:00 | 66738.465 | 10771.038 | 28824.304 | 1707.808 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 1869640000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 144706000000 | 108020.99 |  | 66738.465 | 10771.038 | 28810.446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 170541000000 | 173133.162 |  | 66738.465 | 10771.038 | 28824.304 | 1843.825 | 66813.214 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 31323.08 | 21109.25 | 0 | 52432.34
Cost per Total Building Area ($/m2) | 13.65 | 9.2 | 0 | 22.86
Cost per Net Conditioned Building Area ($/m2) | 13.65 | 9.2 | 0 | 22.86

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 6571.1 | 2864.48 | 2864.48
Net Site Energy | 6571.1 | 2864.48 | 2864.48
Total Source Energy | 12252.38 | 5341.07 | 5341.07
Net Source Energy | 12252.38 | 5341.07 | 5341.07
Area [m2]
Total Building Area | 2293.99
Net Conditioned Building Area | 2293.99
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 22.89 | 4524.02 | 0 | 0 | 0 | 0
Cooling | 13.43 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 971.08 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 57.56 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 198.81 | 0 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 783.29 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 0 | 0 | 0 | 0 | 0
Refrigeration | 0 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 2047.07 | 4524.02 | 0 | 0 | 0 | 0
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BACK_SPACE | 379.89 | Yes | 2317.33 | 1 | 416.17 | 0 | 12.55 | 27.87 | 8.07
CORE_RETAIL | 1600.48 | Yes | 9762.95 | 1 | 356.86 | 0 | 36.25 | 6.19 | 3.23
FRONT_ENTRY | 12 | Yes | 73.2 | 1 | 24.38 | 7.83 | 36.25 | 6.19 | 0
FRONT_RETAIL | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 3.23
POINT_OF_SALE | 150.81 | Yes | 919.94 | 1 | 189.8 | 38.05 | 36.25 | 6.19 | 21.52
Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Conditioned Total | 2293.99 |  | 13993.36 |  | 1177.02 | 83.94 | 32.3252 | 7.11 | 5.217
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BACK_SPACE_WALL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 42.67 | 90 | 90 | E
BACK_SPACE_WALL_NORTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 330.83 | 0 | 90 | N
BACK_SPACE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 42.67 | 270 | 90 | W
BACK_SPACE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 379.89 | 90 | 180
BACK_SPACE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 379.89 | 90 | 0
CORE_RETAIL_WALL_EAST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 178.43 | 90 | 90 | E
CORE_RETAIL_WALL_WEST_2 | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 178.43 | 270 | 90 | W
CORE_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 1600.48 | 0 | 180
CORE_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 1600.48 | 180 | 0
FRONT_ENTRY_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 24.38 | 180 | 90 | S
FRONT_ENTRY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 12 | 180 | 180
FRONT_ENTRY_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 12 | 180 | 0
FRONT_RETAIL_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 153.22 | 180 | 90 | S
FRONT_RETAIL_WALLL_EAST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36.58 | 90 | 90 | E
FRONT_RETAIL_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 90 | 180
FRONT_RETAIL_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 150.81 | 90 | 0
POINT_OF_SALE_WALL_SOUTH | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 153.22 | 180 | 90 | S
POINT_OF_SALE_WALL_WEST | EXT-WALLS-STEELFRAME-NONRES | 0.22 | 0.71 | 0.794 | 36.58 | 270 | 90 | W
POINT_OF_SALE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 150.81 | 180 | 180
POINT_OF_SALE_ROOF | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.357 | 150.81 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
FRONT_ENTRY_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 7.83 | 7.83 | 3.525 | 0.407 | 0.316 | No | FRONT_ENTRY_WALL_SOUTH | 180 | S
FRONT_RETAIL_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 3.525 | 0.407 | 0.316 | No | FRONT_RETAIL_WALL_SOUTH | 180 | S
POINT_OF_SALE_WALL_SOUTH_GLAZING | WINDOW-NONRES-FIXED | 38.05 | 38.05 | 3.525 | 0.407 | 0.316 | No | POINT_OF_SALE_WALL_SOUTH | 180 | S
Total or Average |  |  | 83.94 | 3.52 | 0.407 | 0.316
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 83.94 | 3.52 | 0.407 | 0.316
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 93998.92 | 75072.73 | 18926.19 | 0.8 | 3.89
PSZ-AC:2_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 214171.69 | 171049.35 | 43122.34 | 0.8 | 3.7
PSZ-AC:3_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 42160.1 | 33671.38 | 8488.71 | 0.8 | 3.35
PSZ-AC:4_UNITARY_PACKAGE_COOLCOIL | Coil:Cooling:DX:SingleSpeed | 42160.1 | 33671.38 | 8488.71 | 0.8 | 3.35
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
FRONT_ENTRY UNIT HEATER COIL | Coil:Heating:Electric | 4379.3 | 1
PSZ-AC:1_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 150116.23 | 0.78
PSZ-AC:2_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 474289.12 | 0.78
PSZ-AC:3_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 74766.01 | 0.78
PSZ-AC:4_UNITARY_PACKAGE_HEATCOIL | Coil:Heating:Gas | 74766.01 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
FRONT_ENTRY UNIT HEATERFAN | Fan:ConstantVolume | 0.54 | 49.8 | 0.19 | 17.71 | 1 | Unit Heater Fans
PSZ-AC:1_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.59 | 1109.65 | 5.68 | 10652.76 | 1 | Unitary Fans
PSZ-AC:2_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.6 | 1017.59 | 12.94 | 21920.94 | 1 | Unitary Fans
PSZ-AC:3_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.55 | 2785.35 | 1 | Unitary Fans
PSZ-AC:4_UNITARY_PACKAGE_FAN | Fan:OnOff | 0.57 | 622 | 2.55 | 2785.35 | 1 | Unitary Fans
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
None
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
None
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 82300.5826 | 87.1543 | 260.6008 | 0 | 0.001 | 52256.7136 | 30399.4134
February | 71250.0002 | 75.8252 | 233.4172 | 0 | 0.0009 | 46808.2889 | 26375.082
March | 64948.5077 | 71.0922 | 254.0526 | 0 | 0.0009 | 50959.4377 | 24346.0497
April | 47111.8967 | 53.844 | 231.8913 | 0 | 0.0008 | 46526.7571 | 18010.1544
May | 36248.4107 | 44.0565 | 233.4086 | 0 | 0.0008 | 46842.7268 | 14261.6846
June | 33333.124 | 41.3346 | 231.8199 | 0 | 0.0008 | 46526.6463 | 13241.0777
July | 33795.7322 | 42.0689 | 238.3981 | 0 | 0.0008 | 47847.4059 | 13449.5634
August | 34981.6709 | 43.1961 | 239.4605 | 0 | 0.0008 | 48059.5716 | 13867.8073
September | 37447.5205 | 44.9109 | 228.5134 | 0 | 0.0008 | 45858.2952 | 14640.6654
October | 50791.6036 | 57.6438 | 241.5152 | 0 | 0.0009 | 48455.9262 | 19354.4152
November | 67380.5375 | 72.8559 | 244.7707 | 0 | 0.0009 | 49092.6512 | 25119.4518
December | 76929.0693 | 82.1512 | 257.9267 | 0 | 0.001 | 51725.1753 | 28520.7732
Annual Sum or Average | 636518.6561 | 716.1335 | 2895.775 | 0 | 0.0103 | 580959.5957 | 241586.1383
Minimum of Months | 33333.124 | 41.3346 | 228.5134 | 0 | 0.0008 | 45858.2952 | 13241.0777
Maximum of Months | 82300.5826 | 87.1543 | 260.6008 | 0 | 0.001 | 52256.7136 | 30399.4134
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY [Invalid/Undefined] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY [Invalid/Undefined] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 184132000000 | 123197.481 | 13-JAN-09:09 | 66738.465 | 10771.038 | 38162.109 | 3833.87 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
February | 164934000000 | 123027.3 | 03-FEB-09:09 | 66738.465 | 10771.038 | 38162.109 | 3663.689 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
March | 179561000000 | 120369.47 | 02-MAR-17:00 | 66738.465 | 10771.038 | 38162.109 | 1005.859 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
April | 163942000000 | 117611.562 | 10-APR-08:09 | 66738.465 | 10771.038 | 38162.109 | 1939.951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
May | 165055000000 | 116436.374 | 18-MAY-08:09 | 66738.465 | 10771.038 | 38162.109 | 764.763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
June | 163942000000 | 146459.124 | 20-JUN-16:00 | 66738.465 | 10771.038 | 38144.401 | 0 | 30805.221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
July | 168596000000 | 153787.469 | 29-JUL-16:00 | 66738.465 | 10771.038 | 38144.401 | 0 | 38133.565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
August | 169343000000 | 145280.322 | 15-AUG-16:00 | 66738.465 | 10771.038 | 38144.401 | 0 | 29626.418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
September | 161587000000 | 116876.832 | 29-SEP-08:09 | 66738.465 | 10771.038 | 38162.109 | 1205.221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
October | 170740000000 | 121480.398 | 27-OCT-08:09 | 66738.465 | 10771.038 | 38162.109 | 2116.787 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
November | 172983000000 | 122141.816 | 02-NOV-08:09 | 66738.465 | 10771.038 | 38162.109 | 2778.204 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
December | 182259000000 | 122829.194 | 29-DEC-09:09 | 66738.465 | 10771.038 | 38162.109 | 3465.583 | 0 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Annual Sum or Average | 2047070000000 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum of Months | 161587000000 | 116436.374 |  | 66738.465 | 10771.038 | 38144.401 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Maximum of Months | 184132000000 | 153787.469 |  | 66738.465 | 10771.038 | 38162.109 | 3833.87 | 38133.565 | 3692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 54127.84 | 18647.24 | 0 | 72775.08
Cost per Total Building Area ($/m2) | 23.6 | 8.13 | 0 | 31.72
Cost per Net Conditioned Building Area ($/m2) | 23.6 | 8.13 | 0 | 31.72

## Picture
DOE Commercial Building Benchmark - Retail
Back_Space
Core_Retail
Front_Entry
Point_of_Sale
Front_Retail

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.15 | 70.85 | 3694.32
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.85
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 5.25
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0 | 0 | 0 | 7.2 | 46.3 | 2414.21
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.5
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 2.8
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.7 | 89.4 | 4661.57
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.15
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 8.75
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | 8.44 | 52.69 | 2747.41
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | 7.61
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | 2.88
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 9 | 68 | 3545.71
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 15
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 16.5 | 118 | 6152.86
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | 6.62 | 44.59 | 2325.05
|  |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | 6.9
|  |  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | 4.59
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 455.4 | 3171.6 | 165376.29
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | WinterDesign | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 433.8
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 630 | 4428 | 230888.57
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 | 30 | 654
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 15 | 102 | 5318.57
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 11
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FRONT_ENTRY_COOLING | Temperature | Through 12/31 | All | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400 | 16800 | 876000