## BuildingSummary
Building Summary Supermarket post-1980 construction
|  | Value | Data Source
Program
| Building Name | Benchmark Super Market
| Available Fuel Types | gas, electricity
| Principal Building Activity | Food Sales
Form
| Total Floor Area (m2) | 4181 | 2003 CBECS
| Building Shape | Rectangle
| Aspect Ratio | 1.5
| Number of Floors | 1
| Window Fraction (Window to Wall Ratio) | South: 0.362 East: 0.00 North: 0.00 West: 0.00 Total: 0.109
Skylight/TDD Percentage
| Shading Geometry | None
| Azimuth | 0
| Thermal Zoning | Office, DryStorage, Deli, Sales, Produce, Bakery
| Floor to Ceiling Height (m) | 6.1
| Roof type | Built-up flat roof, insulation entirely above deck | 2003 CBECS
Fabric
Exterior walls
| Construction Type | Mass wall | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 1609.58
| Net Dimensions - Total Area (m2) | 1434.88
| Wall to Skin Ratio | 0.28
Roof
| Construction Type | IEAD | 2003 CBECS
| Gross Dimensions - Total Area (m2) | 4181
| Net Dimensions - Total Area (m2) | 4181
| Roof to Skin Ratio | 0.72
Window
| Dimensions - Total Area (m2) | South: 174.7 East: 0.00 North: 0.00 West: 0.00 Total: 174.7
| Operable area (m2) | 0
Skylights/TDD
Dimensions - Total Area (m2)
Operable area (m2)
Foundation
| Foundation Type | Mass Floor
| Construction | 4 in slab-on-grade
| Dimensions - Total Area (m2) | 4181
Interior Partitions
| Construction | 2x4 steel-frame with gypsum board
Internal Mass
| Construction | 15 cm wood
| Dimensions - Total Area (m2) | 46.47
| Thermal diffusivity (m2/s) | 1.84e-07
Air Barrier System
| Infiltration (ACH) | 0.93 | See Benchmark Technical Report
HVAC
| System Type | PSZ-AC | 2003 CBECS
| Heating Type | Gas furnace | 2003 CBECS
| Cooling Type | Unitary DX | 2003 CBECS
| Fan Control | Constant volume | 2003 CBECS
Service Water Heating
| SWH Type | N/A
| Fuel | N/A
| Thermal Efficiency (%) | N/A
| Temperature Setpoint (ºC ) | N/A
| Water Consumption (m3 ) | N/A

## ZoneSummary
Zone Summary
Zone Name | Conditioned (Y/N) | Multiplier | Area (m2) | Volume (m3) | Floor-to-Ceiling Height (m) | Gross Wall Area (m2) | Window Glass Area (m2) | People (m2/per) | People | Lights (W/m2) | Elec Plug and Process (W/m2) | Gas Plug and Process (W/m2) | SWH (L/h) | Ventilation (L/s/Person) | Ventilation (L/s/m2) | Ventilation Total (L/s) | Exhaust (L/s) | Infiltration (ACH)
Office | Yes | 1 | 88.84 | 541.72 | 6.0977 | 115.0801 | 0 | 18.5806 | 4.7813 | 21.3644 | 8.0729 |  |  | 10 |  | 47.8132 |  | 1.5364
DryStorage | Yes | 1 | 621.89 | 3792.03 | 6.0976 | 477.2404 | 0 | 27.8709 | 22.3132 | 11.9085 | 8.0729 |  |  |  | 0.75 | 466.4175 |  | 1.183
Deli | Yes | 1 | 224.72 | 1370.24 | 6.0975 | 138.4301 | 0 | 11.6129 | 19.3509 | 29.9486 | 53.8195 | 26.9097 | 18.927 |  | 1.5 | 337.08 | 1415.841 | 1.0817
Sales | Yes | 1 | 2324.94 | 14176.6 | 6.0976 | 323.5203 | 174.7002 | 11.6129 | 200.2034 | 29.9486 | 5.3819 |  |  |  | 1.5 | 3487.41 |  | 0.76248
Produce | Yes | 1 | 711.36 | 4337.61 | 6.0976 | 366.1803 | 0 | 11.6129 | 61.2561 | 29.9486 | 5.3819 |  |  |  | 1.5 | 1067.04 |  | 1.0139
Bakery | Yes | 1 | 209.04 | 1274.65 | 6.0976 | 189.1302 | 0 | 11.6129 | 18.0007 | 29.9486 | 53.8195 | 26.9097 | 18.927 |  | 1.5 | 313.56 | 353.9603 | 1.2749
Total Conditioned Zones |  |  | 4180.79 | 25492.85 |  | 1609.5815 | 174.7002 |  | 325.9056 | [6 empty] | 5719.3207 | 1769.8013
Data Source | [7 empty] | 1 |  | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 4 | 4
Sources
[1] ASHRAE Standard 62.1-2004 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[2] ASHRAE Standard 90.1-1989, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[3] ASHRAE Standard 62-1999 Table 6-1, Atlanta, GA: American Society of Heating, Refrigerating and Air-Conditioning Engineers.
[4] DOE Benchmark Report

## LocationSummary
Location Summary
|  | Miami | Houston | Phoenix | Atlanta | Los Angeles | Las Vegas | San Francisco | Baltimore | Albuquerque | Seattle | Chicago | Boulder | Minneapolis | Helena | Duluth | Fairbanks
Program
| ASHRAE 90.1-2004 Climate Zone | 1A | 2A | 2B | 3A | 3B-CA | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 6A | 6B | 7 | 8
| Available Fuel Types | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity | gas, electricity
Fabric
Exterior walls
| Construction Type | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall | Mass wall
| R-value (m2·K / W) | 0.4207 | 0.51787 | 0.42955 | 0.60716 | 0.4207 | 0.60716 | 0.4207 | 1.4684 | 0.92678 | 1.7606 | 1.7606 | 1.2579 | 2.4814 | 2.2272 | 2.8902 | 3.7453
Roof
| Construction Type | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD | IEAD
| R-value (m2·K / W) | 2.3753 | 2.6667 | 3.8314 | 2.445 | 1.7575 | 3.663 | 1.996 | 3.0303 | 2.9851 | 2.7473 | 3.3784 | 3.5088 | 3.9683 | 3.6496 | 4.4053 | 5.7471
Window
| U-Factor (W / m2·K) | 5.835 | 5.835 | 5.835 | 4.092 | 5.835 | 5.835 | 4.092 | 3.354 | 4.092 | 4.092 | 3.354 | 3.354 | 2.956 | 2.956 | 2.956 | 2.956
| SHGC | 0.251 | 0.251 | 0.251 | 0.255 | 0.44 | 0.251 | 0.392 | 0.355 | 0.362 | 0.392 | 0.385 | 0.385 | 0.385 | 0.385 | 0.487 | 0.616
| Visible transmittance | 0.11 | 0.11 | 0.11 | 0.129 | 0.272 | 0.11 | 0.253 | 0.274 | 0.225 | 0.253 | 0.305 | 0.305 | 0.305 | 0.305 | 0.409 | 0.541
Skylights/TDD
| U-Factor (W / m2·K) | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| SHGC | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
| Visible transmittance | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a
Foundation
| Foundation Type | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor | Mass Floor
| Construction | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade | 4 in slab-on-grade
| R-value (m2·K / W) | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051 | 0.32051
HVAC
HVAC Sizing
Air Conditioning (kW)
| PSZ-AC:1_COOLC DXCOIL | 13.3326 | 16.2393 | 11.7725 | 18.2366 | 9.3787 | 12.7544 | 9.9664 | 19.2852 | 14.8379 | 11.2046 | 24.9092 | 18.0169 | 26.9162 | 19.9294 | 27.5084 | 24.2776
| PSZ-AC:2_COOLC DXCOIL | 61.0028 | 90.3245 | 71.5442 | 107.7626 | 56.3991 | 76.0434 | 56.8296 | 107.1643 | 81.1681 | 66.5036 | 134.276 | 110.3403 | 147.419 | 109.6998 | 155.7328 | 130.7395
| PSZ-AC:3_COOLC DXCOIL | 62.9754 | 61.039 | 58.0331 | 56.9426 | 58.4248 | 46.8057 | 38.4664 | 54.5837 | 39.566 | 30.5339 | 54.868 | 38.3035 | 55.5814 | 36.7772 | 38.9196 | 44.3243
| PSZ-AC:4_COOLC DXCOIL | 169.4041 | 265.6029 | 237.1487 | 310.1755 | 211.564 | 269.6599 | 188.1423 | 307.1567 | 235.4409 | 255.7012 | 377.2751 | 277.757 | 412.9861 | 312.6676 | 453.6818 | 371.5453
| PSZ-AC:5_COOLC DXCOIL | 68.9913 | 91.4483 | 79.1562 | 108.3503 | 63.3699 | 78.4429 | 56.2359 | 109.5266 | 78.5799 | 60.6088 | 136.3518 | 94.9937 | 149.5386 | 107.6559 | 157.8985 | 131.5991
| PSZ-AC:6_COOLC DXCOIL | 54.9552 | 53.7484 | 49.711 | 50.3329 | 41.3877 | 41.8989 | 34.5028 | 38.6061 | 39.3285 | 30.9466 | 38.0252 | 38.997 | 38.1435 | 38.5581 | 37.5356 | 47.1434
Heating (kW)
| PSZ-AC:1_HEATC | 14.7094 | 17.895 | 14.5916 | 20.6417 | 12.6193 | 16.6759 | 15.114 | 20.5772 | 18.5818 | 16.5774 | 25.5227 | 22.6798 | 27.5131 | 26.7269 | 28.4334 | 37.2239
| PSZ-AC:2_HEATC | 65.1194 | 97.8759 | 80.6148 | 113.2035 | 70.6624 | 91.2045 | 83.5047 | 118.3989 | 103.2315 | 95.6916 | 146.8181 | 127.1939 | 159.739 | 152.8655 | 165.417 | 216.1322
| PSZ-AC:3_HEATC | 98.1844 | 125.6314 | 100.7748 | 126.4285 | 94.7371 | 103.9926 | 87.2907 | 134.9074 | 116.5591 | 97.9047 | 158.4206 | 134.6985 | 173.4322 | 156.87 | 176.3337 | 262.9847
| PSZ-AC:4_HEATC | 211.584 | 343.4185 | 284.311 | 391.794 | 255.7198 | 328.5388 | 292.4748 | 423.3444 | 373.1848 | 361.8403 | 518.4077 | 454.0651 | 569.3084 | 553.4835 | 599.7033 | 771.7248
| PSZ-AC:5_HEATC | 80.6551 | 116.2643 | 97.5716 | 133.2653 | 86.4857 | 110.9988 | 101.0563 | 143.4522 | 122.9967 | 117.2225 | 177.9816 | 152.0861 | 195.498 | 185.1069 | 201.6849 | 262.529
| PSZ-AC:6_HEATC | 65.0761 | 66.8695 | 65.3035 | 66.8284 | 61.6333 | 60.412 | 55.8735 | 62.2265 | 55.0789 | 52.5962 | 64.748 | 57.2952 | 66.9177 | 62.8451 | 68.1004 | 88.8869
HVAC Efficiency
Air Conditioning (COP)
| PSZ-AC:1_COOLC DXCOIL | 2.99 | 2.98 | 3.07 | 3.02 | 3.1 | 3.13 | 3.19 | 3 | 3.17 | 3.16 | 2.98 | 3.17 | 2.98 | 3.22 | 3 | 3.22
| PSZ-AC:2_COOLC DXCOIL | 2.62 | 2.9 | 2.65 | 2.9 | 2.68 | 3.06 | 2.75 | 2.9 | 3.26 | 3.17 | 2.89 | 3.11 | 2.89 | 3.27 | 2.89 | 3.32
| PSZ-AC:3_COOLC DXCOIL | 2.62 | 2.62 | 2.62 | 2.62 | 2.62 | 2.69 | 3.07 | 2.62 | 3.19 | 3.19 | 2.62 | 3.19 | 2.62 | 3.19 | 3.15 | 2.8
| PSZ-AC:4_COOLC DXCOIL | 2.89 | 2.75 | 2.75 | 2.74 | 2.89 | 2.76 | 3 | 2.74 | 3.07 | 2.79 | 2.74 | 3.07 | 2.73 | 3.07 | 2.73 | 3.07
| PSZ-AC:5_COOLC DXCOIL | 2.62 | 2.9 | 2.65 | 2.9 | 2.68 | 3.1 | 2.8 | 2.9 | 3.35 | 3.35 | 2.89 | 3.32 | 2.89 | 3.32 | 2.89 | 3.32
| PSZ-AC:6_COOLC DXCOIL | 2.67 | 2.67 | 2.72 | 2.7 | 2.78 | 2.78 | 3.19 | 3.13 | 3.19 | 3.19 | 3.15 | 3.19 | 3.15 | 3.19 | 3.19 | 2.8
Heating Efficiency (%)
| PSZ-AC:1_HEATC | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| PSZ-AC:2_HEATC | 0.8 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:3_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:4_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:5_HEATC | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78 | 0.78
| PSZ-AC:6_HEATC | 0.8 | 0.78 | 0.8 | 0.78 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.78 | 0.8 | 0.78 | 0.78
HVAC Control - Economizer
| DELI EXHAUST FAN | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | NoEconomizer
| SALES EXHAUST FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:1_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb
| PSZ-AC:2_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:3_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb
| PSZ-AC:4_FAN | NoEconomizer | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb | NoEconomizer | DifferentialDryBulb
Fan Max Flow Rate (m3/s )
| BAKERY EXHAUST FAN | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
| DELI EXHAUST FAN | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34 | 0.34
| SALES EXHAUST FAN | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08 | 1.08
| PSZ-AC:1_FAN | 0.59 | 0.71 | 0.6 | 0.85 | 0.5 | 0.71 | 0.6 | 0.8 | 0.9 | 0.66 | 1.02 | 1.09 | 1.1 | 1.2 | 1.16 | 1.47
| PSZ-AC:2_FAN | 2.46 | 3.64 | 3.13 | 4.34 | 2.67 | 3.67 | 3.12 | 4.32 | 4.64 | 3.54 | 5.41 | 5.66 | 5.94 | 6.41 | 6.27 | 7.9
| PSZ-AC:3_FAN | 2.54 | 2.46 | 2.34 | 2.29 | 2.35 | 2.23 | 1.96 | 2.2 | 2.39 | 1.84 | 2.21 | 2.31 | 2.24 | 2.22 | 2.22 | 2.68
| PSZ-AC:4_FAN | 6.82 | 10.7 | 9.55 | 12.49 | 8.52 | 11.3 | 9.46 | 12.37 | 14.22 | 11.28 | 15.19 | 16.78 | 16.63 | 18.89 | 18.27 | 22.45
Utility Costs
Electric Utility Rates
| Average Annual Rate ($/kWh) | 0.081003 | 0.10419 | 0.07757 | 0.098528 | 0.12358 | 0.093307 | 0.14443 | 0.070296 | 0.037029 | 0.071201 | 0.095813 | 0.037029 | 0.055488 | 0.070239 | 0.055035 | 0.088618
| Total Cost ($/m2) | 44.87 | 56.02 | 38.09 | 49.11 | 56.02 | 43.56 | 61.87 | 33.34 | 16.86 | 30.84 | 45.4 | 16.88 | 26.37 | 32.17 | 25.4 | 42.07
Gas Utility Rates
| Average Annual Rate ($/MJ) | 0.011442 | 0.0080761 | 0.0082516 | 0.0097125 | 0.0085564 | 0.0077393 | 0.0085045 | 0.0097164 | 0.0069315 | 0.0083764 | 0.0083922 | 0.0069601 | 0.0078667 | 0.0082231 | 0.0078714 | 0.0041382
| Total Cost ($/m2) | 0.88 | 2.43 | 2.46 | 5.14 | 2.68 | 3.33 | 5.35 | 7.77 | 4.39 | 6.87 | 8.37 | 5.62 | 9.55 | 8.71 | 11.61 | 9.16
Total Utility Costs
| Cost Intensity ($/m2) | 45.75 | 58.45 | 40.54 | 54.25 | 58.7 | 46.9 | 67.23 | 41.11 | 21.25 | 37.71 | 53.78 | 22.5 | 35.92 | 40.88 | 37.01 | 51.23
Energy - End Uses
Electricity (kWh)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 258725 | 207236.1111 | 197908.3333 | 119616.6667 | 25450 | 126744.4444 | 5116.6667 | 79055.5556 | 49258.3333 | 7386.1111 | 53630.5556 | 29319.4444 | 45916.6667 | 17263.8889 | 15919.4444 | 3447.2222
| Interior Lighting | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556 | 420180.5556
| Exterior Lighting | 21494.4444 | 21458.3333 | 21450 | 21486.1111 | 21483.3333 | 21461.1111 | 21438.8889 | 21461.1111 | 21458.3333 | 21425 | 21430.5556 | 21436.1111 | 21447.2222 | 21422.2222 | 21416.6667 | 21288.8889
| Interior Equipment | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222 | 218247.2222
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 145436.1111 | 231133.3333 | 176741.6667 | 271508.3333 | 164316.6667 | 242822.2222 | 171172.2222 | 278419.4444 | 309375 | 236994.4444 | 343163.8889 | 367344.4444 | 376094.4444 | 416050 | 414091.6667 | 530300
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 1251950 | 1149522.2222 | 1018225 | 1032900 | 1045597.2222 | 922488.8889 | 954830.5556 | 965677.7778 | 884683.3333 | 906486.1111 | 924563.8889 | 849502.7778 | 905083.3333 | 821613.8889 | 839500 | 791377.7778
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 2316030.5556 | 2247775 | 2052750 | 2083938.8889 | 1895272.2222 | 1951944.4444 | 1790983.3333 | 1983038.8889 | 1903200 | 1810713.8889 | 1981216.6667 | 1906025 | 1986969.4444 | 1914775 | 1929352.7778 | 1984838.8889
Gas (MJ)
| Heating | 106270 | 1041840 | 1028030 | 1993150 | 1089820 | 1582220 | 2411840 | 3122910 | 2430180 | 3206080 | 3949120 | 3155430 | 4851120 | 4206010 | 5942770 | 9022530
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130 | 199130
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 16250 | 18270 | 17110 | 20210 | 19840 | 18510 | 21500 | 21740 | 21450 | 22540 | 23080 | 23020 | 24240 | 24450 | 26150 | 28470
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 321650 | 1259240 | 1244270 | 2212480 | 1308780 | 1799850 | 2632470 | 3343780 | 2650760 | 3427750 | 4171330 | 3377570 | 5074480 | 4429580 | 6168050 | 9250120
Purchased Cooling (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ) | 8659360 | 9351220 | 8634170 | 9714660 | 8131770 | 8826850 | 9080010 | 10482710 | 9502280 | 9946320 | 11303700 | 10239270 | 12227570 | 11322780 | 13113720 | 16395550
Energy - End Use Intensities
Electricity (MJ/m2)
| Heating (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling (elec) | 222.7833 | 178.4471 | 170.4152 | 102.9997 | 21.9145 | 109.1373 | 4.4059 | 68.0733 | 42.4154 | 6.36 | 46.1803 | 25.2464 | 39.538 | 14.8656 | 13.7079 | 2.9683
| Interior Lighting (elec) | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096 | 361.8096
| Exterior Lighting (elec) | 18.5085 | 18.4774 | 18.4702 | 18.5013 | 18.4989 | 18.4798 | 18.4606 | 18.4798 | 18.4774 | 18.4487 | 18.4535 | 18.4582 | 18.4678 | 18.4463 | 18.4415 | 18.3315
| Interior Equipment (elec) | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286 | 187.9286
| Exterior Equipment (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (elec) | 125.2323 | 199.0246 | 152.1889 | 233.7907 | 141.49 | 209.0897 | 147.3932 | 239.7418 | 266.397 | 204.0715 | 295.492 | 316.3134 | 323.8479 | 358.2529 | 356.5666 | 456.6314
| Pumps (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration (elec) | 1078.0307 | 989.8321 | 876.7745 | 889.4109 | 900.3442 | 794.3379 | 822.1867 | 831.5271 | 761.7843 | 780.5582 | 796.1247 | 731.4909 | 779.3503 | 707.4763 | 722.8777 | 681.4406
| Generators (elec) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 1994.2906 | 1935.517 | 1767.5846 | 1794.4408 | 1631.9834 | 1680.7828 | 1542.1822 | 1707.5577 | 1638.8099 | 1559.1718 | 1705.9886 | 1641.2424 | 1710.9422 | 1648.7769 | 1661.3296 | 1709.1076
Gas (MJ/m2)
| Heating (gas) | 25.4186 | 249.1969 | 245.8937 | 476.74 | 260.6732 | 378.45 | 576.8862 | 746.9665 | 581.2729 | 766.8599 | 944.587 | 754.7449 | 1160.3357 | 1006.0324 | 1421.4467 | 2158.0921
| Cooling (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment (gas) | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298 | 47.6298
| Exterior Equipment (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems (gas) | 3.8868 | 4.37 | 4.0925 | 4.834 | 4.7455 | 4.4274 | 5.1426 | 5.2 | 5.1306 | 5.3913 | 5.5205 | 5.5061 | 5.7979 | 5.8482 | 6.2548 | 6.8097
| Refrigeration (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators (gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 76.9352 | 301.1967 | 297.616 | 529.2014 | 313.0461 | 430.5048 | 629.6585 | 799.7962 | 634.0333 | 819.8809 | 997.7373 | 807.8784 | 1213.761 | 1059.5079 | 1475.3312 | 2212.5292
Purchased Cooling (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Purchased Heating (MJ/m2)
| Heating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Lighting | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Interior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fans | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Pumps | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Humidification | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Refrigeration | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Generators | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total End Uses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Building (MJ/m2) | 2071.2258 | 2236.7112 | 2065.2006 | 2323.6422 | 1945.0319 | 2111.2876 | 2171.8407 | 2507.3515 | 2272.8432 | 2379.0528 | 2703.7235 | 2449.1233 | 2924.7032 | 2708.2872 | 3136.6608 | 3921.6392
Peak Energy Demand
Electricity Peak Demand (kW)
| Jan | 422.8988 | 414.0476 | 346.1649 | 377.3623 | 353.6375 | 350.7526 | 350.8774 | 367.1621 | 352.1542 | 357.0715 | 357.6063 | 362.7376 | 358.4614 | 364.9239 | 359.3992 | 375.7845
| Feb | 443.9048 | 402.3938 | 354.0324 | 376.1478 | 367.9409 | 360.7435 | 350.3337 | 356.5133 | 353.7535 | 347.9512 | 359.4443 | 358.7213 | 358.1386 | 369.8259 | 364.4338 | 373.7919
| Mar | 437.8802 | 416.8592 | 388.4524 | 380.8795 | 363.0517 | 350.9952 | 349.0427 | 387.7115 | 357.4656 | 357.6437 | 372.5121 | 366.3639 | 368.5898 | 366.8644 | 365.7622 | 377.0619
| Apr | 453.1118 | 466.3726 | 394.7245 | 420.9104 | 368.3862 | 407.8912 | 360.1434 | 387.3334 | 373.0791 | 362.8469 | 386.8279 | 382.3426 | 380.4827 | 373.0988 | 372.4952 | 376.3509
| May | 473.7304 | 505.5784 | 447.0597 | 476.1831 | 395.2673 | 427.6551 | 362.8988 | 423.162 | 403.2728 | 374.9883 | 435.8474 | 406.0973 | 485.6698 | 385.2363 | 387.5198 | 394.3509
| Jun | 500.6595 | 510.3609 | 525.9733 | 495.4958 | 392.1729 | 489.8098 | 380.9119 | 513.9654 | 429.7162 | 388.3875 | 504.5555 | 432.9455 | 500.5116 | 438.2535 | 443.4482 | 420.6636
| Jul | 496.5133 | 527.7695 | 534.1347 | 533.5623 | 420.8113 | 497.9167 | 402.247 | 543.9463 | 441.2155 | 404.9446 | 535.0131 | 457.7991 | 505.3009 | 443.1157 | 487.5016 | 424.5922
| Aug | 489.5733 | 532.0498 | 525.2802 | 501.7703 | 442.3432 | 517.4136 | 389.1071 | 516.4072 | 455.5115 | 399.6847 | 509.6797 | 458.4125 | 500.7177 | 436.7377 | 464.1087 | 420.0243
| Sep | 481.8304 | 522.8837 | 494.63 | 468.0923 | 436.6625 | 472.103 | 404.6061 | 450.15 | 408.5006 | 419.744 | 464.878 | 417.6179 | 425.6071 | 412.9344 | 404.0243 | 387.0865
| Oct | 483.885 | 467.831 | 422.5231 | 417.5426 | 395.8723 | 424.5814 | 359.4984 | 419.2632 | 389.59 | 362.9807 | 403.582 | 385.6018 | 388.0081 | 376.7018 | 383.5096 | 383.2199
| Nov | 449.0144 | 426.7265 | 375.7006 | 385.8324 | 375.9811 | 353.9841 | 354.2701 | 403.3599 | 359.8282 | 364.1926 | 402.8371 | 361.8484 | 370.3735 | 366.2347 | 383.2662 | 374.1511
| Dec | 423.4633 | 423.1128 | 356.5323 | 380.6982 | 362.9574 | 349.4968 | 348.3643 | 367.3459 | 351.0134 | 351.2077 | 362.0092 | 356.8834 | 362.0428 | 363.1759 | 363.2038 | 379.0949
Time of Peak Electrical Demand
| Jan | 06-JAN-11:00 | 03-JAN-11:00 | 28-JAN-11:45 | 24-JAN-18:15 | 28-JAN-11:45 | 23-JAN-11:15 | 05-JAN-11:15 | 09-JAN-11:15 | 02-JAN-11:15 | 14-JAN-11:15 | 18-JAN-11:15 | 23-JAN-11:15 | 30-JAN-11:15 | 23-JAN-11:15 | 13-JAN-11:15 | 21-JAN-11:15
| Feb | 23-FEB-11:00 | 21-FEB-11:45 | 28-FEB-11:45 | 21-FEB-11:15 | 13-FEB-11:45 | 11-FEB-11:15 | 15-FEB-18:15 | 13-FEB-11:15 | 17-FEB-11:15 | 21-FEB-11:15 | 28-FEB-11:15 | 11-FEB-11:15 | 21-FEB-11:15 | 02-FEB-11:15 | 21-FEB-11:15 | 27-FEB-11:15
| Mar | 13-MAR-17:15 | 25-MAR-10:00 | 17-MAR-17:15 | 29-MAR-17:15 | 04-MAR-11:45 | 11-MAR-11:15 | 30-MAR-10:15 | 09-MAR-18:15 | 08-MAR-11:15 | 30-MAR-10:15 | 14-MAR-17:15 | 27-MAR-10:45 | 29-MAR-10:15 | 31-MAR-10:15 | 30-MAR-10:15 | 09-MAR-11:15
| Apr | 03-APR-17:15 | 29-APR-12:00 | 26-APR-17:15 | 14-APR-17:15 | 11-APR-15:00 | 21-APR-17:15 | 29-APR-10:45 | 04-APR-17:15 | 21-APR-17:15 | 29-APR-10:15 | 10-APR-10:15 | 26-APR-10:45 | 01-APR-17:15 | 24-APR-10:15 | 14-APR-10:15 | 14-APR-10:15
| May | 24-MAY-10:00 | 26-MAY-17:15 | 30-MAY-17:15 | 31-MAY-17:15 | 30-MAY-10:45 | 31-MAY-17:15 | 17-MAY-10:45 | 15-MAY-17:15 | 30-MAY-10:45 | 05-MAY-17:15 | 30-MAY-17:15 | 24-MAY-10:45 | 27-MAY-14:00 | 25-MAY-17:15 | 27-MAY-10:45 | 31-MAY-10:15
| Jun | 27-JUN-17:15 | 13-JUN-17:15 | 28-JUN-17:15 | 19-JUN-17:15 | 28-JUN-10:45 | 27-JUN-10:45 | 16-JUN-10:45 | 30-JUN-17:15 | 29-JUN-10:45 | 28-JUN-10:45 | 08-JUN-12:00 | 28-JUN-10:45 | 29-JUN-17:15 | 30-JUN-10:45 | 14-JUN-17:15 | 21-JUN-17:15
| Jul | 13-JUL-10:00 | 06-JUL-10:00 | 19-JUL-17:15 | 03-JUL-17:15 | 29-JUL-10:45 | 11-JUL-10:45 | 03-JUL-10:45 | 25-JUL-10:00 | 18-JUL-17:15 | 31-JUL-17:15 | 14-JUL-10:00 | 19-JUL-10:45 | 13-JUL-17:15 | 21-JUL-17:15 | 08-JUL-10:00 | 29-JUL-17:15
| Aug | 21-AUG-17:15 | 31-AUG-10:00 | 01-AUG-17:15 | 14-AUG-17:15 | 08-AUG-10:45 | 05-AUG-10:45 | 15-AUG-10:45 | 17-AUG-17:15 | 01-AUG-10:45 | 18-AUG-17:15 | 04-AUG-17:15 | 30-AUG-10:45 | 25-AUG-17:15 | 11-AUG-17:15 | 12-AUG-10:00 | 15-AUG-17:15
| Sep | 26-SEP-10:00 | 16-SEP-10:00 | 08-SEP-17:15 | 06-SEP-17:15 | 09-SEP-10:45 | 01-SEP-10:45 | 29-SEP-10:00 | 09-SEP-10:45 | 02-SEP-10:45 | 02-SEP-14:00 | 06-SEP-10:45 | 09-SEP-10:45 | 14-SEP-10:45 | 01-SEP-17:15 | 08-SEP-17:15 | 01-SEP-10:15
| Oct | 07-OCT-10:00 | 30-OCT-10:00 | 13-OCT-17:15 | 12-OCT-15:00 | 05-OCT-10:00 | 06-OCT-10:45 | 21-OCT-10:15 | 03-OCT-10:45 | 03-OCT-10:45 | 05-OCT-10:15 | 31-OCT-10:45 | 05-OCT-10:45 | 14-OCT-10:15 | 06-OCT-17:15 | 07-OCT-10:15 | 02-OCT-10:15
| Nov | 01-NOV-10:00 | 21-NOV-11:45 | 13-NOV-11:45 | 22-NOV-11:45 | 20-NOV-11:45 | 01-NOV-10:15 | 24-NOV-11:15 | 04-NOV-10:45 | 10-NOV-11:15 | 03-NOV-10:15 | 02-NOV-10:45 | 16-NOV-11:15 | 03-NOV-10:15 | 01-NOV-10:15 | 09-NOV-11:15 | 14-NOV-11:15
| Dec | 16-DEC-11:00 | 02-DEC-11:00 | 13-DEC-11:45 | 26-DEC-11:15 | 04-DEC-11:45 | 05-DEC-11:45 | 04-DEC-11:15 | 23-DEC-11:15 | 22-DEC-11:15 | 05-DEC-11:15 | 12-DEC-11:15 | 30-DEC-11:15 | 02-DEC-11:15 | 29-DEC-11:15 | 02-DEC-11:15 | 18-DEC-11:15
Source Energy
| Total Source Energy (GJ) | 28007.42 | 30765.18 | 24732.99 | 27653.36 | 22546.32 | 27101 | 22829.8 | 29180.25 | 25627.98 | 15098.45 | 29846.49 | 26455.4 | 30126.49 | 28797.85 | 30607.78 | 35624.58
| Total Source Energy (MJ/m2) | 6699.07 | 7358.69 | 5915.86 | 6614.38 | 5392.83 | 6482.26 | 5460.64 | 6979.59 | 6129.93 | 3611.38 | 7138.95 | 6327.84 | 7205.93 | 6888.13 | 7321.04 | 8521.01
Water Consumption (m3)
| Cooling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Water Systems | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12
| Total Building | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12 | 87.12
Emissions
| Carbon Equivalent (kg) | 640970.8599 | 772477.1571 | 642112.3686 | 681826.4358 | 245093.4922 | 690797.9324 | 256775.3291 | 595431.0381 | 825253.9522 | 193693.3006 | 1131500 | 839514.4001 | 771631.9628 | 779608.3372 | 771630.6531 | 725313.4789
| CO2 (kg) | 1487530 | 1946990 | 1522110 | 1572190 | 659535.4437 | 1653060 | 695960.0683 | 1374270 | 1949650 | 491868.0747 | 2654460 | 1990200 | 1832340 | 1858260 | 1843850 | 1881010
| NOX (kg) | 2609.0751 | 2532.4732 | 2521.9075 | 2917.9669 | 567.966 | 2642.2568 | 602.7299 | 2557.5575 | 3303.8019 | 665.4964 | 4635.0679 | 3342.898 | 3101.2573 | 3098.4569 | 3070.0172 | 2190.3029
| SO2 (kg) | 9913.621 | 10722.2207 | 8254.8514 | 7315.2156 | 5515.3669 | 10737.7319 | 5212.2533 | 7239.7787 | 8311.6069 | 1400.4559 | 13352.925 | 8324.1371 | 4690.9227 | 5113.8691 | 4555.2354 | 10106.106
| PM (kg) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Hg (kg) | 0.0452 | 0.0303 | 0.0225 | 0.0269 | 0.0026 | 0.0203 | 0.0026 | 0.0295 | 0.0326 | 0.0058 | 0.0407 | 0.0328 | 0.0347 | 0.0359 | 0.0339 | 0.0352
| Water for Electricity (m3) | 1226.94 | 3657.39 | 60975.7 | 13011.3 | 33276.7 | 53549.6 | 31445.7 | 450.2242 | 8642.05 | 18499.7 | 3073.74 | 8654.88 | 3082.66 | 121290 | 2993.28 | 2027.87

## Miami (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8659.36 | 2071.22 | 2071.22
Net Site Energy | 8659.36 | 2071.22 | 2071.22
Total Source Energy | 28007.42 | 6699.07 | 6699.07
Net Source Energy | 28007.42 | 6699.07 | 6699.07
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 106.27 | 0 | 0 | 0 | 0
Cooling | 931.41 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.38 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 523.57 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 16.25 | 0 | 0 | 0 | 87.12
Refrigeration | 4507.02 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8337.71 | 321.65 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.421 | 0.457 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.251 | 0.11 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 13332.59 | 9343.49 | 3989.1 | 0.7 | 2.99
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 61002.78 | 41242.96 | 19759.82 | 0.68 | 2.62
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 62975.44 | 42576.64 | 20398.8 | 0.68 | 2.62
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 169404.15 | 114531.3 | 54872.85 | 0.68 | 2.89
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 68991.3 | 46643.86 | 22347.44 | 0.68 | 2.62
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 54955.25 | 39215.01 | 15740.24 | 0.71 | 2.67
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 14709.42 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 65119.43 | 0.8
PSZ-AC:3_HEATC | Coil:Heating:Gas | 98184.44 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 211584 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 80655.12 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 65076.14 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.59 | 685.57 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.46 | 2686.58 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.54 | 2773.46 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.82 | 12797.82 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.78 | 3038.4 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.55 | 2790.54 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.78 | 1.67 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 113969.8095 | 198.409 | 747.8224 | 0 | 0.0034 | 92551.3106 | 48959.8488
February | 103778.1699 | 181.2518 | 685.5561 | 0 | 0.0031 | 84845.6221 | 44640.3134
March | 117140.9433 | 204.8897 | 776.1871 | 0 | 0.0035 | 96062.4961 | 50418.3316
April | 119552.7937 | 209.902 | 798.4155 | 0 | 0.0036 | 98814.1282 | 51535.9424
May | 131417.9855 | 230.936 | 879.245 | 0 | 0.004 | 108817.9703 | 56670.9397
June | 132896.0914 | 233.5782 | 889.4865 | 0 | 0.0041 | 110085.5222 | 57312.8235
July | 139642.3253 | 245.4685 | 934.9007 | 0 | 0.0043 | 115706.1352 | 60225.5289
August | 140407.4025 | 246.7984 | 939.9047 | 0 | 0.0043 | 116325.4394 | 60553.9908
September | 131366.7298 | 230.8906 | 879.2539 | 0 | 0.004 | 108819.1057 | 56653.3159
October | 128470.885 | 225.7278 | 859.296 | 0 | 0.0039 | 106348.9958 | 55397.1226
November | 116425.8815 | 204.3367 | 776.9399 | 0 | 0.0035 | 96156.1899 | 50180.4666
December | 112460.7318 | 196.8863 | 746.6132 | 0 | 0.0034 | 92402.505 | 48422.2357
Annual Sum or Average | 1487530 | 2609.0751 | 9913.621 | 0 | 0.0452 | 1226940 | 640970.8599
Minimum of Months | 103778.1699 | 181.2518 | 685.5561 | 0 | 0.0031 | 84845.6221 | 44640.3134
Maximum of Months | 140407.4025 | 246.7984 | 939.9047 | 0 | 0.0043 | 116325.4394 | 60553.9908
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 628938000000 | 422898.835 | 06-JAN-11:00 | 101872.638 | 41401.92 | 24903.294 | 0 | 47477.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207243.214 | 0 | 0
February | 576573000000 | 443904.817 | 23-FEB-11:00 | 101872.638 | 41401.92 | 24903.294 | 0 | 66922.79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208804.175 | 0 | 0
March | 652798000000 | 437880.163 | 13-MAR-17:15 | 67915.092 | 36859.929 | 24903.294 | 0 | 69717.159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238484.69 | 0 | 0
April | 671497000000 | 453111.841 | 03-APR-17:15 | 67915.092 | 36859.929 | 24903.294 | 0 | 84559.698 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238873.828 | 0 | 0
May | 739479000000 | 473730.437 | 24-MAY-10:00 | 101872.638 | 41401.92 | 24903.294 | 0 | 90289.07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215263.515 | 0 | 0
June | 748092000000 | 500659.455 | 27-JUN-17:15 | 67915.092 | 36859.929 | 24903.294 | 0 | 125527.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245453.201 | 0 | 0
July | 786287000000 | 496513.263 | 13-JUL-10:00 | 101872.638 | 41401.92 | 24903.294 | 0 | 110829.057 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217506.354 | 0 | 0
August | 790496000000 | 489573.338 | 21-AUG-17:15 | 67915.092 | 36859.929 | 24903.294 | 0 | 115254.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244640.035 | 0 | 0
September | 739486000000 | 481830.445 | 26-SEP-10:00 | 101872.638 | 41401.92 | 24903.294 | 0 | 96583.455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217069.137 | 0 | 0
October | 722701000000 | 483884.955 | 07-OCT-10:00 | 101872.638 | 41401.92 | 24903.294 | 0 | 99691.48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216015.623 | 0 | 0
November | 653435000000 | 449014.367 | 01-NOV-10:00 | 101872.638 | 41401.92 | 24903.294 | 0 | 69874.285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210962.229 | 0 | 0
December | 627926000000 | 423463.258 | 16-DEC-11:00 | 101872.638 | 41401.92 | 24903.294 | 0 | 49956.843 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205328.563 | 0 | 0
Annual Sum or Average | 8337710000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 576573000000 | 422898.835 |  | 67915.092 | 36859.929 | 24903.294 | 0 | 47477.769 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205328.563 | 0 | 0
Maximum of Months | 790496000000 | 500659.455 |  | 101872.638 | 41401.92 | 24903.294 | 0 | 125527.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245453.201 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 187605.26 | 3680.33 | 0 | 191285.59
Cost per Total Building Area ($/m2) | 44.87 | 0.88 | 0 | 45.75
Cost per Net Conditioned Building Area ($/m2) | 44.87 | 0.88 | 0 | 45.75

## Houston (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 9351.22 | 2236.71 | 2236.71
Net Site Energy | 9351.22 | 2236.71 | 2236.71
Total Source Energy | 30765.18 | 7358.69 | 7358.69
Net Source Energy | 30765.18 | 7358.69 | 7358.69
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1041.84 | 0 | 0 | 0 | 0
Cooling | 746.05 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.25 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 832.08 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 18.27 | 0 | 0 | 0 | 87.12
Refrigeration | 4138.28 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 8091.99 | 1259.24 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.931 | 2.715 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.375 | 0.404 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.251 | 0.11 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 16239.32 | 11314.52 | 4924.8 | 0.7 | 2.98
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 90324.46 | 61066.85 | 29257.61 | 0.68 | 2.9
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 61039.03 | 41267.47 | 19771.57 | 0.68 | 2.62
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 265602.86 | 179569.64 | 86033.22 | 0.68 | 2.75
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 91448.27 | 61826.64 | 29621.63 | 0.68 | 2.9
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 53748.38 | 38325.6 | 15422.78 | 0.71 | 2.67
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 17895 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 97875.87 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 125631.37 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 343418.48 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 116264.33 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 66869.47 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.71 | 822.45 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.64 | 6938.03 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.46 | 2688.18 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1017.59 | 10.7 | 18400.66 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.68 | 7024.35 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.49 | 2724.19 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.78 | 1.67 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 149030.1643 | 189.7972 | 764.0281 | 0 | 0.0022 | 260594.9489 | 58606.5471
February | 133592.9844 | 169.8826 | 681.3208 | 0 | 0.0019 | 232383.8816 | 52503.0112
March | 147598.1067 | 191.1725 | 801.4903 | 0 | 0.0023 | 273387.9089 | 58455.7351
April | 151940.171 | 198.8009 | 853.1432 | 0 | 0.0024 | 291015.7873 | 60433.7774
May | 171811.0097 | 225.3228 | 972.036 | 0 | 0.0027 | 331573.6084 | 68404.6997
June | 181530.4108 | 238.2204 | 1029.1401 | 0 | 0.0029 | 351053.1762 | 72293.8461
July | 193245.3768 | 253.6167 | 1095.8755 | 0 | 0.0031 | 373817.5755 | 76962.2383
August | 191765.7626 | 251.6543 | 1087.196 | 0 | 0.0031 | 370856.8098 | 76370.3074
September | 172228.927 | 225.9888 | 976.052 | 0 | 0.0027 | 332944 | 68586.2885
October | 162081.8709 | 212.2135 | 912.0916 | 0 | 0.0026 | 311124.3089 | 64486.0428
November | 144308.5635 | 187.5781 | 792.9601 | 0 | 0.0022 | 270481.2913 | 57238.816
December | 147859.9479 | 188.2254 | 756.887 | 0 | 0.0022 | 258158.8539 | 58135.8473
Annual Sum or Average | 1946990 | 2532.4732 | 10722.2207 | 0 | 0.0303 | 3657390 | 772477.1571
Minimum of Months | 133592.9844 | 169.8826 | 681.3208 | 0 | 0.0019 | 232383.8816 | 52503.0112
Maximum of Months | 193245.3768 | 253.6167 | 1095.8755 | 0 | 0.0031 | 373817.5755 | 76962.2383
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 576567000000 | 414047.583 | 03-JAN-11:00 | 101872.638 | 41401.92 | 38728.766 | 0 | 27709.508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204334.752 | 0 | 0
February | 514150000000 | 402393.824 | 21-FEB-11:45 | 101872.638 | 41401.92 | 38728.766 | 0 | 20375.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200015.262 | 0 | 0
March | 604871000000 | 416859.153 | 25-MAR-10:00 | 101872.638 | 41401.92 | 38728.766 | 0 | 30843.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204012.249 | 0 | 0
April | 643873000000 | 466372.618 | 29-APR-12:00 | 101872.638 | 41401.92 | 38728.766 | 0 | 97956.739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186412.555 | 0 | 0
May | 733607000000 | 505578.443 | 26-MAY-17:15 | 67915.092 | 36859.929 | 38728.766 | 0 | 118172.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243902.361 | 0 | 0
June | 776706000000 | 510360.928 | 13-JUN-17:15 | 67915.092 | 36859.929 | 38728.766 | 0 | 122830.735 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244026.406 | 0 | 0
July | 827072000000 | 527769.539 | 06-JUL-10:00 | 101872.638 | 41401.92 | 38728.766 | 0 | 125074.618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220691.597 | 0 | 0
August | 820521000000 | 532049.763 | 31-AUG-10:00 | 101872.638 | 41401.92 | 38728.766 | 0 | 128510.739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221535.7 | 0 | 0
September | 736639000000 | 522883.711 | 16-SEP-10:00 | 101872.638 | 41401.92 | 38728.766 | 0 | 122704.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218176.286 | 0 | 0
October | 688363000000 | 467830.997 | 30-OCT-10:00 | 101872.638 | 41401.92 | 38728.766 | 0 | 75772.362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210055.311 | 0 | 0
November | 598440000000 | 426726.508 | 21-NOV-11:45 | 101872.638 | 41401.92 | 38728.766 | 0 | 37473.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207249.991 | 0 | 0
December | 571177000000 | 423112.838 | 02-DEC-11:00 | 101872.638 | 41401.92 | 38728.766 | 0 | 32464.963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208644.552 | 0 | 0
Annual Sum or Average | 8091990000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 514150000000 | 402393.824 |  | 67915.092 | 36859.929 | 38728.766 | 0 | 20375.239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186412.555 | 0 | 0
Maximum of Months | 827072000000 | 532049.763 |  | 101872.638 | 41401.92 | 38728.766 | 0 | 128510.739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244026.406 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 234191.84 | 10169.75 | 0 | 244361.59
Cost per Total Building Area ($/m2) | 56.02 | 2.43 | 0 | 58.45
Cost per Net Conditioned Building Area ($/m2) | 56.02 | 2.43 | 0 | 58.45

## Phoenix (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8634.17 | 2065.2 | 2065.2
Net Site Energy | 8634.17 | 2065.2 | 2065.2
Total Source Energy | 24732.99 | 5915.86 | 5915.86
Net Source Energy | 24732.99 | 5915.86 | 5915.86
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1028.03 | 0 | 0 | 0 | 0
Cooling | 712.47 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.22 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 636.27 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 17.11 | 0 | 0 | 0 | 87.12
Refrigeration | 3665.61 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7389.9 | 1244.27 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.328 | 3.573 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.261 | 0.275 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.251 | 0.11 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11772.52 | 8751.8 | 3020.72 | 0.74 | 3.07
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 71544.23 | 49861.83 | 21682.4 | 0.7 | 2.65
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 58033.12 | 39235.22 | 18797.9 | 0.68 | 2.62
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 237148.65 | 160332.22 | 76816.43 | 0.68 | 2.75
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 79156.2 | 54814.44 | 24341.76 | 0.69 | 2.65
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 49711.01 | 37185.42 | 12525.59 | 0.75 | 2.72
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 14591.56 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 80614.81 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 100774.79 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 284311.01 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 97571.6 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 65303.48 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.6 | 700.95 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.13 | 3418.93 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.34 | 2555.8 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1017.59 | 9.55 | 16429.38 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.4 | 3719.36 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.59 | 2832 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.78 | 1.67 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 115212.0771 | 183.4036 | 570.6807 | 0 | 0.0016 | 4215040 | 47845.9496
February | 102993.9992 | 164.6195 | 514.9759 | 0 | 0.0014 | 3803640 | 42839.2632
March | 115320.0826 | 190.4566 | 620.9938 | 0 | 0.0017 | 4587030 | 48586.6326
April | 112830.6993 | 188.4282 | 622.6566 | 0 | 0.0017 | 4599420 | 47748.4371
May | 125343.1661 | 210.578 | 700.7775 | 0 | 0.0019 | 5176550 | 53170.3427
June | 140942.764 | 237.4236 | 792.6091 | 0 | 0.0022 | 5854920 | 59852.1916
July | 160383.1762 | 270.3338 | 903.1066 | 0 | 0.0025 | 6671170 | 68124.0611
August | 157851.1556 | 266.0409 | 888.6677 | 0 | 0.0024 | 6564510 | 67046.0311
September | 142128.0128 | 239.4565 | 799.5368 | 0 | 0.0022 | 5906100 | 60359.1809
October | 122307.0824 | 204.8506 | 679.269 | 0 | 0.0018 | 5017630 | 51819.0592
November | 110472.9604 | 182.2702 | 593.5819 | 0 | 0.0016 | 4384540 | 46526.1269
December | 116329.4763 | 184.0461 | 567.996 | 0 | 0.0016 | 4195150 | 48195.0926
Annual Sum or Average | 1522110 | 2521.9075 | 8254.8514 | 0 | 0.0225 | 60975700 | 642112.3686
Minimum of Months | 102993.9992 | 164.6195 | 514.9759 | 0 | 0.0014 | 3803640 | 42839.2632
Maximum of Months | 160383.1762 | 270.3338 | 903.1066 | 0 | 0.0025 | 6671170 | 68124.0611
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 510838000000 | 346164.857 | 28-JAN-11:45 | 101872.638 | 41401.92 | 29787.329 | 0 | 4062.612 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169040.358 | 0 | 0
February | 460979000000 | 354032.445 | 28-FEB-11:45 | 101872.638 | 41401.92 | 29787.329 | 0 | 6250.396 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174720.162 | 0 | 0
March | 555922000000 | 388452.409 | 17-MAR-17:15 | 67915.092 | 36859.929 | 29787.329 | 0 | 44415.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 209474.73 | 0 | 0
April | 557423000000 | 394724.457 | 26-APR-17:15 | 67915.092 | 36859.929 | 29787.329 | 0 | 52523.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207638.842 | 0 | 0
May | 627367000000 | 447059.669 | 30-MAY-17:15 | 67915.092 | 36859.929 | 29787.329 | 0 | 97188.652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215308.668 | 0 | 0
June | 709583000000 | 525973.313 | 28-JUN-17:15 | 67915.092 | 36859.929 | 29787.329 | 0 | 168723.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222687.875 | 0 | 0
July | 808506000000 | 534134.717 | 19-JUL-17:15 | 67915.092 | 36859.929 | 29787.329 | 0 | 165941.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233631.307 | 0 | 0
August | 795580000000 | 525280.204 | 01-AUG-17:15 | 67915.092 | 36859.929 | 29787.329 | 0 | 164028.635 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226689.219 | 0 | 0
September | 715785000000 | 494630.035 | 08-SEP-17:15 | 67915.092 | 36859.929 | 29787.329 | 0 | 127479.289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232588.397 | 0 | 0
October | 608108000000 | 422523.091 | 13-OCT-17:15 | 67915.092 | 36859.929 | 29787.329 | 0 | 65234.118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222726.623 | 0 | 0
November | 531381000000 | 375700.58 | 13-NOV-11:45 | 101872.638 | 41401.92 | 29787.329 | 0 | 17273.627 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185365.066 | 0 | 0
December | 508427000000 | 356532.345 | 13-DEC-11:45 | 101872.638 | 41401.92 | 29787.329 | 0 | 40.808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183429.651 | 0 | 0
Annual Sum or Average | 7389900000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 460979000000 | 346164.857 |  | 67915.092 | 36859.929 | 29787.329 | 0 | 40.808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169040.358 | 0 | 0
Maximum of Months | 808506000000 | 534134.717 |  | 101872.638 | 41401.92 | 29787.329 | 0 | 168723.089 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 233631.307 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 159232.03 | 10267.21 | 0 | 169499.25
Cost per Total Building Area ($/m2) | 38.09 | 2.46 | 0 | 40.54
Cost per Net Conditioned Building Area ($/m2) | 38.09 | 2.46 | 0 | 40.54

## Atlanta (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 9714.66 | 2323.64 | 2323.64
Net Site Energy | 9714.66 | 2323.64 | 2323.64
Total Source Energy | 27653.36 | 6614.38 | 6614.38
Net Source Energy | 27653.36 | 6614.38 | 6614.38
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1993.15 | 0 | 0 | 0 | 0
Cooling | 430.62 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.35 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 977.43 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 20.21 | 0 | 0 | 0 | 87.12
Refrigeration | 3718.44 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7502.18 | 2212.48 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.409 | 0.444 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 4.092 | 0.255 | 0.129 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 4.09 | 0.255 | 0.129
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 4.09 | 0.255 | 0.129
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18236.64 | 13036.47 | 5200.17 | 0.71 | 3.02
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 107762.59 | 72856.48 | 34906.11 | 0.68 | 2.9
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56942.56 | 38497.91 | 18444.65 | 0.68 | 2.62
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 310175.45 | 209704.42 | 100471.03 | 0.68 | 2.74
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 108350.25 | 73253.78 | 35096.46 | 0.68 | 2.9
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 50332.94 | 36945.61 | 13387.33 | 0.73 | 2.7
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 20641.67 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 113203.49 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 126428.54 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 391793.96 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 133265.25 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 66828.44 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.85 | 986.57 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.34 | 8277.49 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.29 | 2507.77 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 12.49 | 21163.01 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.36 | 8322.63 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.51 | 2740.73 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.78 | 1.67 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 131255.4256 | 225.8139 | 523.4864 | 0 | 0.002 | 930931.9463 | 55279.3128
February | 116369.7943 | 203.5608 | 480.5713 | 0 | 0.0018 | 854652.5058 | 49320.0786
March | 122244.9076 | 222.7901 | 548.7179 | 0 | 0.002 | 975942.5372 | 52636.8409
April | 120293.2308 | 225.4327 | 570.3479 | 0 | 0.0021 | 1014480 | 52369.0191
May | 132876.1107 | 254.5485 | 657.1413 | 0 | 0.0024 | 1168910 | 58358.1021
June | 139815.9407 | 268.8761 | 696.5263 | 0 | 0.0025 | 1238970 | 61501.421
July | 150401.4117 | 289.4039 | 750.0994 | 0 | 0.0027 | 1334270 | 66173.5033
August | 149974.875 | 288.5547 | 747.8328 | 0 | 0.0027 | 1330240 | 65983.2125
September | 137119.7129 | 263.6512 | 682.8992 | 0 | 0.0025 | 1214730 | 60311.7426
October | 124231.9887 | 234.5001 | 597.288 | 0 | 0.0022 | 1062410 | 54239.4498
November | 119107.9083 | 215.9719 | 529.2398 | 0 | 0.002 | 941287.9873 | 51184.4158
December | 128501.9437 | 224.8631 | 531.0654 | 0 | 0.002 | 944452.6095 | 54469.3374
Annual Sum or Average | 1572190 | 2917.9669 | 7315.2156 | 0 | 0.0269 | 13011300 | 681826.4358
Minimum of Months | 116369.7943 | 203.5608 | 480.5713 | 0 | 0.0018 | 854652.5058 | 49320.0786
Maximum of Months | 150401.4117 | 289.4039 | 750.0994 | 0 | 0.0027 | 1334270 | 66173.5033
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 536767000000 | 377362.298 | 24-JAN-18:15 | 67915.092 | 36859.929 | 44129.107 | 0 | 4221.9 | 4916 | 0 | 0 | 0 | 0 | 0 | 0 | 219320.269 | 0 | 0
February | 492785000000 | 376147.77 | 21-FEB-11:15 | 101872.638 | 41401.92 | 44129.107 | 0 | 3241.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185502.998 | 0 | 0
March | 562719000000 | 380879.531 | 29-MAR-17:15 | 67915.092 | 36859.929 | 44129.107 | 0 | 9549.92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222425.482 | 0 | 0
April | 584937000000 | 420910.421 | 14-APR-17:15 | 67915.092 | 36859.929 | 44129.107 | 0 | 42502.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 229503.862 | 0 | 0
May | 673981000000 | 476183.11 | 31-MAY-17:15 | 67915.092 | 36859.929 | 44129.107 | 0 | 87275.801 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 240003.18 | 0 | 0
June | 714380000000 | 495495.797 | 19-JUN-17:15 | 67915.092 | 36859.929 | 44129.107 | 0 | 109461.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237130.217 | 0 | 0
July | 769327000000 | 533562.343 | 03-JUL-17:15 | 67915.092 | 36859.929 | 44129.107 | 0 | 141518.954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243139.26 | 0 | 0
August | 767003000000 | 501770.342 | 14-AUG-17:15 | 67915.092 | 36859.929 | 44129.107 | 0 | 110680.865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242185.349 | 0 | 0
September | 700404000000 | 468092.321 | 06-SEP-17:15 | 67915.092 | 36859.929 | 44129.107 | 0 | 81946.525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237241.668 | 0 | 0
October | 612575000000 | 417542.619 | 12-OCT-15:00 | 101872.638 | 41401.92 | 44129.107 | 0 | 71504.912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158634.042 | 0 | 0
November | 542738000000 | 385832.354 | 22-NOV-11:45 | 101872.638 | 41401.92 | 44129.107 | 0 | 8974.19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189454.498 | 0 | 0
December | 544562000000 | 380698.232 | 26-DEC-11:15 | 101872.638 | 41401.92 | 44129.107 | 0 | 4349.29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188945.276 | 0 | 0
Annual Sum or Average | 7502180000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 492785000000 | 376147.77 |  | 67915.092 | 36859.929 | 44129.107 | 0 | 3241.106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158634.042 | 0 | 0
Maximum of Months | 769327000000 | 533562.343 |  | 101872.638 | 41401.92 | 44129.107 | 0 | 141518.954 | 4916 | 0 | 0 | 0 | 0 | 0 | 0 | 243139.26 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 205326.52 | 21488.75 | 0 | 226815.27
Cost per Total Building Area ($/m2) | 49.11 | 5.14 | 0 | 54.25
Cost per Net Conditioned Building Area ($/m2) | 49.11 | 5.14 | 0 | 54.25

## LosAngeles (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8131.77 | 1945.03 | 1945.03
Net Site Energy | 8131.77 | 1945.03 | 1945.03
Total Source Energy | 22546.32 | 5392.83 | 5392.83
Net Source Energy | 22546.32 | 5392.83 | 5392.83
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1089.82 | 0 | 0 | 0 | 0
Cooling | 91.62 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.34 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 591.54 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 19.84 | 0 | 0 | 0 | 87.12
Refrigeration | 3764.15 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6822.98 | 1308.78 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.569 | 0.637 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.44 | 0.272 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.44 | 0.272
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.44 | 0.272
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9378.72 | 7091.32 | 2287.39 | 0.76 | 3.1
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56399.12 | 40537.89 | 15861.23 | 0.72 | 2.68
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 58424.83 | 39500.05 | 18924.78 | 0.68 | 2.62
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 211564 | 143034.87 | 68529.13 | 0.68 | 2.89
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 63369.92 | 45366.9 | 18003.01 | 0.72 | 2.68
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 41387.72 | 32393.08 | 8994.64 | 0.78 | 2.78
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 12619.3 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 70662.37 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 94737.09 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 255719.84 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 86485.69 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 61633.28 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.5 | 581.12 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.67 | 2916.43 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.35 | 2573.05 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 8.52 | 15982.84 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.97 | 3244.31 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.39 | 2615.46 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.78 | 1.67 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 57387.2242 | 49.7249 | 425.2874 | 0 | 0.0002 | 2565750 | 21159.3499
February | 51848.4152 | 44.8831 | 391.836 | 0 | 0.0002 | 2363970 | 19140.2998
March | 56495.7146 | 48.7998 | 445.9779 | 0 | 0.0002 | 2690690 | 20913.9229
April | 53881.326 | 46.468 | 438.5077 | 0 | 0.0002 | 2645670 | 19986.2873
May | 55144.6539 | 47.4156 | 474.1803 | 0 | 0.0002 | 2861000 | 20532.3629
June | 53687.9243 | 46.107 | 471.6678 | 0 | 0.0002 | 2845870 | 20020.5206
July | 55781.2609 | 47.8209 | 505.0702 | 0 | 0.0002 | 3047460 | 20846.9373
August | 57561.7125 | 49.3371 | 523.0034 | 0 | 0.0002 | 3155670 | 21517.8682
September | 53966.1203 | 46.2636 | 488.8481 | 0 | 0.0002 | 2949580 | 20169.2212
October | 54165.31 | 46.5051 | 477.998 | 0 | 0.0002 | 2884070 | 20205.0578
November | 53401.2305 | 46.0242 | 439.9109 | 0 | 0.0002 | 2654160 | 19824.4063
December | 56214.5513 | 48.6166 | 433.0791 | 0 | 0.0002 | 2612830 | 20777.258
Annual Sum or Average | 659535.4437 | 567.966 | 5515.3669 | 0 | 0.0026 | 33276700 | 245093.4922
Minimum of Months | 51848.4152 | 44.8831 | 391.836 | 0 | 0.0002 | 2363970 | 19140.2998
Maximum of Months | 57561.7125 | 49.7249 | 523.0034 | 0 | 0.0002 | 3155670 | 21517.8682
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 526075000000 | 353637.484 | 28-JAN-11:45 | 101872.638 | 41401.92 | 28044.119 | 0 | 6652.84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175665.966 | 0 | 0
February | 484703000000 | 367940.913 | 13-FEB-11:45 | 101872.638 | 41401.92 | 28044.119 | 0 | 12308.331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184313.905 | 0 | 0
March | 551693000000 | 363051.719 | 04-MAR-11:45 | 101872.638 | 41401.92 | 28044.119 | 0 | 9826.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181906.044 | 0 | 0
April | 542462000000 | 368386.181 | 11-APR-15:00 | 101872.638 | 41401.92 | 28044.119 | 0 | 42825.76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154241.744 | 0 | 0
May | 586612000000 | 395267.302 | 30-MAY-10:45 | 101872.638 | 41401.92 | 28044.119 | 0 | 23086.077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200862.548 | 0 | 0
June | 583511000000 | 392172.856 | 28-JUN-10:45 | 101872.638 | 41401.92 | 28044.119 | 0 | 21395.847 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199458.332 | 0 | 0
July | 624845000000 | 420811.271 | 29-JUL-10:45 | 101872.638 | 41401.92 | 28044.119 | 0 | 42984.076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206508.518 | 0 | 0
August | 647032000000 | 442343.182 | 08-AUG-10:45 | 101872.638 | 41401.92 | 28044.119 | 0 | 63006.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208017.864 | 0 | 0
September | 604776000000 | 436662.498 | 09-SEP-10:45 | 101872.638 | 41401.92 | 28044.119 | 0 | 56920.249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208423.572 | 0 | 0
October | 591344000000 | 395872.323 | 05-OCT-10:00 | 101872.638 | 41401.92 | 28044.119 | 0 | 30570.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 193982.974 | 0 | 0
November | 544202000000 | 375981.094 | 20-NOV-11:45 | 101872.638 | 41401.92 | 28044.119 | 0 | 13376.717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191285.7 | 0 | 0
December | 535728000000 | 362957.362 | 04-DEC-11:45 | 101872.638 | 41401.92 | 28044.119 | 0 | 6123.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185514.899 | 0 | 0
Annual Sum or Average | 6822980000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 484703000000 | 353637.484 |  | 101872.638 | 41401.92 | 28044.119 | 0 | 6123.785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154241.744 | 0 | 0
Maximum of Months | 647032000000 | 442343.182 |  | 101872.638 | 41401.92 | 28044.119 | 0 | 63006.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 208423.572 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 234226.69 | 11198.49 | 0 | 245425.18
Cost per Total Building Area ($/m2) | 56.02 | 2.68 | 0 | 58.7
Cost per Net Conditioned Building Area ($/m2) | 56.02 | 2.68 | 0 | 58.7

## LasVegas (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 8826.85 | 2111.29 | 2111.29
Net Site Energy | 8826.85 | 2111.29 | 2111.29
Total Source Energy | 27101 | 6482.26 | 6482.26
Net Source Energy | 27101 | 6482.26 | 6482.26
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 1582.22 | 0 | 0 | 0 | 0
Cooling | 456.28 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 874.16 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 18.51 | 0 | 0 | 0 | 87.12
Refrigeration | 3320.96 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7027 | 1799.85 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.647 | 2.185 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.273 | 0.288 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 5.835 | 0.251 | 0.11 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 5.83 | 0.251 | 0.11
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 5.83 | 0.251 | 0.11
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 12754.36 | 9845.84 | 2908.52 | 0.77 | 3.13
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 76043.36 | 55138.7 | 20904.66 | 0.73 | 3.06
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 46805.74 | 33750.27 | 13055.48 | 0.72 | 2.69
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 269659.85 | 184983.9 | 84675.95 | 0.69 | 2.76
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 78442.89 | 57847.29 | 20595.59 | 0.74 | 3.1
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 41898.92 | 32837.76 | 9061.17 | 0.78 | 2.78
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 16675.91 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 91204.53 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 103992.55 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 328538.8 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 110998.81 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 60412.04 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.71 | 828.8 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.67 | 7009.17 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.23 | 2439.72 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 11.3 | 19142.36 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.95 | 7533.95 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.43 | 2655.78 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.78 | 1.67 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 136407.1091 | 207.5504 | 787.5228 | 0 | 0.0015 | 3927030 | 55913.5688
February | 117456.1844 | 183.4489 | 722.6029 | 0 | 0.0014 | 3603500 | 48637.5152
March | 130099.6817 | 203.7219 | 805.3283 | 0 | 0.0015 | 4016060 | 53927.7109
April | 123961.2798 | 200.2715 | 825.2468 | 0 | 0.0016 | 4115630 | 52023.7123
May | 134625.7046 | 218.7044 | 907.555 | 0 | 0.0017 | 4526150 | 56624.4149
June | 148028.9313 | 241.9567 | 1011.8047 | 0 | 0.0019 | 5046120 | 62415.5392
July | 164861.4173 | 269.6602 | 1128.648 | 0 | 0.0021 | 5628850 | 69532.6554
August | 166366.932 | 272.0871 | 1138.6193 | 0 | 0.0021 | 5678580 | 70163.9173
September | 143229.8932 | 233.9734 | 977.6944 | 0 | 0.0018 | 4876000 | 60377.5893
October | 130483.3915 | 211.1949 | 872.2971 | 0 | 0.0016 | 4350290 | 54801.0406
November | 123786.1195 | 194.7394 | 774.7428 | 0 | 0.0015 | 3863570 | 51404.6205
December | 133756.0366 | 204.9479 | 785.6699 | 0 | 0.0015 | 3917850 | 54975.6481
Annual Sum or Average | 1653060 | 2642.2568 | 10737.7319 | 0 | 0.0203 | 53549600 | 690797.9324
Minimum of Months | 117456.1844 | 183.4489 | 722.6029 | 0 | 0.0014 | 3603500 | 48637.5152
Maximum of Months | 166366.932 | 272.0871 | 1138.6193 | 0 | 0.0021 | 5678580 | 70163.9173
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 515320000000 | 350752.614 | 23-JAN-11:15 | 101872.638 | 41401.92 | 39740.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167737.356 | 0 | 0
February | 472865000000 | 360743.461 | 11-FEB-11:15 | 101872.638 | 41401.92 | 39740.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177728.204 | 0 | 0
March | 527003000000 | 350995.204 | 11-MAR-11:15 | 101872.638 | 41401.92 | 39740.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167979.946 | 0 | 0
April | 540069000000 | 407891.242 | 21-APR-17:15 | 67915.092 | 36859.929 | 39740.7 | 0 | 49315.081 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214060.44 | 0 | 0
May | 593940000000 | 427655.103 | 31-MAY-17:15 | 67915.092 | 36859.929 | 39740.7 | 0 | 72077.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211062.336 | 0 | 0
June | 662172000000 | 489809.817 | 27-JUN-10:45 | 101872.638 | 41401.92 | 39740.7 | 0 | 105819.547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200975.012 | 0 | 0
July | 738641000000 | 497916.721 | 11-JUL-10:45 | 101872.638 | 41401.92 | 39740.7 | 0 | 97262.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 217639.403 | 0 | 0
August | 745166000000 | 517413.566 | 05-AUG-10:45 | 101872.638 | 41401.92 | 39740.7 | 0 | 110069.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224329.153 | 0 | 0
September | 639848000000 | 472102.965 | 01-SEP-10:45 | 101872.638 | 41401.92 | 39740.7 | 0 | 85644.594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203443.113 | 0 | 0
October | 570862000000 | 424581.44 | 06-OCT-10:45 | 101872.638 | 41401.92 | 39740.7 | 0 | 41355.797 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200210.386 | 0 | 0
November | 506993000000 | 353984.067 | 01-NOV-10:15 | 101872.638 | 41401.92 | 39740.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170968.809 | 0 | 0
December | 514116000000 | 349496.803 | 05-DEC-11:45 | 101872.638 | 41401.92 | 39740.7 | 0 | 1587.303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164894.243 | 0 | 0
Annual Sum or Average | 7027000000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 472865000000 | 349496.803 |  | 67915.092 | 36859.929 | 39740.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164894.243 | 0 | 0
Maximum of Months | 745166000000 | 517413.566 |  | 101872.638 | 41401.92 | 39740.7 | 0 | 110069.156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224329.153 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 182129.27 | 13929.6 | 0 | 196058.87
Cost per Total Building Area ($/m2) | 43.56 | 3.33 | 0 | 46.9
Cost per Net Conditioned Building Area ($/m2) | 43.56 | 3.33 | 0 | 46.9

## SanFrancisco (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 9080.01 | 2171.84 | 2171.84
Net Site Energy | 9080.01 | 2171.84 | 2171.84
Total Source Energy | 22829.8 | 5460.64 | 5460.64
Net Source Energy | 22829.8 | 5460.64 | 5460.64
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2411.84 | 0 | 0 | 0 | 0
Cooling | 18.42 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.18 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 616.22 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 21.5 | 0 | 0 | 0 | 87.12
Refrigeration | 3437.39 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6447.54 | 2632.47 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 2.377 | 3.691 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.501 | 0.553 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 4.092 | 0.392 | 0.253 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 9966.41 | 7959.72 | 2006.68 | 0.8 | 3.19
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56829.63 | 43466.13 | 13363.49 | 0.76 | 2.75
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 38466.37 | 28515.22 | 9951.15 | 0.74 | 3.07
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 188142.31 | 138654.06 | 49488.25 | 0.74 | 3
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 56235.88 | 44913.08 | 11322.8 | 0.8 | 2.8
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 34502.77 | 27555.82 | 6946.95 | 0.8 | 3.19
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 15113.95 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 83504.69 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 87290.69 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 292474.83 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 101056.26 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 55873.46 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.6 | 698.35 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.12 | 3409.28 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.96 | 2144.88 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.59 | 1017.59 | 9.46 | 16272.09 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.57 | 622 | 3.4 | 3715.28 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.08 | 2279.46 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.78 | 1.67 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 66002.1854 | 57.5833 | 418.6796 | 0 | 0.0002 | 2525590 | 24120.8423
February | 55031.4113 | 47.7972 | 387.5045 | 0 | 0.0002 | 2337720 | 20228.7248
March | 61348.3809 | 53.3177 | 425.9116 | 0 | 0.0002 | 2569400 | 22532.2174
April | 56957.0861 | 49.3825 | 416.6616 | 0 | 0.0002 | 2513690 | 20984.1613
May | 57188.4748 | 49.4327 | 445.2786 | 0 | 0.0002 | 2686450 | 21151.5547
June | 54545.8093 | 47.0616 | 440.2363 | 0 | 0.0002 | 2656090 | 20221.54
July | 55107.7015 | 47.4622 | 459.8264 | 0 | 0.0002 | 2774340 | 20475.7802
August | 56129.9913 | 48.3357 | 469.6164 | 0 | 0.0002 | 2833410 | 20859.4656
September | 54019.0509 | 46.5061 | 454.0647 | 0 | 0.0002 | 2739590 | 20081.4179
October | 56558.8915 | 48.8207 | 452.5052 | 0 | 0.0002 | 2730100 | 20955.7029
November | 57810.1459 | 50.1335 | 420.8698 | 0 | 0.0002 | 2539070 | 21292.2459
December | 65260.9394 | 56.8968 | 421.0986 | 0 | 0.0002 | 2540220 | 23871.6762
Annual Sum or Average | 695960.0683 | 602.7299 | 5212.2533 | 0 | 0.0026 | 31445700 | 256775.3291
Minimum of Months | 54019.0509 | 46.5061 | 387.5045 | 0 | 0.0002 | 2337720 | 20081.4179
Maximum of Months | 66002.1854 | 57.5833 | 469.6164 | 0 | 0.0002 | 2833410 | 24120.8423
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 517841000000 | 350877.414 | 05-JAN-11:15 | 101872.638 | 41401.92 | 28650.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178952.598 | 0 | 0
February | 479321000000 | 350333.737 | 15-FEB-18:15 | 67915.092 | 36859.929 | 28650.258 | 0 | 138.278 | 4916 | 0 | 0 | 0 | 0 | 0 | 0 | 211854.18 | 0 | 0
March | 526823000000 | 349042.726 | 30-MAR-10:15 | 101872.638 | 41401.92 | 28650.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177117.91 | 0 | 0
April | 515401000000 | 360143.42 | 29-APR-10:45 | 101872.638 | 41401.92 | 28650.258 | 0 | 3836.186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 184382.418 | 0 | 0
May | 550823000000 | 362898.804 | 17-MAY-10:45 | 101872.638 | 41401.92 | 28650.258 | 0 | 2993.937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187980.051 | 0 | 0
June | 544598000000 | 380911.948 | 16-JUN-10:45 | 101872.638 | 41401.92 | 28650.258 | 0 | 13979.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195007.414 | 0 | 0
July | 568844000000 | 402247.039 | 03-JUL-10:45 | 101872.638 | 41401.92 | 28650.258 | 0 | 25765.703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204556.52 | 0 | 0
August | 580956000000 | 389107.13 | 15-AUG-10:45 | 101872.638 | 41401.92 | 28650.258 | 0 | 13323.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203858.56 | 0 | 0
September | 561719000000 | 404606.14 | 29-SEP-10:00 | 101872.638 | 41401.92 | 28650.258 | 0 | 34274.931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198406.394 | 0 | 0
October | 559772000000 | 359498.45 | 21-OCT-10:15 | 101872.638 | 41401.92 | 28650.258 | 0 | 37.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187536.311 | 0 | 0
November | 520604000000 | 354270.08 | 24-NOV-11:15 | 101872.638 | 41401.92 | 28650.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 182345.264 | 0 | 0
December | 520840000000 | 348364.325 | 04-DEC-11:15 | 101872.638 | 41401.92 | 28650.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176439.509 | 0 | 0
Annual Sum or Average | 6447540000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 479321000000 | 348364.325 |  | 67915.092 | 36859.929 | 28650.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176439.509 | 0 | 0
Maximum of Months | 580956000000 | 404606.14 |  | 101872.638 | 41401.92 | 28650.258 | 0 | 34274.931 | 4916 | 0 | 0 | 0 | 0 | 0 | 0 | 211854.18 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 258677.72 | 22387.79 | 0 | 281065.51
Cost per Total Building Area ($/m2) | 61.87 | 5.35 | 0 | 67.23
Cost per Net Conditioned Building Area ($/m2) | 61.87 | 5.35 | 0 | 67.23

## Baltimore (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 10482.71 | 2507.35 | 2507.35
Net Site Energy | 10482.71 | 2507.35 | 2507.35
Total Source Energy | 29180.25 | 6979.59 | 6979.59
Net Source Energy | 29180.25 | 6979.59 | 6979.59
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3122.91 | 0 | 0 | 0 | 0
Cooling | 284.6 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.26 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1002.31 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 21.74 | 0 | 0 | 0 | 87.12
Refrigeration | 3476.44 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7138.94 | 3343.78 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.681 | 0.759 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.33 | 0.352 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 3.354 | 0.355 | 0.274 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.35 | 0.355 | 0.274
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.35 | 0.355 | 0.274
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19285.18 | 13203.21 | 6081.97 | 0.68 | 3
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 107164.33 | 72452 | 34712.32 | 0.68 | 2.9
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 54583.65 | 36903.09 | 17680.56 | 0.68 | 2.62
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 307156.66 | 207663.47 | 99493.2 | 0.68 | 2.74
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 109526.63 | 74049.12 | 35477.51 | 0.68 | 2.9
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 38606.12 | 29761.32 | 8844.8 | 0.77 | 3.13
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 20577.25 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 118398.9 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 134907.43 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 423344.44 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 143452.19 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 62226.49 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.8 | 932.21 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.32 | 8231.53 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.2 | 2403.88 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 12.37 | 20957.04 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.41 | 8412.99 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.16 | 2357.98 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.78 | 1.67 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 126448.326 | 211.3506 | 533.7682 | 0 | 0.0022 | 33185.7016 | 52594.3906
February | 110590.0215 | 187.595 | 482.0143 | 0 | 0.002 | 29969.1818 | 46249.8616
March | 112803.6235 | 202.3028 | 552.1392 | 0 | 0.0023 | 34333.6325 | 48177.1071
April | 102373.8727 | 190.2883 | 538.0294 | 0 | 0.0022 | 33458.6588 | 44334.4189
May | 107750.8216 | 209.7623 | 618.6298 | 0 | 0.0025 | 38474.1833 | 47529.7596
June | 116796.0371 | 231.906 | 695.6022 | 0 | 0.0028 | 43262.6883 | 51934.3569
July | 125396.2682 | 249.5191 | 749.7862 | 0 | 0.003 | 46632.8008 | 55807.6009
August | 126541.8543 | 251.7279 | 756.2459 | 0 | 0.003 | 47034.5367 | 56310.9824
September | 109301.3007 | 216.0498 | 645.5825 | 0 | 0.0026 | 40151.4481 | 48512.6119
October | 107284.703 | 204.357 | 591.1188 | 0 | 0.0024 | 36761.8162 | 46912.885
November | 108186.4822 | 196.7122 | 544.3914 | 0 | 0.0022 | 33852.8237 | 46451.1242
December | 120792.8761 | 205.9865 | 532.4709 | 0 | 0.0022 | 33106.7558 | 50615.939
Annual Sum or Average | 1374270 | 2557.5575 | 7239.7787 | 0 | 0.0295 | 450224.2277 | 595431.0381
Minimum of Months | 102373.8727 | 187.595 | 482.0143 | 0 | 0.002 | 29969.1818 | 44334.4189
Maximum of Months | 126541.8543 | 251.7279 | 756.2459 | 0 | 0.003 | 47034.5367 | 56310.9824
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 526206000000 | 367162.066 | 09-JAN-11:15 | 101872.638 | 41401.92 | 43426.55 | 0 | 2465.393 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177995.565 | 0 | 0
February | 475203000000 | 356513.34 | 13-FEB-11:15 | 101872.638 | 41401.92 | 43426.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169812.232 | 0 | 0
March | 544408000000 | 387711.491 | 09-MAR-18:15 | 67915.092 | 36859.929 | 43426.55 | 0 | 10344.86 | 4916 | 0 | 0 | 0 | 0 | 0 | 0 | 224249.06 | 0 | 0
April | 530534000000 | 387333.409 | 04-APR-17:15 | 67915.092 | 36859.929 | 43426.55 | 0 | 15172.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223959.068 | 0 | 0
May | 610062000000 | 423162.035 | 15-MAY-17:15 | 67915.092 | 36859.929 | 43426.55 | 0 | 36719.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238241.462 | 0 | 0
June | 685991000000 | 513965.373 | 30-JUN-17:15 | 67915.092 | 36859.929 | 43426.55 | 0 | 119211.414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246552.388 | 0 | 0
July | 739429000000 | 543946.267 | 25-JUL-10:00 | 101872.638 | 41401.92 | 43426.55 | 0 | 132848.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224396.959 | 0 | 0
August | 745799000000 | 516407.207 | 17-AUG-17:15 | 67915.092 | 36859.929 | 43426.55 | 0 | 121953.527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246252.109 | 0 | 0
September | 636658000000 | 450150.034 | 09-SEP-10:45 | 101872.638 | 41401.92 | 43426.55 | 0 | 51506.934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211941.991 | 0 | 0
October | 582910000000 | 419263.187 | 03-OCT-10:45 | 101872.638 | 41401.92 | 43426.55 | 0 | 27442.856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205119.223 | 0 | 0
November | 536784000000 | 403359.885 | 04-NOV-10:45 | 101872.638 | 41401.92 | 43426.55 | 0 | 17098.747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199560.03 | 0 | 0
December | 524954000000 | 367345.88 | 23-DEC-11:15 | 101872.638 | 41401.92 | 43426.55 | 0 | 1480.639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 179164.133 | 0 | 0
Annual Sum or Average | 7138940000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 475203000000 | 356513.34 |  | 67915.092 | 36859.929 | 43426.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169812.232 | 0 | 0
Maximum of Months | 745799000000 | 543946.267 |  | 101872.638 | 41401.92 | 43426.55 | 0 | 132848.2 | 4916 | 0 | 0 | 0 | 0 | 0 | 0 | 246552.388 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 139399.16 | 32489.61 | 0 | 171888.76
Cost per Total Building Area ($/m2) | 33.34 | 7.77 | 0 | 41.11
Cost per Net Conditioned Building Area ($/m2) | 33.34 | 7.77 | 0 | 41.11

## Albuquerque (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 9502.28 | 2272.84 | 2272.84
Net Site Energy | 9502.28 | 2272.84 | 2272.84
Total Source Energy | 25627.98 | 6129.93 | 6129.93
Net Source Energy | 25627.98 | 6129.93 | 6129.93
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 2430.18 | 0 | 0 | 0 | 0
Cooling | 177.33 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.25 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1113.75 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 21.45 | 0 | 0 | 0 | 87.12
Refrigeration | 3184.86 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6851.52 | 2650.76 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 1.079 | 1.287 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.335 | 0.358 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 4.092 | 0.362 | 0.225 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 4.09 | 0.362 | 0.225
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 4.09 | 0.362 | 0.225
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 14837.87 | 11850.34 | 2987.53 | 0.8 | 3.17
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 81168.13 | 63218.46 | 17949.67 | 0.78 | 3.26
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39565.95 | 31599.56 | 7966.4 | 0.8 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 235440.93 | 188036.14 | 47404.79 | 0.8 | 3.07
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 78579.93 | 62758.27 | 15821.65 | 0.8 | 3.35
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 39328.5 | 31409.92 | 7918.59 | 0.8 | 3.19
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 18581.77 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 103231.51 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 116559.06 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 373184.75 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 122996.72 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 55078.89 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.55 | 622 | 0.9 | 1021.12 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.64 | 8849.21 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.39 | 2613.96 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 14.22 | 24097.9 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 4.75 | 9054.6 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.38 | 2598.28 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.78 | 1.67 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 167128.5234 | 270.8179 | 645.4189 | 0 | 0.0026 | 670994.5057 | 69527.262
February | 146954.9091 | 241.1553 | 583.8962 | 0 | 0.0023 | 607056.6469 | 61431.7453
March | 159578.575 | 265.2707 | 652.455 | 0 | 0.0026 | 678359.6149 | 67042.311
April | 147733.4078 | 250.9889 | 633.2993 | 0 | 0.0025 | 658481.7281 | 62596.4436
May | 156964.3289 | 271.7459 | 700.3348 | 0 | 0.0027 | 728217.1265 | 67005.4319
June | 165561.8819 | 288.9756 | 751.3877 | 0 | 0.0029 | 781317.8856 | 70905.6122
July | 183200.5735 | 320.4894 | 835.3735 | 0 | 0.0033 | 868653.7248 | 78531.0777
August | 182341.4428 | 318.814 | 830.5225 | 0 | 0.0032 | 863608.3628 | 78145.8842
September | 163052.7543 | 284.3403 | 738.6157 | 0 | 0.0029 | 768035.4776 | 69805.9294
October | 155306.4939 | 265.0781 | 672.3831 | 0 | 0.0026 | 699127.9308 | 65925.2198
November | 154038.8769 | 254.7786 | 622.8593 | 0 | 0.0025 | 647579.7484 | 64589.0862
December | 167785.0506 | 271.3472 | 645.0609 | 0 | 0.0026 | 670618.3459 | 69747.949
Annual Sum or Average | 1949650 | 3303.8019 | 8311.6069 | 0 | 0.0326 | 8642050 | 825253.9522
Minimum of Months | 146954.9091 | 241.1553 | 583.8962 | 0 | 0.0023 | 607056.6469 | 61431.7453
Maximum of Months | 183200.5735 | 320.4894 | 835.3735 | 0 | 0.0033 | 868653.7248 | 78531.0777
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 531973000000 | 352154.248 | 02-JAN-11:15 | 101872.638 | 41401.92 | 48365.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160513.699 | 0 | 0
February | 481282000000 | 353753.508 | 17-FEB-11:15 | 101872.638 | 41401.92 | 48365.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162112.96 | 0 | 0
March | 537812000000 | 357465.645 | 08-MAR-11:15 | 101872.638 | 41401.92 | 48365.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165825.096 | 0 | 0
April | 522052000000 | 373079.064 | 21-APR-17:15 | 67915.092 | 36859.929 | 48365.99 | 0 | 19314.777 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200623.275 | 0 | 0
May | 577339000000 | 403272.784 | 30-MAY-10:45 | 101872.638 | 41401.92 | 48365.99 | 0 | 19565.068 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192067.168 | 0 | 0
June | 619438000000 | 429716.225 | 29-JUN-10:45 | 101872.638 | 41401.92 | 48365.99 | 0 | 38127.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199947.878 | 0 | 0
July | 688679000000 | 441215.532 | 18-JUL-17:15 | 67915.092 | 36859.929 | 48365.99 | 0 | 63893.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224181.11 | 0 | 0
August | 684679000000 | 455511.517 | 01-AUG-10:45 | 101872.638 | 41401.92 | 48365.99 | 0 | 52202.827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 211668.142 | 0 | 0
September | 608908000000 | 408500.645 | 02-SEP-10:45 | 101872.638 | 41401.92 | 48365.99 | 0 | 21555.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195304.416 | 0 | 0
October | 554277000000 | 389589.999 | 03-OCT-10:45 | 101872.638 | 41401.92 | 48365.99 | 0 | 12841.194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185108.257 | 0 | 0
November | 513409000000 | 359828.16 | 10-NOV-11:15 | 101872.638 | 41401.92 | 48365.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168187.612 | 0 | 0
December | 531674000000 | 351013.388 | 22-DEC-11:15 | 101872.638 | 41401.92 | 48365.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159372.84 | 0 | 0
Annual Sum or Average | 6851520000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 481282000000 | 351013.388 |  | 67915.092 | 36859.929 | 48365.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159372.84 | 0 | 0
Maximum of Months | 688679000000 | 455511.517 |  | 101872.638 | 41401.92 | 48365.99 | 0 | 63893.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224181.11 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 70473.52 | 18373.67 | 0 | 88847.19
Cost per Total Building Area ($/m2) | 16.86 | 4.39 | 0 | 21.25
Cost per Net Conditioned Building Area ($/m2) | 16.86 | 4.39 | 0 | 21.25

## Seattle (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 9946.32 | 2379.05 | 2379.05
Net Site Energy | 9946.32 | 2379.05 | 2379.05
Total Source Energy | 15098.45 | 3611.38 | 3611.38
Net Source Energy | 15098.45 | 3611.38 | 3611.38
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3206.08 | 0 | 0 | 0 | 0
Cooling | 26.59 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.13 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 853.18 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 22.54 | 0 | 0 | 0 | 87.12
Refrigeration | 3263.35 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6518.57 | 3427.75 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.364 | 0.391 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 4.092 | 0.392 | 0.253 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 4.09 | 0.392 | 0.253
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 4.09 | 0.392 | 0.253
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 11204.64 | 8816.32 | 2388.33 | 0.79 | 3.16
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 66503.61 | 50187.44 | 16316.17 | 0.75 | 3.17
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30533.92 | 24386.07 | 6147.84 | 0.8 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 255701.22 | 178869.25 | 76831.97 | 0.7 | 2.79
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 60608.75 | 48405.49 | 12203.25 | 0.8 | 3.35
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 30946.64 | 24715.69 | 6230.94 | 0.8 | 3.19
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 16577.38 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 95691.62 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 97904.73 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 361840.33 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 117222.53 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 52596.15 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.54 | 622 | 0.66 | 759.89 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.54 | 6746.02 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.84 | 2017.25 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 11.28 | 19114.94 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.58 | 1109.65 | 3.66 | 6983.82 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 1.87 | 2044.52 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.78 | 1.67 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 52454.5475 | 65.1631 | 112.2679 | 0 | 0.0005 | 1482150 | 20034.1187
February | 43216.6578 | 55.0518 | 101.2095 | 0 | 0.0004 | 1336430 | 16652.0248
March | 46753.1296 | 60.2782 | 114.0981 | 0 | 0.0005 | 1506760 | 18091.952
April | 40816.4803 | 54.3913 | 110.8928 | 0 | 0.0005 | 1464740 | 15983.9189
May | 37038.4225 | 52.36 | 119.8036 | 0 | 0.0005 | 1582920 | 14826.0662
June | 33518.2138 | 49.1194 | 119.5 | 0 | 0.0005 | 1579140 | 13602.8714
July | 32931.1073 | 49.8449 | 127.5324 | 0 | 0.0005 | 1685480 | 13534.4532
August | 32869.8766 | 50.4374 | 131.6704 | 0 | 0.0005 | 1740250 | 13582.6774
September | 34303.8884 | 50.1309 | 121.4083 | 0 | 0.0005 | 1604340 | 13906.7499
October | 39910.4191 | 54.7943 | 118.7135 | 0 | 0.0005 | 1568300 | 15801.5813
November | 45923.5744 | 58.9383 | 110.3474 | 0 | 0.0005 | 1457180 | 17741.9835
December | 52131.7574 | 64.9869 | 113.0119 | 0 | 0.0005 | 1492010 | 19934.9035
Annual Sum or Average | 491868.0747 | 665.4964 | 1400.4559 | 0 | 0.0058 | 18499700 | 193693.3006
Minimum of Months | 32869.8766 | 49.1194 | 101.2095 | 0 | 0.0004 | 1336430 | 13534.4532
Maximum of Months | 52454.5475 | 65.1631 | 131.6704 | 0 | 0.0005 | 1740250 | 20034.1187
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 522251000000 | 357071.481 | 14-JAN-11:15 | 101872.638 | 41401.92 | 37797.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175999.562 | 0 | 0
February | 470906000000 | 347951.211 | 21-FEB-11:15 | 101872.638 | 41401.92 | 37797.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166879.293 | 0 | 0
March | 530922000000 | 357643.67 | 30-MAR-10:15 | 101872.638 | 41401.92 | 37797.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176571.751 | 0 | 0
April | 516117000000 | 362846.873 | 29-APR-10:15 | 101872.638 | 41401.92 | 37797.36 | 0 | 48.449 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181726.505 | 0 | 0
May | 557759000000 | 374988.321 | 05-MAY-17:15 | 67915.092 | 36859.929 | 37797.36 | 0 | 9485.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 222930.902 | 0 | 0
June | 556428000000 | 388387.461 | 28-JUN-10:45 | 101872.638 | 41401.92 | 37797.36 | 0 | 12996.483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194319.06 | 0 | 0
July | 593898000000 | 404944.643 | 31-JUL-17:15 | 67915.092 | 36859.929 | 37797.36 | 0 | 33729.56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228642.702 | 0 | 0
August | 613195000000 | 399684.725 | 18-AUG-17:15 | 67915.092 | 36859.929 | 37797.36 | 0 | 29177.388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227934.956 | 0 | 0
September | 565308000000 | 419744.042 | 02-SEP-14:00 | 101872.638 | 41401.92 | 37797.36 | 0 | 77931.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160740.617 | 0 | 0
October | 552608000000 | 362980.692 | 05-OCT-10:15 | 101872.638 | 41401.92 | 37797.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 181908.773 | 0 | 0
November | 513452000000 | 364192.607 | 03-NOV-10:15 | 101872.638 | 41401.92 | 37797.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183120.689 | 0 | 0
December | 525728000000 | 351207.733 | 05-DEC-11:15 | 101872.638 | 41401.92 | 37797.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170135.815 | 0 | 0
Annual Sum or Average | 6518570000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 470906000000 | 347951.211 |  | 67915.092 | 36859.929 | 37797.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160740.617 | 0 | 0
Maximum of Months | 613195000000 | 419744.042 |  | 101872.638 | 41401.92 | 37797.36 | 0 | 77931.506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228642.702 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 128924.9 | 28712.22 | 0 | 157637.12
Cost per Total Building Area ($/m2) | 30.84 | 6.87 | 0 | 37.71
Cost per Net Conditioned Building Area ($/m2) | 30.84 | 6.87 | 0 | 37.71

## Chicago (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 11303.7 | 2703.72 | 2703.72
Net Site Energy | 11303.7 | 2703.72 | 2703.72
Total Source Energy | 29846.49 | 7138.95 | 7138.95
Net Source Energy | 29846.49 | 7138.95 | 7138.95
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3949.12 | 0 | 0 | 0 | 0
Cooling | 193.07 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.15 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1235.39 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 23.08 | 0 | 0 | 0 | 87.12
Refrigeration | 3328.43 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7132.38 | 4171.33 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.568 | 0.621 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.296 | 0.314 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 3.354 | 0.385 | 0.305 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24909.23 | 16931.24 | 7977.99 | 0.68 | 2.98
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 134275.95 | 90781.72 | 43494.23 | 0.68 | 2.89
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 54867.95 | 37095.3 | 17772.65 | 0.68 | 2.62
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 377275.14 | 255069.39 | 122205.75 | 0.68 | 2.74
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 136351.77 | 92185.15 | 44166.63 | 0.68 | 2.89
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 38025.2 | 29594.01 | 8431.18 | 0.78 | 3.15
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 25522.71 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 146818.11 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 158420.58 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 518407.72 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 177981.64 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 64747.98 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.02 | 1159.67 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.41 | 10144.03 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.21 | 2416.4 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 15.19 | 25741.16 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.49 | 10300.85 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.17 | 2372.91 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.78 | 1.67 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 230665.045 | 378.909 | 1017.2647 | 0 | 0.0032 | 234132.5402 | 96042.7272
February | 202976.4539 | 337.5304 | 919.7623 | 0 | 0.0028 | 211698.1079 | 84906.4194
March | 218201.7971 | 369.9881 | 1031.5528 | 0 | 0.0032 | 237439.6908 | 91957.8858
April | 200568.1859 | 350.277 | 1009.2693 | 0 | 0.0031 | 232325.8512 | 85500.6307
May | 212994.267 | 381.704 | 1130.1015 | 0 | 0.0034 | 260154.1967 | 91727.6596
June | 229642.6816 | 416.3763 | 1247.4304 | 0 | 0.0038 | 287170.2985 | 99359.8919
July | 251531.8629 | 456.9267 | 1371.501 | 0 | 0.0041 | 315733.6416 | 108913.1374
August | 246188.1157 | 447.0505 | 1341.3516 | 0 | 0.004 | 308792.7205 | 106583.1559
September | 218221.7515 | 394.6134 | 1179.0663 | 0 | 0.0036 | 271430.8425 | 94317.4989
October | 209300.0866 | 370.2103 | 1081.2862 | 0 | 0.0033 | 248910.1973 | 89670.7832
November | 207697.9525 | 356.0078 | 1004.8574 | 0 | 0.0031 | 231300.7825 | 87897.4164
December | 226470.7225 | 375.4745 | 1019.4816 | 0 | 0.0032 | 234648.3359 | 94626.7002
Annual Sum or Average | 2654460 | 4635.0679 | 13352.925 | 0 | 0.0407 | 3073740 | 1131500
Minimum of Months | 200568.1859 | 337.5304 | 919.7623 | 0 | 0.0028 | 211698.1079 | 84906.4194
Maximum of Months | 251531.8629 | 456.9267 | 1371.501 | 0 | 0.0041 | 315733.6416 | 108913.1374
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 543287000000 | 357606.261 | 18-JAN-11:15 | 101872.638 | 41401.92 | 52265.928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162065.776 | 0 | 0
February | 491230000000 | 359444.292 | 28-FEB-11:15 | 101872.638 | 41401.92 | 52265.928 | 0 | 504.593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163399.214 | 0 | 0
March | 550961000000 | 372512.135 | 14-MAR-17:15 | 67915.092 | 36859.929 | 52265.928 | 0 | 2592.262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212878.924 | 0 | 0
April | 539095000000 | 386827.92 | 10-APR-10:15 | 101872.638 | 41401.92 | 52265.928 | 0 | 2874.059 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188413.375 | 0 | 0
May | 603668000000 | 435847.354 | 30-MAY-17:15 | 67915.092 | 36859.929 | 52265.928 | 0 | 40644.685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238161.721 | 0 | 0
June | 666357000000 | 504555.503 | 08-JUN-12:00 | 101872.638 | 41401.92 | 52265.928 | 0 | 117463.851 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191551.166 | 0 | 0
July | 732636000000 | 535013.077 | 14-JUL-10:00 | 101872.638 | 41401.92 | 52265.928 | 0 | 118672.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220799.861 | 0 | 0
August | 716530000000 | 509679.733 | 04-AUG-17:15 | 67915.092 | 36859.929 | 52265.928 | 0 | 107857.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244781.022 | 0 | 0
September | 629835000000 | 464877.971 | 06-SEP-10:45 | 101872.638 | 41401.92 | 52265.928 | 0 | 56406.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212930.595 | 0 | 0
October | 577577000000 | 403581.953 | 31-OCT-10:45 | 101872.638 | 41401.92 | 52265.928 | 0 | 12267.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 195774.456 | 0 | 0
November | 536716000000 | 402837.113 | 02-NOV-10:45 | 101872.638 | 41401.92 | 52265.928 | 0 | 11151.659 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196144.968 | 0 | 0
December | 544484000000 | 362009.247 | 12-DEC-11:15 | 101872.638 | 41401.92 | 52265.928 | 0 | 507.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165961.464 | 0 | 0
Annual Sum or Average | 7132380000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 491230000000 | 357606.261 |  | 67915.092 | 36859.929 | 52265.928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162065.776 | 0 | 0
Maximum of Months | 732636000000 | 535013.077 |  | 101872.638 | 41401.92 | 52265.928 | 0 | 118672.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244781.022 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 189826.48 | 35006.71 | 0 | 224833.19
Cost per Total Building Area ($/m2) | 45.4 | 8.37 | 0 | 53.78
Cost per Net Conditioned Building Area ($/m2) | 45.4 | 8.37 | 0 | 53.78

## Boulder (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 10239.27 | 2449.12 | 2449.12
Net Site Energy | 10239.27 | 2449.12 | 2449.12
Total Source Energy | 26455.4 | 6327.84 | 6327.84
Net Source Energy | 26455.4 | 6327.84 | 6327.84
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 3155.43 | 0 | 0 | 0 | 0
Cooling | 105.55 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.17 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1322.44 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 23.02 | 0 | 0 | 0 | 87.12
Refrigeration | 3058.21 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6861.69 | 3377.57 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.795 | 0.902 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.285 | 0.302 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 3.354 | 0.385 | 0.305 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 3.35 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 3.35 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 18016.91 | 14389.3 | 3627.61 | 0.8 | 3.17
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 110340.26 | 81997.27 | 28342.98 | 0.74 | 3.11
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 38303.52 | 30591.31 | 7712.21 | 0.8 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 277757.04 | 221832.12 | 55924.92 | 0.8 | 3.07
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 94993.68 | 75867.2 | 19126.48 | 0.8 | 3.32
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 38997.03 | 31145.18 | 7851.85 | 0.8 | 3.19
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 22679.84 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 127193.91 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 134698.52 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 454065.12 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 152086.09 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 57295.18 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.09 | 1239.9 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.66 | 10616.21 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.31 | 2530.56 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 16.78 | 28245.63 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.74 | 10765.5 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.36 | 2576.38 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.78 | 1.67 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 176420.6523 | 283.1692 | 666.658 | 0 | 0.0027 | 693054.9369 | 73127.4739
February | 156018.2765 | 252.6811 | 601.7902 | 0 | 0.0024 | 625636.002 | 64892.1776
March | 168548.8836 | 277.3605 | 673.8589 | 0 | 0.0027 | 700593.3499 | 70534.1522
April | 154894.6344 | 260.5745 | 650.0289 | 0 | 0.0026 | 675859.1041 | 65377.587
May | 160987.8275 | 275.4629 | 700.7028 | 0 | 0.0027 | 728578.7106 | 68404.3294
June | 162183.2316 | 281.5441 | 727.7493 | 0 | 0.0028 | 756728.0723 | 69308.1247
July | 179626.0675 | 314.0039 | 817.8166 | 0 | 0.0032 | 850395.8676 | 76976.0326
August | 177049.6614 | 309.1183 | 804.0202 | 0 | 0.0031 | 836047.4591 | 75834.5058
September | 156573.7884 | 270.5333 | 695.6885 | 0 | 0.0027 | 723382.3358 | 66786.0913
October | 158890.5963 | 269.1346 | 676.7458 | 0 | 0.0027 | 703650.3173 | 67244.4691
November | 162177.2695 | 266.2409 | 644.9503 | 0 | 0.0026 | 670533.2171 | 67805.5165
December | 176831.9583 | 283.0747 | 664.1277 | 0 | 0.0027 | 690418.6823 | 73223.9401
Annual Sum or Average | 1990200 | 3342.898 | 8324.1371 | 0 | 0.0328 | 8654880 | 839514.4001
Minimum of Months | 154894.6344 | 252.6811 | 601.7902 | 0 | 0.0024 | 625636.002 | 64892.1776
Maximum of Months | 179626.0675 | 314.0039 | 817.8166 | 0 | 0.0032 | 850395.8676 | 76976.0326
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 549462000000 | 362737.635 | 23-JAN-11:15 | 101872.638 | 41401.92 | 56105.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163357.986 | 0 | 0
February | 496012000000 | 358721.314 | 11-FEB-11:15 | 101872.638 | 41401.92 | 56105.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159341.665 | 0 | 0
March | 555439000000 | 366363.925 | 27-MAR-10:45 | 101872.638 | 41401.92 | 56105.091 | 0 | 834.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166150.26 | 0 | 0
April | 535829000000 | 382342.56 | 26-APR-10:45 | 101872.638 | 41401.92 | 56105.091 | 0 | 6781.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176181.011 | 0 | 0
May | 577626000000 | 406097.26 | 24-MAY-10:45 | 101872.638 | 41401.92 | 56105.091 | 0 | 15162.39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191555.22 | 0 | 0
June | 599943000000 | 432945.518 | 28-JUN-10:45 | 101872.638 | 41401.92 | 56105.091 | 0 | 35544.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 198021.694 | 0 | 0
July | 674204000000 | 457799.132 | 19-JUL-10:45 | 101872.638 | 41401.92 | 56105.091 | 0 | 50717.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207702.439 | 0 | 0
August | 662828000000 | 458412.541 | 30-AUG-10:45 | 101872.638 | 41401.92 | 56105.091 | 0 | 51904.641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207128.251 | 0 | 0
September | 573506000000 | 417617.886 | 09-SEP-10:45 | 101872.638 | 41401.92 | 56105.091 | 0 | 22037.512 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 196200.725 | 0 | 0
October | 557862000000 | 385601.825 | 05-OCT-10:45 | 101872.638 | 41401.92 | 56105.091 | 0 | 10292.523 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175929.652 | 0 | 0
November | 531607000000 | 361848.354 | 16-NOV-11:15 | 101872.638 | 41401.92 | 56105.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162468.705 | 0 | 0
December | 547372000000 | 356883.397 | 30-DEC-11:15 | 101872.638 | 41401.92 | 56105.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157503.748 | 0 | 0
Annual Sum or Average | 6861690000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 496012000000 | 356883.397 |  | 101872.638 | 41401.92 | 56105.091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157503.748 | 0 | 0
Maximum of Months | 674204000000 | 458412.541 |  | 101872.638 | 41401.92 | 56105.091 | 0 | 51904.641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207702.439 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 70577.84 | 23508.39 | 0 | 94086.23
Cost per Total Building Area ($/m2) | 16.88 | 5.62 | 0 | 22.5
Cost per Net Conditioned Building Area ($/m2) | 16.88 | 5.62 | 0 | 22.5

## Minneapolis (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 12227.57 | 2924.7 | 2924.7
Net Site Energy | 12227.57 | 2924.7 | 2924.7
Total Source Energy | 30126.49 | 7205.93 | 7205.93
Net Source Energy | 30126.49 | 7205.93 | 7205.93
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4851.12 | 0 | 0 | 0 | 0
Cooling | 165.3 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.21 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1353.94 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 24.24 | 0 | 0 | 0 | 87.12
Refrigeration | 3258.3 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7153.09 | 5074.48 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.403 | 0.429 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.252 | 0.265 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 2.956 | 0.385 | 0.305 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 26916.15 | 18302.89 | 8613.26 | 0.68 | 2.98
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 147418.99 | 99667.5 | 47751.48 | 0.68 | 2.89
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 55581.39 | 37577.65 | 18003.75 | 0.68 | 2.62
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 412986.07 | 279212.95 | 133773.12 | 0.68 | 2.73
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 149538.57 | 101100.52 | 48438.05 | 0.68 | 2.89
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 38143.52 | 29827.45 | 8316.06 | 0.78 | 3.15
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 27513.06 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 159738.99 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 173432.23 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 569308.42 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 195498.01 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 66917.68 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.1 | 1254.5 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 5.94 | 11136.93 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.24 | 2447.82 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 16.63 | 27995.9 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.02 | 11297.06 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.2 | 2405.69 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.78 | 1.67 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 180894.4838 | 275.3572 | 362.7835 | 0 | 0.0028 | 238272.1448 | 73233.1456
February | 154771.7408 | 240.8353 | 327.4634 | 0 | 0.0025 | 215103.1632 | 63158.7128
March | 154700.0036 | 253.3206 | 368.3292 | 0 | 0.0028 | 242012.6395 | 64333.5358
April | 136122.3093 | 234.0862 | 360.5222 | 0 | 0.0027 | 236934.7906 | 57677.0971
May | 142467.2654 | 254.2961 | 407.6047 | 0 | 0.003 | 267916.1253 | 61254.3768
June | 148352.6905 | 268.9697 | 438.0164 | 0 | 0.0032 | 287921.6169 | 64183.2904
July | 157987.0006 | 286.9966 | 468.2837 | 0 | 0.0034 | 307819.3321 | 68404.9534
August | 158715.9871 | 288.337 | 470.4971 | 0 | 0.0034 | 309274.3258 | 68722.1335
September | 138178.3433 | 248.0224 | 399.8333 | 0 | 0.0029 | 262813.3257 | 59542.4182
October | 139966.8117 | 240.9754 | 371.6093 | 0 | 0.0027 | 244222.3941 | 59332.6351
November | 148129.7786 | 242.8262 | 353.5466 | 0 | 0.0026 | 232300.8365 | 61626.5044
December | 172050.5471 | 267.2345 | 362.4332 | 0 | 0.0027 | 238071.4839 | 70163.1597
Annual Sum or Average | 1832340 | 3101.2573 | 4690.9227 | 0 | 0.0347 | 3082660 | 771631.9628
Minimum of Months | 136122.3093 | 234.0862 | 327.4634 | 0 | 0.0025 | 215103.1632 | 57677.0971
Maximum of Months | 180894.4838 | 288.337 | 470.4971 | 0 | 0.0034 | 309274.3258 | 73233.1456
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 552893000000 | 358461.392 | 30-JAN-11:15 | 101872.638 | 41401.92 | 56668.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158518.013 | 0 | 0
February | 499131000000 | 358138.611 | 21-FEB-11:15 | 101872.638 | 41401.92 | 56668.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158195.231 | 0 | 0
March | 561572000000 | 368589.798 | 29-MAR-10:15 | 101872.638 | 41401.92 | 56668.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168646.419 | 0 | 0
April | 549789000000 | 380482.691 | 01-APR-17:15 | 56595.91 | 32317.938 | 56668.821 | 0 | 8343.888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 226556.134 | 0 | 0
May | 621679000000 | 485669.844 | 27-MAY-14:00 | 101872.638 | 41401.92 | 56668.821 | 0 | 109444.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176282.269 | 0 | 0
June | 668100000000 | 500511.596 | 29-JUN-17:15 | 67915.092 | 36859.929 | 56668.821 | 0 | 96050.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243016.792 | 0 | 0
July | 714272000000 | 505300.856 | 13-JUL-17:15 | 67915.092 | 36859.929 | 56668.821 | 0 | 99142.468 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244714.546 | 0 | 0
August | 717648000000 | 500717.715 | 25-AUG-17:15 | 67915.092 | 36859.929 | 56668.821 | 0 | 96064.265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243209.608 | 0 | 0
September | 609839000000 | 425607.064 | 14-SEP-10:45 | 101872.638 | 41401.92 | 56668.821 | 0 | 25720.98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 199942.704 | 0 | 0
October | 566700000000 | 388008.065 | 14-OCT-10:15 | 101872.638 | 41401.92 | 56668.821 | 0 | 2464.101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 185600.584 | 0 | 0
November | 539037000000 | 370373.497 | 03-NOV-10:15 | 101872.638 | 41401.92 | 56668.821 | 0 | 1552.329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168877.789 | 0 | 0
December | 552427000000 | 362042.837 | 02-DEC-11:15 | 101872.638 | 41401.92 | 56668.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162099.457 | 0 | 0
Annual Sum or Average | 7153090000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 499131000000 | 358138.611 |  | 56595.91 | 32317.938 | 56668.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158195.231 | 0 | 0
Maximum of Months | 717648000000 | 505300.856 |  | 101872.638 | 41401.92 | 56668.821 | 0 | 109444.196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244714.546 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 110252.58 | 39919.27 | 0 | 150171.85
Cost per Total Building Area ($/m2) | 26.37 | 9.55 | 0 | 35.92
Cost per Net Conditioned Building Area ($/m2) | 26.37 | 9.55 | 0 | 35.92

## Helena (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 11322.78 | 2708.28 | 2708.28
Net Site Energy | 11322.78 | 2708.28 | 2708.28
Total Source Energy | 28797.85 | 6888.13 | 6888.13
Net Source Energy | 28797.85 | 6888.13 | 6888.13
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 4206.01 | 0 | 0 | 0 | 0
Cooling | 62.15 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.12 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1497.78 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 24.45 | 0 | 0 | 0 | 87.12
Refrigeration | 2957.81 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6893.19 | 4429.58 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.449 | 0.481 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.274 | 0.289 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 2.956 | 0.385 | 0.305 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 2.96 | 0.385 | 0.305
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 2.96 | 0.385 | 0.305
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 19929.4 | 15916.72 | 4012.68 | 0.8 | 3.22
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 109699.75 | 86267.01 | 23432.74 | 0.79 | 3.27
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 36777.18 | 29372.29 | 7404.89 | 0.8 | 3.19
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 312667.58 | 249713.61 | 62953.97 | 0.8 | 3.07
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 107655.89 | 85979.94 | 21675.95 | 0.8 | 3.32
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 38558.05 | 30794.59 | 7763.46 | 0.8 | 3.19
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 26726.93 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 152865.55 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 156870 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 553483.51 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 185106.88 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 62845.05 | 0.8
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.2 | 1371.52 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.41 | 12017.44 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.22 | 2429.72 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 18.89 | 31795.75 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.5 | 12200.49 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.33 | 2547.37 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.78 | 1.67 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 177782.5318 | 277.1895 | 419.6551 | 0 | 0.003 | 9950220 | 72725.9476
February | 155497.5155 | 246.123 | 380.3571 | 0 | 0.0027 | 9019130 | 63965.4011
March | 158860.4599 | 260.4989 | 421.3233 | 0 | 0.003 | 9992170 | 66223.8789
April | 146035.9218 | 243.7304 | 402.721 | 0 | 0.0028 | 9551710 | 61289.6354
May | 146390.2067 | 250.4207 | 425.755 | 0 | 0.003 | 10099000 | 62027.8765
June | 146453.8856 | 255.3957 | 443.5383 | 0 | 0.0031 | 10521600 | 62525.2295
July | 153913.9613 | 271.1715 | 476.1361 | 0 | 0.0033 | 11295300 | 65977.5566
August | 154756.9991 | 272.1172 | 476.7926 | 0 | 0.0033 | 11310700 | 66286.7768
September | 142833.3171 | 247.6349 | 427.3403 | 0 | 0.003 | 10137100 | 60839.6353
October | 148132.5594 | 249.6696 | 417.3269 | 0 | 0.0029 | 9898520 | 62405.4226
November | 154248.8295 | 251.6418 | 404.4091 | 0 | 0.0029 | 9590810 | 64176.2562
December | 173358.183 | 272.8636 | 418.5143 | 0 | 0.003 | 9923650 | 71164.7208
Annual Sum or Average | 1858260 | 3098.4569 | 5113.8691 | 0 | 0.0359 | 121290000 | 779608.3372
Minimum of Months | 142833.3171 | 243.7304 | 380.3571 | 0 | 0.0027 | 9019130 | 60839.6353
Maximum of Months | 177782.5318 | 277.1895 | 476.7926 | 0 | 0.0033 | 11310700 | 72725.9476
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 565495000000 | 364923.905 | 23-JAN-11:15 | 101872.638 | 41401.92 | 62493.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159156.149 | 0 | 0
February | 512579000000 | 369825.875 | 02-FEB-11:15 | 101872.638 | 41401.92 | 62493.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164058.119 | 0 | 0
March | 567879000000 | 366864.395 | 31-MAR-10:15 | 101872.638 | 41401.92 | 62493.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161096.638 | 0 | 0
April | 542846000000 | 373098.843 | 24-APR-10:15 | 101872.638 | 41401.92 | 62493.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167331.086 | 0 | 0
May | 573950000000 | 385236.292 | 25-MAY-17:15 | 67915.092 | 36859.929 | 62493.199 | 0 | 13235.323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 204732.749 | 0 | 0
June | 597966000000 | 438253.478 | 30-JUN-10:45 | 101872.638 | 41401.92 | 62493.199 | 0 | 29261.885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 203223.836 | 0 | 0
July | 641936000000 | 443115.709 | 21-JUL-17:15 | 67915.092 | 36859.929 | 62493.199 | 0 | 59070.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216776.782 | 0 | 0
August | 642817000000 | 436737.708 | 11-AUG-17:15 | 67915.092 | 36859.929 | 62493.199 | 0 | 46166.127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223303.362 | 0 | 0
September | 576116000000 | 412934.356 | 01-SEP-17:15 | 67915.092 | 36859.929 | 62493.199 | 0 | 30992.161 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214673.976 | 0 | 0
October | 562556000000 | 376701.798 | 06-OCT-17:15 | 67915.092 | 36859.929 | 62493.199 | 0 | 8632.798 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200800.78 | 0 | 0
November | 545069000000 | 366234.708 | 01-NOV-10:15 | 101872.638 | 41401.92 | 62493.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160466.952 | 0 | 0
December | 563985000000 | 363175.947 | 29-DEC-11:15 | 101872.638 | 41401.92 | 62493.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157408.191 | 0 | 0
Annual Sum or Average | 6893190000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 512579000000 | 363175.947 |  | 67915.092 | 36859.929 | 62493.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157408.191 | 0 | 0
Maximum of Months | 642817000000 | 443115.709 |  | 101872.638 | 41401.92 | 62493.199 | 0 | 59070.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 223303.362 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 134492.82 | 36424.92 | 0 | 170917.74
Cost per Total Building Area ($/m2) | 32.17 | 8.71 | 0 | 40.88
Cost per Net Conditioned Building Area ($/m2) | 32.17 | 8.71 | 0 | 40.88

## Duluth (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 13113.72 | 3136.66 | 3136.66
Net Site Energy | 13113.72 | 3136.66 | 3136.66
Total Source Energy | 30607.78 | 7321.04 | 7321.04
Net Source Energy | 30607.78 | 7321.04 | 7321.04
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 5942.77 | 0 | 0 | 0 | 0
Cooling | 57.31 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 77.1 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1490.73 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 26.15 | 0 | 0 | 0 | 87.12
Refrigeration | 3022.2 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 6945.67 | 6168.05 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.346 | 0.365 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.227 | 0.237 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 2.956 | 0.487 | 0.409 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 2.96 | 0.487 | 0.409
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 2.96 | 0.487 | 0.409
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 27508.37 | 18923.89 | 8584.48 | 0.69 | 3
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 155732.81 | 105288.34 | 50444.47 | 0.68 | 2.89
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 38919.61 | 30305.3 | 8614.31 | 0.78 | 3.15
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 453681.83 | 306726.67 | 146955.16 | 0.68 | 2.73
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 157898.51 | 106752.53 | 51145.98 | 0.68 | 2.89
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 37535.55 | 29977.96 | 7557.58 | 0.8 | 3.19
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 28433.43 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 165417.03 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 176333.66 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 599703.26 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 201684.93 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 68100.38 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.16 | 1322.97 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.27 | 11765.01 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.22 | 2431.45 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 18.27 | 30754.62 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 6.36 | 11928.62 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.27 | 2479.82 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.78 | 1.67 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 183213.8893 | 279.3535 | 368.9514 | 0 | 0.0028 | 242325.7286 | 74216.6451
February | 161589.828 | 248.9119 | 333.6416 | 0 | 0.0025 | 219148.2978 | 65698.9076
March | 165800.2617 | 264.468 | 371.87 | 0 | 0.0028 | 244306.5315 | 68277.7921
April | 143628.6849 | 239.6992 | 356.6476 | 0 | 0.0027 | 234358.0484 | 60160.3103
May | 139517.8516 | 241.9229 | 376.0192 | 0 | 0.0028 | 247127.7634 | 59306.7666
June | 137050.7316 | 245.4001 | 394.6224 | 0 | 0.0029 | 259385.9044 | 58999.3342
July | 150244.7136 | 271.8064 | 441.6698 | 0 | 0.0032 | 290320.87 | 64945.1137
August | 148295.848 | 266.7322 | 430.8983 | 0 | 0.0031 | 283234.6589 | 63954.6667
September | 137611.706 | 242.067 | 382.1138 | 0 | 0.0028 | 251147.3464 | 58826.2137
October | 143766.5726 | 244.1741 | 370.8117 | 0 | 0.0027 | 243684.2954 | 60623.8094
November | 155058.872 | 250.8187 | 359.1236 | 0 | 0.0027 | 235949.7489 | 64187.4564
December | 178067.4355 | 274.6631 | 368.866 | 0 | 0.0028 | 242286.9072 | 72433.6373
Annual Sum or Average | 1843850 | 3070.0172 | 4555.2354 | 0 | 0.0339 | 2993280 | 771630.6531
Minimum of Months | 137050.7316 | 239.6992 | 333.6416 | 0 | 0.0025 | 219148.2978 | 58826.2137
Maximum of Months | 183213.8893 | 279.3535 | 441.6698 | 0 | 0.0032 | 290320.87 | 74216.6451
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 562299000000 | 359399.215 | 13-JAN-11:15 | 101872.638 | 41401.92 | 60813.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155311.253 | 0 | 0
February | 508517000000 | 364433.826 | 21-FEB-11:15 | 101872.638 | 41401.92 | 60813.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 160345.864 | 0 | 0
March | 566895000000 | 365762.223 | 30-MAR-10:15 | 101872.638 | 41401.92 | 60813.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161674.261 | 0 | 0
April | 543810000000 | 372495.182 | 14-APR-10:15 | 101872.638 | 41401.92 | 60813.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168407.22 | 0 | 0
May | 573441000000 | 387519.814 | 27-MAY-10:45 | 101872.638 | 41401.92 | 60813.404 | 0 | 4572.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178859.677 | 0 | 0
June | 601885000000 | 443448.158 | 14-JUN-17:15 | 67915.092 | 36859.929 | 60813.404 | 0 | 40258.324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237601.408 | 0 | 0
July | 673668000000 | 487501.605 | 08-JUL-10:00 | 101872.638 | 41401.92 | 60813.404 | 0 | 70997.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 212416.367 | 0 | 0
August | 657225000000 | 464108.702 | 12-AUG-10:00 | 101872.638 | 41401.92 | 60813.404 | 0 | 52518.342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207502.398 | 0 | 0
September | 582768000000 | 404024.323 | 08-SEP-17:15 | 67915.092 | 36859.929 | 60813.404 | 0 | 10193.389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 228242.509 | 0 | 0
October | 565451000000 | 383509.608 | 07-OCT-10:15 | 101872.638 | 41401.92 | 60813.404 | 0 | 3292.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 176128.686 | 0 | 0
November | 547504000000 | 383266.183 | 09-NOV-11:15 | 101872.638 | 41401.92 | 60813.404 | 0 | 1306.228 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 177871.992 | 0 | 0
December | 562209000000 | 363203.784 | 02-DEC-11:15 | 101872.638 | 41401.92 | 60813.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159115.822 | 0 | 0
Annual Sum or Average | 6945670000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 508517000000 | 359399.215 |  | 67915.092 | 36859.929 | 60813.404 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155311.253 | 0 | 0
Maximum of Months | 673668000000 | 487501.605 |  | 101872.638 | 41401.92 | 60813.404 | 0 | 70997.275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 237601.408 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 106182.11 | 48551.21 | 0 | 154733.32
Cost per Total Building Area ($/m2) | 25.4 | 11.61 | 0 | 37.01
Cost per Net Conditioned Building Area ($/m2) | 25.4 | 11.61 | 0 | 37.01

## Fairbanks (hidden)
| Total Energy [GJ] | Energy Per Total Building Area [MJ/m2] | Energy Per Conditioned Building Area [MJ/m2]
Total Site Energy | 16395.55 | 3921.63 | 3921.63
Net Site Energy | 16395.55 | 3921.63 | 3921.63
Total Source Energy | 35624.58 | 8521.01 | 8521.01
Net Source Energy | 35624.58 | 8521.01 | 8521.01
Area [m2]
Total Building Area | 4180.79
Net Conditioned Building Area | 4180.79
Unconditioned Building Area | 0
| Electricity [GJ] | Natural Gas [GJ] | Other Fuel [GJ] | District Cooling [GJ] | District Heating [GJ] | Water [m3]
Heating | 0 | 9022.53 | 0 | 0 | 0 | 0
Cooling | 12.41 | 0 | 0 | 0 | 0 | 0
Interior Lighting | 1512.65 | 0 | 0 | 0 | 0 | 0
Exterior Lighting | 76.64 | 0 | 0 | 0 | 0 | 0
Interior Equipment | 785.69 | 199.13 | 0 | 0 | 0 | 0
Exterior Equipment | 0 | 0 | 0 | 0 | 0 | 0
Fans | 1909.08 | 0 | 0 | 0 | 0 | 0
Pumps | 0 | 0 | 0 | 0 | 0 | 0
Heat Rejection | 0 | 0 | 0 | 0 | 0 | 0
Humidification | 0 | 0 | 0 | 0 | 0 | 0
Heat Recovery | 0 | 0 | 0 | 0 | 0 | 0
Water Systems | 0 | 28.47 | 0 | 0 | 0 | 87.12
Refrigeration | 2848.96 | 0 | 0 | 0 | 0 | 0
Generators | 0 | 0 | 0 | 0 | 0 | 0
Total End Uses | 7145.42 | 9250.12 | 0 | 0 | 0 | 87.12
| Area [m2] | Conditioned (Y/N) | Volume [m3] | Multipliers | Gross Wall Area [m2] | Window Glass Area [m2] | Lighting [W/m2] | People [m2] per person | Plug and Process [W/m2]
BAKERY | 209.04 | Yes | 1274.65 | 1 | 189.08 | 0 | 29.94 | 11.61 | 80.6828
DELI | 224.72 | Yes | 1370.24 | 1 | 138.39 | 0 | 29.94 | 11.61 | 83.1351
DRYSTORAGE | 621.89 | Yes | 3792.03 | 1 | 477.11 | 0 | 11.9 | 27.87 | 8.07
OFFICE | 88.84 | Yes | 541.72 | 1 | 115.05 | 0 | 21.36 | 18.58 | 8.07
PRODUCE | 711.36 | Yes | 4337.61 | 1 | 366.09 | 0 | 29.94 | 11.61 | 5.38
SALES | 2324.94 | Yes | 14176.6 | 1 | 323.44 | 174.7 | 29.94 | 11.61 | 5.38
Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Conditioned Total | 4180.79 |  | 25492.85 |  | 1609.16 | 174.7 | 27.0742 | 12.83 | 13.7818
Unconditioned Total | 0 |  | 0 |  | 0 | 0
| Construction | Reflectance | U-Factor with Film [W/m2-K] | U-Factor no Film [W/m2-K] | Gross Area [m2] | Azimuth [deg] | Tilt [deg] | Cardinal Direction
BAKERY_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 60.34 | 180 | 90 | S
BAKERY_WALL__2 | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 128.73 | 90 | 90 | E
BAKERY_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 209.04 | 0 | 180
BAKERY_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 209.04 | 180 | 0
DELI_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 138.39 | 90 | 90 | E
DELI_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 224.72 | 0 | 180
DELI_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 224.72 | 180 | 0
DRYSTORAGE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 422.4 | 0 | 90 | N
DRYSTORAGE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 54.71 | 270 | 90 | W
DRYSTORAGE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 621.89 | 0 | 180
DRYSTORAGE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 621.89 | 180 | 0
OFFICE_WALL_EAST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 54.71 | 90 | 90 | E
OFFICE_WALL_NORTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 60.34 | 0 | 90 | N
OFFICE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 88.84 | 0 | 180
OFFICE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 88.84 | 180 | 0
PRODUCE_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 98.96 | 180 | 90 | S
PRODUCE_WALL_WEST | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 267.12 | 270 | 90 | W
PRODUCE_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 711.36 | 0 | 180
PRODUCE_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 711.36 | 180 | 0
SALES_WALL_SOUTH | EXT-WALLS-MASS-NONRES | 0.08 | 0.267 | 0.278 | 323.44 | 180 | 90 | S
SALES_FLOOR | EXT-SLAB | 0.3 | 3.12 | 12.904 | 2324.94 | 0 | 180
SALES_CEILING | ROOF-IEAD-NONRES | 0.3 | 0.174 | 0.18 | 2324.94 | 180 | 0
| Construction | Area of One Opening [m2] | Area of Openings [m2] | U-Factor [W/m2-K] | SHGC | Visible Transmittance | Shade Control | Parent Surface | Azimuth [deg] | Cardinal Direction
SALES_WALL_SOUTH_WINDOW | WINDOW-NONRES-FIXED | 174.7 | 174.7 | 2.956 | 0.616 | 0.541 | No | SALES_WALL_SOUTH | 180 | S
Total or Average |  |  | 174.7 | 2.96 | 0.616 | 0.541
North Total or Average |  |  | 0 | - | - | -
Non-North Total or Average |  |  | 174.7 | 2.96 | 0.616 | 0.541
| Type | Nominal Capacity [W] | Nominal Efficiency [W/W]
None
| Type | Nominal Total Capacity [W] | Nominal Sensible Capacity [W] | Nominal Latent Capacity [W] | Nominal Sensible Heat Ratio | Nominal Efficiency [W/W]
PSZ-AC:1_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 24277.58 | 19389.42 | 4888.16 | 0.8 | 3.22
PSZ-AC:2_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 130739.48 | 104415.78 | 26323.71 | 0.8 | 3.32
PSZ-AC:3_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 44324.28 | 35399.82 | 8924.46 | 0.8 | 2.8
PSZ-AC:4_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 371545.35 | 296736.65 | 74808.7 | 0.8 | 3.07
PSZ-AC:5_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 131599.1 | 105102.31 | 26496.79 | 0.8 | 3.32
PSZ-AC:6_COOLC DXCOIL | Coil:Cooling:DX:SingleSpeed | 47143.44 | 37651.36 | 9492.08 | 0.8 | 2.8
| Type | Nominal Total Capacity [W] | Nominal Efficiency [W/W]
PSZ-AC:1_HEATC | Coil:Heating:Gas | 37223.95 | 0.8
PSZ-AC:2_HEATC | Coil:Heating:Gas | 216132.22 | 0.78
PSZ-AC:3_HEATC | Coil:Heating:Gas | 262984.71 | 0.78
PSZ-AC:4_HEATC | Coil:Heating:Gas | 771724.85 | 0.78
PSZ-AC:5_HEATC | Coil:Heating:Gas | 262529.01 | 0.78
PSZ-AC:6_HEATC | Coil:Heating:Gas | 88886.92 | 0.78
| Type | Total Efficiency [W/W] | Delta Pressure [pa] | Max Flow Rate [m3/s] | Rated Power [W] | Motor Heat In Air Fraction | End Use
BAKERY EXHAUST FAN | Fan:ZoneExhaust | 0.34 | 125 | 0.35 | 130.92 | 1 | Zone Exhaust Fans
DELI EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 0.34 | 0 | 1 | Zone Exhaust Fans
SALES EXHAUST FAN | Fan:ZoneExhaust | 1 | 0 | 1.08 | 0 | 1 | Zone Exhaust Fans
PSZ-AC:1_FAN | Fan:ConstantVolume | 0.55 | 622 | 1.47 | 1670.75 | 1 | Fan Energy
PSZ-AC:2_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.9 | 14816.52 | 1 | Fan Energy
PSZ-AC:3_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.68 | 2928.33 | 1 | Fan Energy
PSZ-AC:4_FAN | Fan:ConstantVolume | 0.6 | 1017.59 | 22.45 | 37783.14 | 1 | Fan Energy
PSZ-AC:5_FAN | Fan:ConstantVolume | 0.59 | 1109.65 | 7.95 | 14913.93 | 1 | Fan Energy
PSZ-AC:6_FAN | Fan:ConstantVolume | 0.57 | 622 | 2.85 | 3114.58 | 1 | Fan Energy
| Type | Control | Head [pa] | Power [W] | Motor Efficiency [W/W]
SWHSYS1 PUMP | Pump:VariableSpeed | INTERMITTENT | 0.1 | 0 | 1
| Type | Storage Volume [m3] | Input [W] | Thermal Efficiency [W/W] | Recovery Efficiency [W/W] | Energy Factor
SWHSYS1 WATER HEATER | WaterHeater:Mixed | 0.4 | 845000 | 0.78 | 1.67 | 0.58
| CO2:FACILITY [kg] | NOX:FACILITY [kg] | SO2:FACILITY [kg] | PM:FACILITY [kg] | HG:FACILITY [kg] | WATERENVIRONMENTALFACTORS:FACILITY [L] | CARBON EQUIVALENT:FACILITY [kg]
January | 204700.4355 | 226.2738 | 846.9458 | 0 | 0.003 | 169897.8205 | 77072.3958
February | 180044.0123 | 199.9427 | 764.2578 | 0 | 0.0027 | 153315.3747 | 67931.095
March | 176800.5582 | 201.1854 | 851.8454 | 0 | 0.003 | 170910.7137 | 67452.8577
April | 145539.2134 | 170.6652 | 806.9349 | 0 | 0.0028 | 161922.7357 | 56303.6041
May | 128422.2121 | 156.2394 | 830.1574 | 0 | 0.0028 | 166604.6601 | 50550.5744
June | 124921.5767 | 154.4312 | 858.7995 | 0 | 0.0029 | 172361.0501 | 49549.7547
July | 131903.3341 | 163.7378 | 920.9299 | 0 | 0.0031 | 184832.7537 | 52423.0025
August | 131449.5652 | 162.1444 | 896.2112 | 0 | 0.003 | 179868.4508 | 52084.1419
September | 130186.8974 | 157.4147 | 821.2361 | 0 | 0.0028 | 164810.991 | 51095.6747
October | 154077.0756 | 180.1233 | 842.6863 | 0 | 0.0029 | 169094.5964 | 59521.3553
November | 178090.6665 | 200.7994 | 819.2727 | 0 | 0.0029 | 164367.1583 | 67659.7477
December | 194869.5708 | 217.3455 | 846.829 | 0 | 0.003 | 169884.5077 | 73669.2752
Annual Sum or Average | 1881010 | 2190.3029 | 10106.106 | 0 | 0.0352 | 2027870 | 725313.4789
Minimum of Months | 124921.5767 | 154.4312 | 764.2578 | 0 | 0.0027 | 153315.3747 | 49549.7547
Maximum of Months | 204700.4355 | 226.2738 | 920.9299 | 0 | 0.0031 | 184832.7537 | 77072.3958
| ELECTRICITY:FACILITY [J] | ELECTRICITY:FACILITY {Maximum}[W] | ELECTRICITY:FACILITY {TIMESTAMP} | INTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | INTERIOREQUIPMENT:ELECTRICITY {AT MAX/MIN} [W] | FANS:ELECTRICITY {AT MAX/MIN} [W] | HEATING:ELECTRICITY {AT MAX/MIN} [W] | COOLING:ELECTRICITY {AT MAX/MIN} [W] | EXTERIORLIGHTS:ELECTRICITY {AT MAX/MIN} [W] | PUMPS:ELECTRICITY {AT MAX/MIN} [W] | HEATREJECTION:ELECTRICITY [Invalid/Undefined] | EXTERIOREQUIPMENT:ELECTRICITY [Invalid/Undefined] | HUMIDIFICATION:ELECTRICITY [Invalid/Undefined] | HEATRECOVERY:ELECTRICITY [Invalid/Undefined] | WATERSYSTEMS:ELECTRICITY [Invalid/Undefined] | REFRIGERATION:ELECTRICITY {AT MAX/MIN} [W] | GENERATORS:ELECTRICITY [Invalid/Undefined] | ELECTRICITYPRODUCED:FACILITY [Invalid/Undefined]
January | 598653000000 | 375784.503 | 21-JAN-11:15 | 101872.638 | 41401.92 | 75358.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157151.782 | 0 | 0
February | 540223000000 | 373791.923 | 27-FEB-11:15 | 101872.638 | 41401.92 | 75358.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155159.201 | 0 | 0
March | 602222000000 | 377061.895 | 09-MAR-11:15 | 101872.638 | 41401.92 | 75358.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 158429.174 | 0 | 0
April | 570552000000 | 376350.873 | 14-APR-10:15 | 101872.638 | 41401.92 | 75358.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 157718.152 | 0 | 0
May | 587050000000 | 394350.92 | 31-MAY-10:15 | 101872.638 | 41401.92 | 75358.163 | 0 | 106.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175611.228 | 0 | 0
June | 607333000000 | 420663.603 | 21-JUN-17:15 | 67915.092 | 36859.929 | 75358.163 | 0 | 20340.863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220189.556 | 0 | 0
July | 651278000000 | 424592.23 | 29-JUL-17:15 | 56595.91 | 32317.938 | 75358.163 | 0 | 36233.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 224086.819 | 0 | 0
August | 633786000000 | 420024.297 | 15-AUG-17:15 | 67915.092 | 36859.929 | 75358.163 | 0 | 23030.422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 216860.691 | 0 | 0
September | 580729000000 | 387086.501 | 01-SEP-10:15 | 101872.638 | 41401.92 | 75358.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168453.78 | 0 | 0
October | 595823000000 | 383219.915 | 02-OCT-10:15 | 101872.638 | 41401.92 | 75358.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164587.193 | 0 | 0
November | 579165000000 | 374151.105 | 14-NOV-11:15 | 101872.638 | 41401.92 | 75358.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155518.384 | 0 | 0
December | 598606000000 | 379094.933 | 18-DEC-11:15 | 101872.638 | 41401.92 | 75358.163 | 0 | 0 | 4916 | 0 | 0 | 0 | 0 | 0 | 0 | 155546.211 | 0 | 0
Annual Sum or Average | 7145420000000 | [9 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
Minimum of Months | 540223000000 | 373791.923 |  | 56595.91 | 32317.938 | 75358.163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155159.201 | 0 | 0
Maximum of Months | 651278000000 | 424592.23 |  | 101872.638 | 41401.92 | 75358.163 | 0 | 36233.4 | 4916 | 0 | 0 | 0 | 0 | 0 | 0 | 224086.819 | 0 | 0
| Electric | Gas | Other | Total
Cost ($) | 175892.8 | 38278.48 | 0 | 214171.28
Cost per Total Building Area ($/m2) | 42.07 | 9.16 | 0 | 51.23
Cost per Net Conditioned Building Area ($/m2) | 42.07 | 9.16 | 0 | 51.23

## Picture
DOE Commercial Building Benchmark - Super Market
Sales
Bakery
Deli
Produce
Office
DryStorage

## Schedules
Schedule | Type | Through | Day of Week | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | Hours Per Day | Hours Per Week | Hours Per Year
Hours_of_operation | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 112 | 5840
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
ALWAYS_ON | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ALWAYS_OFF | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HVACOperationSchd | On/Off | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 112 | 5840
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
BLDG_LIGHT_SCH | Fraction | Through 12/31 | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.5 | 0.2 | 0.05 | 0.05 | 11.3 | 72.2 | 3764.71
|  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.6 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.5 | 0.3 | 0.3 | 0.1 | 0.05 | 0.05 | 9.9
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.05 | 0.05 | 5.8
BLDG_OCC_SCH | Fraction | Through 12/31 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | 0.8 | 0.7 | 0.5 | 0.5 | 0.3 | 0.3 | 0.3 | 0 | 0 | 7.6 | 49 | 2555
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.5 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 7.6
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0 | 0 | 3.4
BLDG_EQUIP_SCH | Fraction | Through 12/31 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.8 | 0.7 | 0.4 | 0.2 | 0.2 | 13.9 | 91.6 | 4776.29
|  |  | Sat | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.5 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.5 | 0.5 | 0.3 | 0.15 | 0.15 | 12.3
|  |  | SummerDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun, Hol, Other | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.3 | 0.3 | 0.3 | 0.3 | 0.6 | 0.6 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.6 | 0.4 | 0.4 | 0.4 | 0.4 | 0.15 | 0.15 | 9.8
BLDG_ELEVATORS | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12 | 0.22 | 0.64 | 0.74 | 0.68 | 0.68 | 0.71 | 0.72 | 0.72 | 0.73 | 0.68 | 0.68 | 0.58 | 0.54 | 0 | 0 | 0 | 8.44 | 52.69 | 2747.41
|  |  | Sat, WinterDesign | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0.21 | 0.56 | 0.66 | 0.68 | 0.68 | 0.69 | 0.7 | 0.69 | 0.66 | 0.58 | 0.47 | 0.43 | 0.43 | 0.08 | 0 | 0 | 7.61
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11 | 0.13 | 0.35 | 0.37 | 0.37 | 0.39 | 0.41 | 0.38 | 0.34 | 0.03 | 0 | 0 | 0 | 0 | 0 | 2.88
BLDG_SWH_SCH | Fraction | Through 12/31 | WD, SummerDesign | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.15 | 0.23 | 0.32 | 0.41 | 0.57 | 0.62 | 0.61 | 0.5 | 0.45 | 0.46 | 0.47 | 0.42 | 0.34 | 0.33 | 0.23 | 0.13 | 0.08 | 6.62 | 44.59 | 2325.05
|  |  | Sat, WinterDesign | 0.11 | 0.1 | 0.08 | 0.06 | 0.06 | 0.06 | 0.07 | 0.2 | 0.24 | 0.27 | 0.42 | 0.54 | 0.59 | 0.6 | 0.49 | 0.48 | 0.47 | 0.46 | 0.44 | 0.36 | 0.29 | 0.22 | 0.16 | 0.13 | 6.9
|  |  | Sun, Hol, Other | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.1 | 0.12 | 0.14 | 0.29 | 0.31 | 0.36 | 0.36 | 0.34 | 0.35 | 0.37 | 0.34 | 0.25 | 0.27 | 0.21 | 0.16 | 0.1 | 0.06 | 4.59
ACTIVITY_SCH | Any Number | Through 12/31 | All | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2880 | 20160 | 1051200
WORK_EFF_SCH | Fraction | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AIR_VELO_SCH | Any Number | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
CLOTHING_SCH | Any Number | Through 04/30 | All | [24 empty] | 24 | 168 | 6924 | bar: 1 to 24
|  | Through 09/30 | All | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 12 | 84
|  | Through 12/31 | All | [24 empty] | 24 | 168 | bar: 1 to 24
INFIL_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8 | 56 | 2920
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 8
INFIL_HALF_ON_SCH | Fraction | Through 12/31 | WD, SummerDesign | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16 | 115.5 | 6022.5
|  |  | Sat | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 19.5
SHADING_SCH | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PlantOnSched | On/Off | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
FAN_SCH | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
ReheatCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
CoolingCoilAvailSched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
HTGSETP_SCH | Temperature | Through 12/31 | WD, WinterDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8 | 3225.6 | 168192
|  |  | SummerDesign | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 374.4
|  |  | Sat | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
|  |  | Sun, Hol, Other | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 15.6 | 15.6 | 460.8
CLGSETP_SCH | Temperature | Through 12/31 | WD, SummerDesign | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624 | 4368 | 227760
|  |  | Sat | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
|  |  | WinterDesign | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720
|  |  | Sun, Hol, Other | 30 | 30 | 30 | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 624
Humidity Setpoint Schedule | Humidity | Through 12/31 | WD, SummerDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200 | 8400 | 438000
|  |  | Sat, WinterDesign | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
|  |  | Sun, Hol, Other | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200
MinRelHumSetSch | Humidity | Through 12/31 | All | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 720 | 5040 | 262800
MaxRelHumSetSch | Humidity | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
MinOA_MotorizedDamper_Sched | Fraction | Through 12/31 | WD, SummerDesign | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16 | 112 | 5840
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
|  |  | WinterDesign | [24 empty] | 24 | bar: 1 to 24
|  |  | Sun, Hol, Other | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 16
MinOA_Sched | Fraction | Through 12/31 | All | [24 empty] | 24 | 168 | 8760 | bar: 1 to 24
Dual Zone Control Type Sched | Control Type | Through 12/31 | All | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 96 | 672 | 35040
Seasonal-Reset-Supply-Air-Temp-Sch | Temperature | Through 3/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184 | 113880
|  | Through 9/30 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
|  | Through 12/31 | All | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 312 | 2184
CW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 160.8 | 1125.6 | 58692
HW-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
Heating-Supply-Air-Temp-Sch | Temperature | Through 12/31 | All | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 384 | 2688 | 140160
Deli Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Deli Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Deli Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Deli Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Deli_Case:1_ MULTIDECKDIARYANDDELICASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Deli_Case:2_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Deli_Case:2_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Deli_Case:2_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Deli_Case:2_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Sales_Case:1_MEATDISPLAYCASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:1_MEATDISPLAYCASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:1_MEATDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:2_ MULTIDECKDIARYANDDELICASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Sales_Case:3_GLASSDOORFROZENFOOD_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57 | 3.97 | 206.83
Sales_Case:3_GLASSDOORFROZENFOOD_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73 | 5.13 | 267.67
Sales_Case:3_GLASSDOORFROZENFOOD_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:3_GLASSDOORFROZENFOOD_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Sales_Case:4_OPENWELLICECREAMDISPLAYCASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Sales_Case:5_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:5_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:5_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Sales_Case:5_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Sales_Case:6_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:6_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:6_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Sales_Case:6_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Sales_Case:7_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Sales_Case:7_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Sales_Case:7_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Sales_Case:7_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseStockingSched | Any Number | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 595 | 31025
Produce_Case:1_ MULTIDECKDIARYANDDELICASE_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.2 | 0.2 | 0.2 | 10.4 | 72.8 | 3796
Bakery Water Equipment Latent fract sched | Fraction | Through 12/31 | All | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 1.2 | 8.4 | 438
Bakery Water Equipment Sensible fract sched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 4.8 | 33.6 | 1752
Bakery Water Equipment Temp Sched | Temperature | Through 12/31 | All | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 43.3 | 1039.2 | 7274.4 | 379308
Bakery Water Equipment Hot Supply Temp Sched | Temperature | Through 12/31 | All | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1320 | 9240 | 481800
Bakery_Case:1_WALKINFREEZER_CaseDefrost2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.67 | 4.67 | 243.33
Bakery_Case:1_WALKINFREEZER_CaseDripDown2aDaySched | On/Off | Through 12/31 | All | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 365
Bakery_Case:1_WALKINFREEZER_WalkInStockingSched | Any Number | Through 12/31 | Tue, Fri | 0 | 0 | 0 | 0 | 725 | 417 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 1432 | 74668.57
|  |  | Other | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 125 | 117 | 90 | 0 | 0 | 664
Bakery_Case:1_WALKINFREEZER_CaseCreditReduxSched | Fraction | Through 12/31 | All | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.2 | 0.2 | 0.2 | 7.6 | 53.2 | 2774
SWHSys1-Loop-Temp-Schedule | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Setpoint Temperature Schedule Name | Temperature | Through 12/31 | All | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1440 | 10080 | 525600
SWHSys1 Water Heater Ambient Temperature Schedule Name | Temperature | Through 12/31 | All | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 528 | 3696 | 192720