## Instructions
Title Block
Test Report Template Name: | Single Packaged Vertical Unit
Version Number: | v2.0
Latest Template Revision: | 2015-06-05
Tab Name: | Instructions
File Name: | Single Packaged Vertical Unit - v2.0.xlsx
Reference Test Procedure
For DOE Testing: 10 CFR 431.96 (which references AHRI 390, Performance Rating of Single Package Vertical Air-Conditioners and Heat Pumps)
AHRI 390 - 2003: Performance Rating of Single Package Vertical Air-Conditioners and Heat Pumps
Table of Contents
Tab | Contents
Instructions | Instructions for workbook and summary of results
General Info and Test Results | Space to describe general lab and product information
Instrumentation | Space to describe list of instruments used and instrument calibration data
Setup | Space to describe test setup
Photos | Space to add photographs taken of the test setup and device
Test Settings | Specification of settings for each test performed
Cooling Mode Test Data | Recorded data for the cooling mode test (steady-state wet coil cooling mode)
Heating Mode Test Data | Recorded data for the heating mode test (steady-state maximum temperature and high temperature heating mode)
Test Comments | Space to describe any notable information about the test
Report Sign-off Block | Report review history
Drop-Downs | Drop-downs used
Tables | Reference tables
Version Control | Revision history
Legend
Tabs | Tabs with input cells
Cells | Input cell
Auto-populated cell
Provided data
NOT USED
Instructions for Completing this Workbook
Follow the steps below, filling in all input cells (shaded light blue) in each tab you are instructed to complete. Using TAB to "hop" from input cell to input cell is useful, but does not ensure that all input cells are reached. To guarantee that you enter all required information, you must visually scan for light blue cells in the entire area bounded by yellow-shaded cells.
Important: Start with a clean (unused) template copy for each new report. Enter only data and information that are unique to the unit tested and the current test of that unit. All abbreviations and variable names should be consistent with the reference test procedure.
STEP: | FILL IN INPUT CELLS IN THIS TAB:
Step 1 | General Info and Test Results
Step 2 | Instrumentation
Step 3 | Setup
Step 4 | Photos
Step 5 | Test Settings
Step 6 | Fill in the 'Test Data' tabs for the appropriate completed tests:
Step 6-1 | Cooling Mode Test Data
Step 6-2 | Heating Mode Test Data
Step 7 | Test Comments
Step 8 | Report Sign-off Block

## General Info and Test Results
Title Block
Test Report Template Name: | Single Packaged Vertical Unit |  | Back to Instructions
Version Number: | v2.0
Latest Template Revision: | 2015-06-05
Tab Name: | General Info and Test Results
File Name: | Single Packaged Vertical Unit - v2.0.xlsx
Test Completion Date: | [MM/DD/YYYY]
Lab Information |  |  | Test Results
Lab Name: |  |  | Measured Values
Test Location: |  |  | Variable | Result
EER
Test Information |  |  | COP
Date Energy Test Started: | [MM/DD/YYYY]
Date Energy Test Finished: | [MM/DD/YYYY]
Date of Last Calibration for Test Room | [MM/DD/YYYY]
NOTE: This is a copy; sign-off is done in the Report Sign-Off Block tab
Product Information |  |  | Test Report Sign-Off Block
We certify that the information and data in this report: (1) were obtained from the specific test unit under test; (2) were obtained during the specific test being reported; (3) were not copied from any other source, except where instructed to do so; and (4) were not altered or modified in any way.
General Information
Product Type
|  |  | Role |  | Date | Entity
Product Design |  |  | Test Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Refrigerant Used (R-22, R-410A, Other)? |  |  | Template Completion |  | [MM/DD/YYYY] | [Test Lab Name]
If Other (please specify) |  |  | Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
|  |  | Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Rated Performance (Complete Unit)
Product Reported Cooling Capacity: |  | BTU
Product Reported EER:
Product Reported Heating Capacity (if applicable): |  | BTU
Product Reported COP (if applicable):
Product Input Voltage: |  | V
Date Received: | [MM/DD/YYYY]
Condition as Received:
Packaged unit (if applicable)
Brand:
Manufacturer:
Manufacturer Model Number:
Serial Number:
Date of Manufacture (if available):

## Instrumentation
Title Block
Test Report Template Name: | Single Packaged Vertical Unit |  | Back to Instructions
Version Number: | v2.0
Latest Template Revision: | 2015-06-05
Tab Name: | Instrumentation
File Name: | Single Packaged Vertical Unit - v2.0.xlsx
Test Completion Date: | [MM/DD/YYYY]
Setup (This table should include instrumentation, sensors, and all equipment used during testing)
Instrument Type | Brand | Model # | Sensor Location | Accuracy | Date of Last Calibration | Deadline for Next Calibration
Sensor Placement
Describe placement of sensors used to measure indoor and outdoor temperatures:
If additional sensors were used, describe placement:

## Setup
Title Block
Test Report Template Name: | Single Packaged Vertical Unit | Back to Instructions
Version Number: | v2.0
Latest Template Revision: | 2015-06-05
Tab Name: | Setup
File Name: | Single Packaged Vertical Unit - v2.0.xlsx
Test Completion Date: | [MM/DD/YYYY]
Setup of test room
Were the test rooms set up according to AHRI Standard 390-2003, which incorporates sections 8.1.2 and 8.1.3 of ASHRAE Standard 37-1988?
If No, list and describe all differences between actual setup and AHRI Standard 390-2003 (which includes sections 8.1.2 and 8.1.3 of ASHRAE Standard 37-1988).
Setup of SPVU
Was the test unit set up according to the applicable sections of AHRI Standard 390 - 2003, which incorporates sections of ASHRAE Standard 37-1988?
If No, list and describe all differences between actual setup and AHRI Standard 390-2003 (which includes sections of ASHRAE Standard 37-1988).
Quote the manufacturer instructions for installing this unit, and note in detail all differences between the manufacturer instructions and the actual installation.
(1) Include all instructions, (2) A PDF file containing the instructions (downloaded or scanned) is acceptable.

## Photos
Title Block |  | Back to Instructions
Test Report Template Name: | Single Packaged Vertical Unit
Version Number: | v2.0
Latest Template Revision: | 2015-06-05
Tab Name: | Photos
File Name: | Single Packaged Vertical Unit - v2.0.xlsx
Test Completion Date: | [MM/DD/YYYY]
Photos 1-4 are to be taken of the unit directly out of the box, before installation.
1. Picture of unit on both sides (front and back), once it is out of the package. (Include as many pictures as neccesary)
2. Identification sticker showing model number and serial number. |  |  | 3. Sticker showing nameplate information (if separate from #2)
4. FTC EnergyGuide label (if present).
5. Picture of indoor side of SPVU as installed in final set-up (showing all sensors) |  |  | 6. Picture of outdoor side of SPVU as installed in final set-up (showing all sensors)
7. Additional Photos of sensor placements (if necessary)

## Test Settings
Title Block
Test Report Template Name: | Single Packaged Vertical Unit |  | Back to Instructions
Version Number: | v2.0
Latest Template Revision: | 2015-06-05
Tab Name: | Test Settings
File Name: | Single Packaged Vertical Unit - v2.0.xlsx
Test Completion Date: | [MM/DD/YYYY]
SPVU Settings - Controls
>>>>>>>>>> Paste photo(s) showing exact settings and/or displays for the unit (during test) to |  | the Photos tab (Photo Box #4)
Please include a description of how the settings were entered, specific to this particular test unit:
Electromechanical or Electronic Controls?
Cooling Setting *
Heating Setting *
Fan Setting *
Temperature Setting *
* Include unit of measure if necessary
Other settings (if neccesary) | Extra Setting #1 |  | Extra Setting #2 | Extra Setting #3
--- Description
--- Setting *
* Include unit of measure if necessary
Additional Description
Describe settings used on the SPVU for test, or reference any picture of controls in the 'Photos' Tab

## Cooling Mode Test Data
Title Block |  |  | Back to Instructions
Test Report Template Name: | Single Packaged Vertical Unit
Version Number: | v2.0
Latest Template Revision: | 2015-06-05
Tab Name: | Cooling Mode Test Data
File Name: | Single Packaged Vertical Unit - v2.0.xlsx
Test Completion Date: | [MM/DD/YYYY]
Cooling Test Conditions Summary - Test Chamber Devices
Compliance with Equilibrium Requirements
Has chamber been at equilibrium for the minimum 30 minutes?
Length of Compressor Run-in Time (hours)
Cooling Mode - Indoor Air Enthalpy Method
Electrical Input Measurements
Measurement
|  | Avg | Min | Max
Applied voltage to unit (V)
Frequency (Hz)
Line current (Amps)
Total system power (Watts)
Pressure Measurements
Measurement
|  | Avg | Min | Max
Barometric pressure - (in. Hg)
Indoor nozzle pressure delta (in. H2O)
Indoor external static pressure (in. H2O)
Refrigerant Measurements
Measurement
|  | Avg | Min | Max
Suction temperature at compressor (°F)
Discharge temperature at compressor (°F)
Vapor temperature at condenser coil (°F)
Liquid line temperature at condenser coil (°F)
Airflow Measurements
Measurement
|  | Avg | Min | Max
Unit indoor airflow (cfm)
Unit indoor standard airflow (scfm)
Indoor Fan Speed (rpm) [if recorded]
Air Temperatures
Measurement
|  | Avg | Min | Max
Indoor air entering dry-bulb temperature (°F)
Indoor air entering wet-bulb temperature (°F)
Indoor entering enthalpy (Btu/lbm)
Indoor air leaving dry-bulb temperature (°F)
Indoor air leaving wet-bulb temperature (°F)
Indoor leaving enthalpy (Btu/lbm)
Indoor nozzle dry-bulb temperature (°F)
Indoor nozzle wet-bulb temperature (°F)
Outdoor air entering dry-bulb temperature (°F)
Outdoor air entering wet-bulb temperature (°F)
Outdoor entering enthalpy (Btu/lbm)
Cooling Capacity
Measurement
Total sensible cooling capacity (Btu/hr)
Total latent cooling capacity (Btu/hr)
Duct loss (Btu/hr) (if applicable)
Total cooling capacity (Btu/hr)
Results
|  | Measurement |  |  | Calculated Result (rounded per significant figures conventions and instrumentation resolution)
Total corrected cooling capacity (Btu/hr)
| Total system power (Watts) | 0
System Efficiency (EER)
Cooling Mode - Outdoor Air Enthalpy Method
Electrical Input Measurements
Measurement
|  | Avg | Min | Max
Applied voltage to unit (V)
Frequency (Hz)
Line current (Amps)
Total system power (Watts)
Pressure Measurements
Measurement
|  | Avg | Min | Max
Barometric pressure - (in. Hg)
Indoor nozzle pressure delta (in. H2O)
Indoor external static pressure (in. H2O)
Refrigerant Measurements
Measurement
|  | Avg | Min | Max
Suction temperature at compressor (°F)
Discharge temperature at compressor (°F)
Vapor temperature at condenser coil (°F)
Liquid line temperature at condenser coil (°F)
Airflow Measurements
Measurement
|  | Avg | Min | Max
Unit indoor airflow (cfm)
Unit indoor standard airflow (scfm)
Indoor Fan Speed (rpm) [if recorded]
Unit outdoor airflow (cfm)
Unit outdoor standard airflow (scfm)
Outdoor Fan Speed (rpm) [if recorded]
Air Temperatures
Measurement
|  | Avg | Min | Max
Indoor air entering dry-bulb temperature (°F)
Indoor air entering wet-bulb temperature (°F)
Indoor entering enthalpy (Btu/lbm)
Indoor air leaving dry-bulb temperature (°F)
Indoor air leaving wet-bulb temperature (°F)
Indoor leaving enthalpy (Btu/lbm)
Indoor nozzle dry-bulb temperature (°F)
Indoor nozzle wet-bulb temperature (°F)
Outdoor air entering dry-bulb temperature (°F)
Outdoor air entering wet-bulb temperature (°F)
Outdoor entering enthalpy (Btu/lbm)
Outdoor air leaving dry-bulb temperature (°F)
Outdoor air leaving wet-bulb temperature (°F)
Outdoor leaving enthalpy (Btu/lbm)
Outdoor nozzle dry-bulb temperature (°F)
Outdoor nozzle wet-bulb temperature (°F)
Cooling Capacity
Indoor Measurements
Indoor sensible cooling capacity (Btu/hr)
Indoor latent cooling capacity (Btu/hr)
Indoor duct loss (Btu/hr) (if applicable)
Indoor total cooling capacity (Btu/hr)
Outdoor Measurements
Outdoor sensible cooling capacity (Btu/hr)
Outdoor latent cooling capacity (Btu/hr)
Outdoor duct loss (Btu/hr) (if applicable)
Outdoor power draw (Btu/h)
Outdoor total cooling capacity
Comparison
Heat balance (%) (indoor vs. outdoor total capacity) [must be <6%]
Heat balance (%) (indoor air enthalpy vs outdoor air enthalpy) [must be <2%]
Results
Measurement
Total corrected cooling capacity (Btu/hr)
| Total system power (Watts) | 0
System Efficiency (EER)

## Heating Mode Test Data
Title Block |  |  | Back to Instructions
Test Report Template Name: | Single Packaged Vertical Unit
Version Number: | v2.0
Latest Template Revision: | 2015-06-05
Tab Name: | Heating Mode Test Data
File Name: | Single Packaged Vertical Unit - v2.0.xlsx
Test Completion Date: | [MM/DD/YYYY]
Heating Mode - Indoor Air Enthalpy Method
Electrical Input Measurements
Measurement
|  | Avg | Min | Max
Applied voltage to unit (V)
Frequency (Hz)
Line current (Amps)
Total system power (Watts)
Pressure Measurements
Measurement
|  | Avg | Min | Max
Barometric pressure - (in. Hg)
Indoor nozzle pressure delta (in. H2O)
Indoor external static pressure (in. H2O)
Refrigerant Measurements
Measurement
|  | Avg | Min | Max
Suction temperature at compressor (F)
Discharge temperature at compressor (F)
Vapor temperature at condenser coil (F)
Liquid line temperature at condenser coil (F)
Airflow Measurements
Measurement
|  | Avg | Min | Max
Unit indoor airflow (cfm)
Unit indoor standard airflow (scfm)
Indoor Fan Speed (rpm) [if recorded]
Air Temperatures
Measurement
|  | Avg | Min | Max
Indoor air entering dry-bulb temperature (F)
Indoor air entering wet-bulb temperature (F)
Indoor entering enthalpy (Btu/lbm)
Indoor air leaving dry-bulb temperature (F)
Indoor air leaving wet-bulb temperature (F)
Indoor leaving enthalpy (Btu/lbm)
Indoor nozzle dry-bulb temperature (F)
Indoor nozzle wet-bulb temperature (F)
Outdoor air entering dry-bulb temperature (F)
Outdoor air entering wet-bulb temperature (F)
Outdoor entering enthalpy (Btu/lbm)
Heating Capacity
Measurement
Total sensible heating capacity (Btu/hr)
Duct loss (Btu/hr) (if applicable)
Total heating capacity (Btu/hr)
Results
|  | Measurement |  |  | Calculated Result (rounded per significant figures conventions and instrumentation resolution)
Total corrected heating capacity (Btu/hr)
| Total system power (Watts) | 0
System Efficiency (COP)
Heating Mode - Outdoor Air Enthalpy Method
Electrical Input Measurements
Measurement
|  | Avg | Min | Max
Applied voltage to unit (V)
Frequency (Hz)
Line current (Amps)
Total system power (Watts)
Pressure Measurements
Measurement
|  | Avg | Min | Max
Barometric pressure - (in. Hg)
Indoor nozzle pressure delta (in. H2O)
Indoor external static pressure (in. H2O)
Refrigerant Measurements
Measurement
|  | Avg | Min | Max
Suction temperature at compressor (F)
Discharge temperature at compressor (F)
Vapor temperature at condenser coil (F)
Liquid line temperature at condenser coil (F)
Airflow Measurements
Measurement
|  | Avg | Min | Max
Unit indoor airflow (cfm)
Unit indoor standard airflow (scfm)
Indoor Fan Speed (rpm) [if recorded]
Unit outdoor airflow (cfm)
Unit outdoor standard airflow (scfm)
Outdoor Fan Speed (rpm) [if recorded]
Air Temperatures
Measurement
|  | Avg | Min | Max
Indoor air entering dry-bulb temperature (F)
Indoor air entering wet-bulb temperature (F)
Indoor entering enthalpy (Btu/lbm)
Indoor air leaving dry-bulb temperature (F)
Indoor air leaving wet-bulb temperature (F)
Indoor leaving enthalpy (Btu/lbm)
Indoor nozzle dry-bulb temperature (F)
Indoor nozzle wet-bulb temperature (F)
Outdoor air entering dry-bulb temperature (F)
Outdoor air entering wet-bulb temperature (F)
Outdoor entering enthalpy (Btu/lbm)
Outdoor air leaving dry-bulb temperature (F)
Outdoor air leaving wet-bulb temperature (F)
Outdoor leaving enthalpy (Btu/lbm)
Outdoor nozzle dry-bulb temperature (F)
Outdoor nozzle wet-bulb temperature (F)
Heating Capacity
Indoor Measurements
Indoor sensible heating capacity (Btu/hr)
Indoor duct loss (Btu/hr) (if applicable)
Indoor total heating capacity (Btu/hr)
Outdoor Measurements
Outdoor sensible heating capacity (Btu/hr)
Outdoor latent cooling capacity (Btu/hr)
Outdoor duct loss (Btu/hr) (if applicable)
Outdoor power draw (Btu/h)
Outdoor total heating capacity
Comparison
Heat balance (%) (indoor vs. outdoor total capacity) [must be <6%]
Heat balance (%) (indoor air enthalpy vs outdoor air enthalpy) [must be <2%]
Results
Measurement
Total corrected heating capacity (Btu/hr)
| Total system power (Watts) | 0
System Efficiency (COP)

## Test Comments
Title Block
Test Report Template Name: | Single Packaged Vertical Unit | Back to Instructions
Version Number: | v2.0
Latest Template Revision: | 2015-06-05
Tab Name: | Test Comments
File Name: | Single Packaged Vertical Unit - v2.0.xlsx
Test Completion Date: | [MM/DD/YYYY]
Comments

## Report Sign-off Block
Title Block
Test Report Template Name: | Single Packaged Vertical Unit |  | Back to Instructions
Version Number: | v2.0
Latest Template Revision: | 2015-06-05
Tab Name: | Report Sign-off Block
File Name: | Single Packaged Vertical Unit - v2.0.xlsx
Test Completion Date: | [MM/DD/YYYY]
Test Report Sign-Off Block
By signing in the space below, we certify that the information and data in this report: (1) were obtained from the specific test unit under test; (2) were obtained during the specific test being reported; (3) were not copied from any other source, except where instructed to do so; and (4) were not altered or modified in any way.
Role |  | Date | Entity
Test Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Template Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Report Reviewer by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]

## Drop-Downs
Title Block
Test Report Template Name: | Single Packaged Vertical Unit
Version Number: | v2.0 |  | Back to Instructions
Latest Template Revision: | 2015-06-05
Tab Name: | Drop-Downs
File Name: | Single Packaged Vertical Unit - v2.0.xlsx
Test Completion Date: | [MM/DD/YYYY]
Y_N |  | Product_Type |  | Refrigerant | Control
Yes |  | SPVAC |  | R-22 | Electromechanical
No |  | SPVHP |  | R-410A | Electronic
Other

## Tables
Title Block
Test Report Template Name: | Single Packaged Vertical Unit
Version Number: | v2.0 |  | Back to Instructions
Latest Template Revision: | 2015-06-05
Tab Name: | Tables
File Name: | Single Packaged Vertical Unit - v2.0.xlsx
Test Completion Date: | [MM/DD/YYYY]
Minimum External Static Pressure Table
Cooling Capacity Range (Btu/h) |  | External Static Pressure (in. H20)
Min | Max
0 | 28000 | 0.1
28001 | 42000 | 0.15
42001 | 70000 | 0.2
70001 | 105000 | 0.25
105001 | 134000 | 0.3

## Version Control
Title Block
Test Report Template Name: | Single Packaged Vertical Unit | Back to Instructions
Version Number: | v2.0
Latest Template Revision: | 2015-06-05
Tab Name: | Version Control
File Name: | Single Packaged Vertical Unit - v2.0.xlsx
Test Completion Date: | [MM/DD/YYYY]
Revisions List
Version | Date
1.0_draft 3 | 2013-07-20
1.0_draft 4 | 2013-08-01
v1.0 | 2015-03-09
v2.0 | 2015-06-05