## Instructions
Title Block
Test Report Template Name: | Illuminated Exit Signs
Version Number: | v1.1
Latest Template Revision: | 2013-11-20
Tab Name: | Instructions
File Name: | Illuminated Exit Signs - v1.1.xlsx
Reference Test Procedure
10 CFR 431 Subpart L - Illuminated Exit Signs
Table of Contents
Tab | Contents
Instructions | Instructions and table of contents
General Info & Test Results | Lab information, product information and test results
Setup & Instrumentation | Instrumentation requirements and space for sensor placement descriptions
Photos | Inputs for photographs
Test Data Inputs | Measurement inputs
Comments | Inputs for report template user to provide comments
Report Sign-Off Block | Report review history
Drop-Downs | Drop-downs used
Version Control | Revision history
LEGEND
Tabs | Tabs with input cells
Cells | Input cell
Auto-populated cell
Provided data
NOT USED
Instructions for completing this Workbook
Follow the steps below, filling in all input cells (shaded light blue) in each tab you are instructed to complete. Using TAB to "hop" from input cell to input cell is useful, but does not ensure that all input cells are reached. To guarantee that you enter all required information, you must visually scan for light blue cells in the entire area bounded by yellow-shaded cells.
Important: Start with a clean (unused) template copy for each new report. Enter only data and information that are unique to the unit tested and the current test of that unit. All abbreviations and variable names should be consistent with the reference test procedure.
STEP: | FILL IN INPUT CELLS IN THIS TAB:
Step 1 | General Info and Test Results
Step 2 | Setup & Instrumentation
Step 3 | Photos
Step 4 | Test Data Inputs
Step 5 | Comments
Step 6 | Report Sign-off Block

## General Info & Test Results
Title Block
Test Report Template Name: | Illuminated Exit Signs
Version Number: | v1.1 | Back to Instructions tab
Latest Template Revision: | 2013-11-20
Tab Name: | General Info & Test Results
File Name: | Illuminated Exit Signs - v1.1.xlsx
Test Completion Date: | [MM/DD/YYYY]
Lab Information |  | Test Results
Lab Name: |  | Variable | Result | Units
Lab Location: |  | Input Power (entire unit) |  | Watts
|  | Input Power (per face) |  | Watts/Face
Test Information
Date Test Started: | [MM/DD/YYYY] | NOTE: This is only a copy; sign off is done in the Report Sign-Off Block tab
Date Test Finished: | [MM/DD/YYYY] | Test Report Sign-Off Block
We certify that the information and data in this report: (1) were obtained from the specific test unit under test; (2) were obtained during the specific test being reported; (3) were not copied from any other source, except where instructed to do so; and (4) were not altered or modified in any way.
Product Information
Brand:
Manufacturer: |  | Role |  | Date | Entity
Manufacturer model number: |  | Test Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Serial number: |  | Template Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Date of Manufacture (if available): |  | Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Date Product Received: | [MM/DD/YYYY] | Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Condition as received: |  | Report Review by DOE |  | [MM/DD/YYYY] | DOE
Outer Dimensions (in)
Height
Width
Depth
Product Characteristics
Does unit have a rechargeable battery?
Rated Input Voltage:
Number of faces (an illuminated side of an illuminated exit sign) on unit:
Is unit designed to be permanently fixed in place to identify an exit?
Does the unit consist of an electrically powered integral light source that:
Illuminates the legend "EXIT" and any directional indicators?
Provides contrast between the legend, and directional indicators, and the background?

## Setup & Instrumentation
Title Block
Test Report Template Name: | Illuminated Exit Signs
Version Number: | v1.1 |  | Back to Instructions tab
Latest Template Revision: | 2013-11-20
Tab Name: | Setup & Instrumentation
File Name: | Illuminated Exit Signs - v1.1.xlsx
Test Completion Date: | [MM/DD/YYYY]
Setup (This table should include instrumentation, sensors, and all equipment used during testing)
Instrument Type | Brand | Model # | Sensor Location | Accuracy | Date of Last Calibration | Deadline for Next Calibration
Describe placement of sensors used to measure ambient air temperature:
If additional sensors were used, describe placement:

## Photos
Title Block
Test Report Template Name: | Illuminated Exit Signs
Version Number: | v1.1 | Back to Instructions tab
Latest Template Revision: | 2013-11-20
Tab Name: | Photos
File Name: | Illuminated Exit Signs - v1.1.xlsx
Test Completion Date: | [MM/DD/YYYY]
1. Nameplate showing model number and serial number (if applicable) |  |  | 2. FTC EnergyGuide label (if present)
3. Photos of test unit from all sides (including photo of control panel, if applicable)
4. Exact placement of all sensors on, in, or around the device
5. Additional photos (if necessary)

## Test Data Inputs
Title Block
Test Report Template Name: | Illuminated Exit Signs
Version Number: | v1.1 |  |  | Back to Instructions tab
Latest Template Revision: | 2013-11-20
Tab Name: | Test Data Inputs
File Name: | Illuminated Exit Signs - v1.1.xlsx
Test Completion Date: | [MM/DD/YYYY]
Test Conditions
|  | Measured Test Conditions |  | Required Test Conditions
Is the Test Room considered to have Clear (non-smoke) Conditions? |  |  |  | Testing shall be conducted in clear (non-smoke) conditions
Test Room Ambient Air Temperature |  |  | °C | All measurements shall be made in a stable ambient air temperature of 25°C ± 5°C
Test Voltage |  |  | V | All voltages shall be provided within ± 0.5% by a constant voltage power supply
Duration of Pre-conditioning (prior to Input Power Measurement) |  |  | hours | Prior to input power or photometric measurements, the exit sign model shall be operated at the rated input voltage for a period of 100 hours. All of the light sources in the sign must produce light throughout the first 100 hours of operation, before any measurements are taken.
Duration of Operation from Battery (prior to Input Power Measurement) |  |  | hours | Exit Sign Models with an internal battery shall be operated from the battery for 1½ hours, and then recharged for the period specified by the sign manufacturer
Duration of Battery Recharge (prior to Input Power Measurement) |  |  | hours
Input Power Measurement
|  | Measurement |  | Measurement Requirements
Input Power (entire unit) |  |  | Watts | The input power fo the exit sign model in its entirety shall be measured with an appropriate True RMS Watt Meter at the rated input voltage which represents normal operation. For an exit sign model that includes a battery, the battery circuit shall be connected and the battery fully charged before any measurements are made.
|  | Calculated Result (unrounded) | Calculated Result (rounded per significant figures conventions and instrumentation resolution)
Input Power (per face) |  |  |  | Watts/face
Notes/Comments: (Please clarify any pertinent details, unusual events, etc.)

## Comments
Title Block
Test Report Template Name: | Illuminated Exit Signs
Version Number: | v1.1 | Back to Instructions tab
Latest Template Revision: | 2013-11-20
Tab Name: | Comments
File Name: | Illuminated Exit Signs - v1.1.xlsx
Test Completion Date: | [MM/DD/YYYY]
Comments

## Report Sign-Off Block
Title Block
Test Report Template Name: | Illuminated Exit Signs
Version Number: | v1.1 |  | Back to Instructions tab
Latest Template Revision: | 2013-11-20
Tab Name: | Report Sign-Off Block
File Name: | Illuminated Exit Signs - v1.1.xlsx
Test Completion Date: | [MM/DD/YYYY]
Test Report Sign-Off Block
By signing in the space below, we certify that the information and data in this report: (1) were obtained from the specific test unit under test; (2) were obtained during the specific test being reported; (3) were not copied from any other source, except where instructed to do so; and (4) were not altered or modified in any way.
Role |  | Date | Entity
Test Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Template Completion |  | [MM/DD/YYYY] | [Test Lab Name]
Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Report Review by Test Lab |  | [MM/DD/YYYY] | [Test Lab Name]
Report Review by DOE |  | [MM/DD/YYYY] | DOE

## Drop-Downs
Title Block
Test Report Template Name: | Illuminated Exit Signs
Version Number: | v1.1 |  | Back to Instructions tab
Latest Template Revision: | 2013-11-20
Tab Name: | Drop-Downs
File Name: | Illuminated Exit Signs - v1.1.xlsx
Test Completion Date: | [MM/DD/YYYY]
DD_RechargeableBattery_Y_N |  | DD_Clear_Conditions_Y_N
Yes |  | Yes
No |  | No
DD_Permanently_Fixed_Y_N |  | DD_Integral_Exit_Y_N | DD_Integral_Contrast_Y_N
Yes |  | Yes | Yes
No |  | No | No

## Version Control
Title Block
Test Report Template Name: | Illuminated Exit Signs
Version Number: | v1.1 | Back to Instructions tab
Latest Template Revision: | 2013-11-20
Tab Name: | Version Control
File Name: | Illuminated Exit Signs - v1.1.xlsx
Test Completion Date: | [MM/DD/YYYY]
Revisions List
Version | Date
0.1 | 2011-08-03
0.2 | 2011-08-04
0.3 | 2011-08-17
1 | 2011-08-17
v1.1 | 2013-11-20